## 1.a. Gas turb. simple cycle, NG
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - small |  |  |  |  | Obs original data was taken from "large"
year |  | 2025 | 2025 | 2025 | Note | Ref | data in 2022 prices
est |  |  | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 22.5 | 5 | 40 | F
| Electrical efficiency (net, name plate) [] | 38% | 32% | 40% | [G, H] | [6, 12]
| Electrical efficiency (net, annual average) [] | 36% | 30% | 38% |  | [6, 11]
| Cb coefficient (50°C/100°C) | 0.765 | 0.61 | 0.8 |  | [6, 12]
| Cv coefficient (50°C/100°C) |  |  |  | J
| Forced outage [] | 2% | 2% | 3% |  | 6
| Planned outage [weeks per year] | 2.65 | 2 | 3.5 |  | 6
| Technical lifetime [years] | 25 | 25 |  | E | [6, 7]
| Construction time [years] | 1.5 | 1 | 1.5 |  | 6
| Space requirement [1000 m2/MW_e] | 0.04 | 0.03 | 0.07 | G | 7
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 0% | 0% | 0% | I
| Secondary regulation (of full load, per minute) [] | 20% | 20% | 50% | C | 6
| Minimum load (of full load) [] | 21.5% | 20% | 25% | A | 6
| Warm start-up time [hours] | 0.215 | 0.1 | 0.5 |  | [5, 6, 8]
| Cold start-up time [hours] | 0.5 | 0.4 | 1 |  | [5, 6, 8]
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 0%
| NOX [g/GJ_i] | 12.5 | 10 | 30 | D | [7, 9]
| CH4 [g/GJ_i] | 1.5 | 1 | 8 |  | 9
| N2O [g/GJ_i] | 1 | 0.7 | 1.2 |  | 9
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.77721 | 0.63802 | 1.0634 | 0 | [6, 10]
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | K
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | K
| Variable O&M (*total) [EUR/MWh_e] | 5.7068 | 5.3169 | 7.4436 | 0 | 6
| Fixed O&M (*total) [EUR/MW_e/y] | 20707.4114 | 0 | 0 | B | 6
Technology-specific data
| Possible wintertime production ( October to March) | 4192.8
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 1.b. Gas engines, NG
Technology |  | Engine - back pressure - natural gas - small
year |  | 2025 | 2025 | 2025 | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 5.5 | 1 | 10
| Electrical efficiency (net, name plate) [] | 47.5% | 40% | 48% | A | [3, 4]
| Electrical efficiency (net, annual average) [] | 46% | 38% | 46% | A | [3, 4, 7]
| Cb coefficient (50°C/100°C) | 0.97 | 0.65 | 1.02 |  | [3, 4, 7]
| Cv coefficient (50°C/100°C) |  |  |  | G
| Forced outage [] | 3% | 2% | 5% |  | [5, 6]
| Planned outage [weeks per year] | 0.8 |  |  | H | [5, 6]
| Technical lifetime [years] | 25 | 25 |  | D | [4, 5, 7]
| Construction time [years] | 1 | 0.5 | 1.5 | B | [3, 6]
| Space requirement [1000 m2/MW_e] | 0.04 | 0.03 | 0.05
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 32.5% | 10% | 40% |  | 12
| Secondary regulation (of full load, per minute) [] | 35% | 20% | 100% | C | [6, 12, 13]
| Minimum load (of full load) [] | 50% | 30% | 50% |  | 6
| Warm start-up time [hours] | 0.05 | 0.01 | 0.15 | C | [6, 10]
| Cold start-up time [hours] | 0.3 | 0.2 | 0.4 | E | [6, 10]
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 0% |  | 4
| NOX [g/GJ_i] | 60 | 50 | 100 |  | 4
| CH4 [g/GJ_i] | 297.5 | 300 | 400 |  | 4
| N2O [g/GJ_i] | 0.6 |  |  | H
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.0055 | 0.95704 | 1.1697 | 0 | [3, 5, 11]
| Nominal investment (equipment) [MEUR/MW_e] | 0.62503 | 0 | 0 | H | [3, 5]
| Nominal investment (installation) [MEUR/MW_e] | 0.38045 | 0 | 0 | H | [3, 5]
| Variable O&M (*total) [EUR/MWh_e] | 5.7068 | 4.2535 | 12.7605 | F | [3, 5, 11]
| Fixed O&M (*total) [EUR/MW_e/y] | 10353.7057 | 7443.609 | 21267.4544 | F | 5
Technology-specific data
| Possible wintertime production ( October to March) | 4105.2
Notes:
A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D. Technical- and design life most often > 25 years
E. For a medium size engine; small engines with less thermal mass might be faster
F. When operating 4000 hours a year
G. Only relevant for steam based CHP
H. No data available
I. DGC estimate for years 2030, 2050
J. No known use, data from n-gas engines
K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. ASUE BHKW Kenndata 2014/2015
4. DGC Efficiency and emission test reports
5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8. Ongoing Sulpur research project at DGC (MUDP)
10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12. Suppliers association information etc.
13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012

## 1.c. Gas engines, biogas
Technology |  | Engine - back pressure - biogas - small
year |  | 2025 | 2025 | 2025 | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 5.5 | 1 | 10
| Electrical efficiency (net, name plate) [] | 44% | 38% | 44% | A | [3, 4]
| Electrical efficiency (net, annual average) [] | 42% | 36% | 42% | A | [3, 4, 7]
| Cb coefficient (50°C/100°C) | 0.89 | 0.59 | 0.96 |  | [3, 4, 7]
| Cv coefficient (50°C/100°C) |  |  |  | G
| Forced outage [] | 3% | 2% | 5% |  | [5, 6]
| Planned outage [weeks per year] | 1 |  |  | H | [5, 6]
| Technical lifetime [years] | 25 | 25 |  | D | [4, 5, 7]
| Construction time [years] | 1 | 0.5 | 1.5 | B | [3, 6]
| Space requirement [1000 m2/MW_e] | 0.04 | 0.03 | 0.05
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 35% | 10% | 40% | J | 8
| Secondary regulation (of full load, per minute) [] | 35% | 20% | 100% | C | [6, 8, 13]
| Minimum load (of full load) [] | 50% | 30% | 50% |  | 6
| Warm start-up time [hours] | 0.05 | 0.01 | 0.15 | C | [6, 10]
| Cold start-up time [hours] | 0.3 | 0.2 | 0.4 | E | [6, 10]
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 99.9% | K | 8
| NOX [g/GJ_i] | 100 | 90 | 120 |  | 4
| CH4 [g/GJ_i] | 300 | 300 | 400 |  | 4
| N2O [g/GJ_i] | 1 |  |  | J
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.0055 | 0.8507 | 1.276 | 0 | [3, 5, 11]
| Nominal investment (equipment) [MEUR/MW_e] | 0.62503 | 0 | 0 | 0 | [3, 5]
| Nominal investment (installation) [MEUR/MW_e] | 0.38045 | 0 | 0 | 0 | [3, 5]
| Variable O&M (*total) [EUR/MWh_e] | 7.8808 | 6.3802 | 13.8238 | F | [3, 5, 11]
| Fixed O&M (*total) [EUR/MW_e/y] | 10353.7057 | 7443.609 | 21267.4544 | F | 5
Technology-specific data
| Possible wintertime production ( October to March) | 4105.2
Notes:
A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D. Technical- and design life most often > 25 years
E. For a medium size engine; small engines with less thermal mass might be faster
F. When operating 4000 hours a year
G. Only relevant for steam based CHP
H. No data available
I. DGC estimate for years 2030, 2050
J. No known use, data from n-gas engines
K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. ASUE BHKW Kenndata 2014/2015
4. DGC Efficiency and emission test reports
5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8. Ongoing Sulpur research project at DGC (MUDP)
10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12. Suppliers association information etc.
13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012

## 2.a. PV residential rooftop
Technology |  | PV - renewable power - solar - residential rooftop
year |  | 2025 | 2025 | 2025 | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.006 |  |  | B3,C
| Forced outage [] | 0%
| Planned outage [weeks per year] | 0
| Technical lifetime [years] | 37.5
| Construction time [years] | 0
| Space requirement [1000 m2/MW_e] | 4.845 |  |  |  | 6
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.0641 | 0.8 | 1.3 | M,O | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 1.0135 | 0.8 | 1.2 | M,N | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0.028886 | 0.03 | 0.03
| Nominal investment (inverter) [MEUR/MW_e] | 0.18811 | 0.17 | 0.22
| Nominal investment (pv modules) [MEUR/MW_e] | 0.39015 | 0.35 | 0.48 | M,O
| Nominal investment (installation) [MEUR/MW_e] | 0.26081 | 0.13 | 0.28
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0.19485 | 0.17 | 0.22
Nominal investment (soft costs) [MEUR/MW_e]
| Fixed O&M (*total) [EUR/MW_e/y] | 12317.7778 | 3000 | 14000 | P
Fixed O&M (land rent) [EUR/MW_e/y]
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | 0.0063 |  |  | B3,C
| Space requirement (per DC) [1000m2/MW_e] | 4.615 |  |  |  | 6
| Nominal investment (installation, per DC) [MEUR/MW_e] | 0.24839 | 0.23 | 0.28
| Nominal investment (inverter, per DC) [MEUR/MW_e] | 0.17915 | 0.16 | 0.22
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | 0.18557 | 0.17 | 0.21
| Nominal investment (pv module, per DC) [MEUR/MW_e] | 0.37157 | 0.32 | 0.49 | M,O
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | 0.02751 | 0.03 | 0.03
| Fixed O&M (*total, per DC) [EUR/MW_e/y] | 11755.5556 | 10500 | 14100 | P
Fixed O&M (land rent, per DC) [EUR/MW_e/y]
| Fixed O&M (other, per DC) [EUR/MW_e/y] | 11755.5556
| Average annual degradation of full-load hours [] | 0.35%
| Global horizontal irradiance [kWh/m2/y] | 1205 | 1000 | 1400 | A | 1
| Transposition factor | 1.1 |  |  | E
| Performance ratio (contribution from bifaciality) [] | 0 |  |  |  | 3
| Performance ratio (measure of combined losses) [] | 87.5% |  |  | F
| PV module conversion efficiency [] | 21.75% |  |  | U | 3
| Inverter lifetime [years] | 13.75 |  |  |  | 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.05 |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | 1159.8125 |  |  | A1,I
| Average annual full-load hours [MWh_e/MW_e] | 1104.5833 |  |  | A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Ukraine is 1205 (kWh/m2/y) (1022-1387) . The best sites demonstrate values around 1380 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 2.b. PV comm. & industrial
Technology |  | PV - renewable power - solar - commercial/industrial rooftop
year |  | 2025 | 2025 | 2025 | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.1 |  |  | B2,C
| Forced outage [] | 0%
| Planned outage [weeks per year] | 0
| Technical lifetime [years] | 37.5
| Construction time [years] | 0
| Space requirement [1000 m2/MW_e] | 5.075 |  |  |  | 6
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.736 | 0.7 | 0.78 | M,O | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 0.66444 | 0.6 | 0.72 | M,N | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0.040889 | 0.03 | 0.05
| Nominal investment (inverter) [MEUR/MW_e] | 0.14311 | 0.12 | 0.16
| Nominal investment (pv modules) [MEUR/MW_e] | 0.34756 | 0.3 | 0.4 | M,O
| Nominal investment (installation) [MEUR/MW_e] | 0.12267 | 0.11 | 0.13
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0.081778 | 0.07 | 0.09
Nominal investment (soft costs) [MEUR/MW_e]
| Fixed O&M (*total) [EUR/MW_e/y] | 9750 | 9500 | 11000 | P
Fixed O&M (land rent) [EUR/MW_e/y]
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | 0.11 |  |  | B2,C
| Space requirement (per DC) [1000m2/MW_e] | 4.615 |  |  | W | 6
| Nominal investment (installation, per DC) [MEUR/MW_e] | 0.11244 | 0.1 | 0.13
| Nominal investment (inverter, per DC) [MEUR/MW_e] | 0.13289 | 0.11 | 0.15
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | 0.071556 | 0.06 | 0.08
| Nominal investment (pv module, per DC) [MEUR/MW_e] | 0.31689 | 0.29 | 0.35 | M,O
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | 0.035778 | 0.04 | 0.04
| Fixed O&M (*total, per DC) [EUR/MW_e/y] | 9046.6667 | 8600 | 10000 | P
Fixed O&M (land rent, per DC) [EUR/MW_e/y]
| Fixed O&M (other, per DC) [EUR/MW_e/y] | 9046.6667
| Average annual degradation of full-load hours [] | 0.35%
| Global horizontal irradiance [kWh/m2/y] | 1205 | 9800 | 1400 | A | 1
| Transposition factor | 1.1 |  |  | E
| Performance ratio (contribution from bifaciality) [] | 0% |  |  |  | 3
| Performance ratio (measure of combined losses) [] | 87.5% |  |  | F
| PV module conversion efficiency [] | 21.75% |  |  | U | 3
| Inverter lifetime [years] | 13.75 |  |  |  | 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.1 |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | 1159.8125 |  |  | A1,I
| Average annual full-load hours [MWh_e/MW_e] | 1054.375 |  |  | A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Ukraine is 1205 (kWh/m2/y) (1022-1387) . The best sites demonstrate values around 1380 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 2.c. PV Utility scale, ground
Technology |  | PV - renewable power - solar - utility-scale, ground mounted
year |  | 2025 |  | 2025 |  | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl |  | lower | upper | - | -
cat | par | without tracker | with tracker
Energy/technical data
| Generating capacity for one unit [MW_e] | 40
| Forced outage [] | 0%
| Planned outage [weeks per year] | 0
| Technical lifetime [years] | 37.5 |  | 25
| Construction time [years] | 0.5 |  | 1
| Space requirement [1000 m2/MW_e] | 13.005 |  |  |  | B,B1 | 6
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | G
| Secondary regulation (of full load, per minute) [] |  |  |  |  | G
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.48044 |  | 0.38436 | 0.57653 | M,N,O,Q | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 0.38844 |  | 0.31076 | 0.46613 | M,N,O,Q | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0.056222 |  | 0.044978 | 0.067467
| Nominal investment (inverter) [MEUR/MW_e] | 0.025556 |  | 0.020444 | 0.030667
| Nominal investment (pv modules) [MEUR/MW_e] | 0.20444 |  | 0.16356 | 0.24533
| Nominal investment (installation) [MEUR/MW_e] | 0.11756 |  | 0.094044 | 0.14107
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0.046 |  | 0.0368 | 0.0552
| Nominal investment (soft costs) [MEUR/MW_e] | 0.035778 |  | 0.028622 | 0.042933 | V
| Fixed O&M (*total) [EUR/MW_e/y] | 10631.1111 |  | 8504.8889 | 12757.3333
| Fixed O&M (land rent) [EUR/MW_e/y] | 4242.2222 |  |  |  | S
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | 50 |  |  |  | C
| Space requirement (per DC) [1000m2/MW_e] | 10.4 |  |  |  | B,B1 | 6
| Nominal investment (installation, per DC) [MEUR/MW_e] | 0.092 |  |  |  | V
| Nominal investment (inverter, per DC) [MEUR/MW_e] | 0.020444
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | 0.035778
| Nominal investment (pv module, per DC) [MEUR/MW_e] | 0.16356
| Nominal investment (soft costs, per DC) [MEUR/MW_e] | 0.025556 |  |  |  | V
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | 0.046 |  |  |  | R
| Fixed O&M (*total, per DC) [EUR/MW_e/y] | 8484.4444 |  | 6787.5556 | 10181.3333
| Fixed O&M (land rent, per DC) [EUR/MW_e/y] | 3373.3333 |  |  |  | S | 6
| Fixed O&M (other, per DC) [EUR/MW_e/y] | 511111% |  |  |  | P2
| Average annual degradation of full-load hours [] | 0.0035 |  | 0.003 | 0.005 | A2
| Global horizontal irradiance [kWh/m2/y] | 1205 |  | 1000 | 1400 | A | 1
| Transposition factor | 117% |  |  |  | E
| Performance ratio (contribution from bifaciality) [] | 3% |  |  |  | H | 3
| Performance ratio (measure of combined losses) [] | 90.5% |  |  |  | F
| PV module conversion efficiency [] | 21.75% |  | 20% | 0.21 | U | 3
| Inverter lifetime [years] | 13.75 |  |  |  |  | 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.25 |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | 1275.9143 |  |  |  | A1, K
| Average annual full-load hours [MWh_e/MW_e] | 1020.7314 | 1190.2138 |  |  | A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 2.d. PV Utility scale, floating
| Technology | Floating PV - Large scale grid connected
|  | 2025 | 2025 |  | Note | Ref |  | Average of 2020 and 2030 data in 2022 prices
| Energy/technical data |  | Lower | Upper
| Generating capacity for one unit [MW_e] | 10 |  |  | C |  | Opdateres ikke
| Electricity efficiency, net (%), name plate | - |  |  | A
| Electricity efficiency, net (%), annual average | - |  |  | A
| Forced outage [] | -
| Planned outage [weeks per year] | -
| Technical lifetime [years] | 35 | 25 | 40 |  | 1,6
| Construction time [years] | 0.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 8.3 | 7.2 | 10 |  | 10
Additional data for non thermal plants
| Capacity factor (%), theoretical | 22.8082 | 14 | 22 |  | 1,2,5
| Capacity factor (%), incl. outages | 22.8082 | 14 | 22 |  | 1,2,5
Ramping configurations
| Ramping (% per minute) | - | - | - | B
| Minimum load (% of full load) | - | - | - | B
| Warm start-up time (hours) | - | - | - | B
| Cold start-up time (hours) | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0
| SO2 (degree of desulphuring, %) | 0
| NOX (g per GJ fuel) | 0
| CH4 (g per GJ fuel) | 0
| N2O (g per GJ fuel) | 0
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.58267 | 0.99915 | 1.684 | D,R,S | 1,3,4
| - of which equipment | 67.22%
| - of which installation | 32.78%
| Fixed O&M (*total) [EUR/MW_e/y] | 10631.1111 | 8000 | 13300 | E,Q | 3
| Variable O&M [EUR/MWh] | 0 | 0 | 0
| Start-up costs [EUR/MW_e/start-up] | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance [kWh/m2/y] | 1205 | 1000 | 1400 | F | 8
| Sizing factor (DC/AC) [W_e/W_e] | 1.2 |  |  | G
| Transposition factor | 1.15 |  |  | H | 8
| Performance ratio (measure of combined losses) [] | 86% |  |  | I | 5.6
| PV module conversion efficiency [] | 21% |  |  | T | 6
| Inverter lifetime [years] | 12.5 |  |  |  | 6
Output
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | 1200 |  |  | J, L
| Average annual full-load hours [MWh_e/MW_e] | 1000 |  |  | K, L
Financial data
| PV module & inverter cost (EUR/Wp) | 0.20393 |  |  |  | 6.9
| Balance Of Plant cost (EUR/Wp) | 0.27358 |  |  |  | 6.9
| Specific investment, total system (EUR/Wp) | 0.48556 |  |  | M | 11
| Specific investment, total system (million EUR/MW) | 0.58267 |  |  | P
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IRENA, Renewable Power Generation Costs in 2022, 2023
4 | Learning curve approach for the development of financial parameters.
5 | Benefits of pairing floating solar photovoltaics with hydropower reservoirs in Europe 2023, https://www.sciencedirect.com/science/article/pii/S136403212200870X?via%3Dihub
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | M Rosa-Clot and G.M. Tina, Levelized Cost of Energy (LCOE) Analysis
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
10 | Iselectric brochure. Last accessed: September 2020
11 | Average investment cost of floating PV plants in Asia
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1800 kWh/m2 corresponds to a good location in Indonesia, in the top 20% percentile of the best solar sites.
G | The DC/AC equals module peak capacity Wp divided by plant capacity We(output of the inverter). The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Ukraine the TF factor for fixed systems adding 10-20% to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | The forecasted price is based on estimated learning rates for the module and invester (25 % and 19% learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's Announced Pledges Scenario 2021. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Indonesian prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
T | PV module conversion efficiency (%) is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module. | Is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module
U | Estimations of space requirements are based on the mapping of the average polygonal area occupied by PV arrays and electrical equipments like inverter pad of existing floating PV plants in Indonesia and Singapore.

## 3.a. Wind onshore parks
Technology |  | Onshore wind turbine, utility - renewable power - wind - large
year |  | 2025 | 2025 | 2025 | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  |  | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 4.5 | 2 | 6 | A1 | 2
| Forced outage [] | 2.5% | 1% | 5% | B | 18
| Planned outage [weeks per year] | 0.003 | 0.05 | 0.26 | C | 18
| Technical lifetime [years] | 27 | 25 | 35 | D | 11
| Construction time [years] | 1.5 | 1 | 3 | E | 18
| Space requirement [1000 m2/MW_e] |  |  |  | F
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] |  |  |  | G
| Secondary regulation (of full load, per minute) [] |  |  |  | G
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.211 | 0.96877 | 1.4531 | [I, M] | [12, 1, 18]
| Nominal investment (equipment) [MEUR/MW_e] | 0.88329 | 0.70663 | 1.0599 |  | 20
| Nominal investment (installation) [MEUR/MW_e] | 0.091504 | 0.073203 | 0.10981 |  | 20
| Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | 0.03229 | 0.025832 | 0.038747 |  | 20
| Nominal investment (grid connection) [MEUR/MW_e] | 0.017827 | 0.014262 | 0.021392 | O | 20
| Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | 0.071722 | 0.057377 | 0.086066 | [Q] | [20, 21]
| Nominal investment (land rent) [MEUR/MW_e] | 0.11342 | 0.090739 | 0.13611 | P | 20
| Variable O&M (*total) [EUR/MWh_e] | 2.1068 | 1.6854 | 2.5282 | [J, N] | [13, 21]
| Fixed O&M (*total) [EUR/MW_e/y] | 17773.0036 | 14218.4028 | 21327.6043 | [J, N] | [20, 21]
Technology-specific data
| Availability [] | 97% | 98.9% | 94.5% |  | [18, 21]
| Hub height [m] | 90 | 85 | 120 |  | [18, 21]
| Rotor diameter [m] | 135 | 90 | 130 | K | [18, 21]
| Specific power [W_e/m2] | 310 | 314.38 | 452.04
| Average capacity factor [] | 39.95% | 22.83% | 45.66% |  | [18, 21]
| Average annual full-load hours [MWh_e/MW_e] | 3500 | 2000 | 4000 | [A, L] | 2
Notes:
A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present max. 150m tip height.
A. The full load hours (annual produktion (MWh) per installed power (MW)) depending on the actual location of the wind farm, wake losses and technological characteristics of the individual turbine. The value is an average for the expected locations of the wind farms. FLH also depends on wake losses, noise reduction and technological characteristics of the individual turbine. The level for 2020 is based on expectations from the November 18 auction winners locations and the 2019 prefered technology choice. For 2030 and 2050 a slight increase is assumed based on decrease in specific power and increase in hub height.
B. Modern turbines has typically higher forced outage than older smaller turbines had when they were newer due to more complex technology.
C. Planned outage is typically 1-2 service visits a year, with a maximum duration of one work day, but there can also be planned outage due to shadow flicker stop or sector management (protect turbines at given wind speeds and directions, where they are dense spaced).
D. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine.
E. The construction time is the periode from FID to commissioning. But from first "dig" to turbines are in operation less than ½ a year is needed for smaller wind farms (clusters), where the similar periode for larger wind farms will be longer. The planning time from idea to construction starts will typically be 2-3 years, but can be essentially more if permitting problems occour.
F. An area of around 50 m x 50 m is needed for a modern wind turbine. Another way of defining the "area use" could be the noise zone, which ranges up to 600-800 m from the wind turbine in worst case.
G. Wind turbines can be downward regulated within very short time and can therefore (if the wind is blowing) be used in both the primary and secondary downward regulation.
H. 2015 Investment costs are based on a number of prospects for projects published in relation to Køberetsordningen. 2020 investment costs are based on updated data from Køberetsordningen. Note that the investment costs listed here includes construction loan interests.
I. The grid connection is sozialized in Denmark and can be subtracted from the given nominal investment seen from the project owner (change with new auction system from 2018).
J. 75 % of the total yearly O&M costs are assumed to be fixed cost and 25 % are assumed to be variable cost.
K. Currently only turbines up to 150 m total height is installed commercially in Denmark because of strict demands to higher turbines. No change in the national regulation is assumed until after 2020. Some test sites allow for larger turbines. Aboard e.g. in Germany turbines with at total higher of 200 m is installed today.
L. It is expected that the production (FLH) increase 13% from 2015 to 2020 and 3% from 2020-2030 and 1% per decade from 2030-2050.
M. It is assumed that the investment cost for on shore turbine projects will be reduced 5% in each decade from 2020
N. It is assumed that the operation cost for on shore turbines will be reduced 5% in each decade from 2020.
O. Only internal grid costs included, see also note I
P. Land costs can be as well purchace as annual rent. Here is chosen to add annual rent x 10 to purchace costs in CAPEX and then remove land rent from OPEX.
Q. Purchase of neighbour settlements includes only the needed due to noise and distance demands, not the "new" 2022 politically decided "Sales option"
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. DTU International Energy Report - Perspectives on Wind Energy, DTU, 2021
2. Master data register of wind turbines, March 2022, Danish Energy Agency, 2023
11. Information from Energinet.dk based on analyses of installed projects (2013-14), published under "Købsretsordningen", 2015
12. Schwabe, P., Lensink, S. & Hand, M., IEA Wind Task 26: Multi-national case study of the financial cost of wind energy, 2011
13. Hvor længe holder en mølle, Naturlig Energi, januar 2012
18. Nielsen, P. et. al., Vindmøllers økonomi EUDP projekt 33033-0196, 2010
19. Når all-inclusive service alligevel ikke dækker alt, Naturlig Energi, nov. 2014
20. Analysis of "køberets" projects 2017-2018
21. Interviews with project developers and suppliers Dec. 2018 - Jan. 2019

## 3.c. Wind domestic turbines
Technology |  | Onshore wind turbine, residential - renewable power - wind - small
year |  | 2025 | 2025 | 2025 | Note | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.01 | 0.008 | 0.03
| Forced outage [] | 3% | 2.4% | 10%
| Planned outage [weeks per year] | 0.16 | 0.128 | 0.26 | B
| Technical lifetime [years] | 20 | 16 | 24
| Construction time [years] | 1 | 0.8 | 1.5
| Space requirement [1000 m2/MW_e] | 0.8 |  |  | C
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] |  |  |  | D
| Secondary regulation (of full load, per minute) [] |  |  |  | D
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 4.0273 | 3.2219 | 4.8328 | [E, F]
| Nominal investment (equipment) [MEUR/MW_e] | 0.9783 | 0.78264 | 1.174 | [E, F]
| Nominal investment (installation) [MEUR/MW_e] | 0.1087 | 0.08696 | 0.13044 | [E, F]
| Variable O&M (*total) [EUR/MWh_e] | 0 | 0 | 0 | 0
| Fixed O&M (*total) [EUR/MW_e/y] | 100547.7981 | 80438.2385 | 120657.3577 | G
Technology-specific data
| Fixed O&M (*total) [EUR/unit/y] | 552 | 350 | 700 | [E, F]
| Hub height [m] | 18 | 14 | 18 | H
| Rotor diameter [m] | 11.5 | 4 | 14 | H
| Average annual full-load hours [MWh_e/MW_e] | 1900 | 1000 | 2300 | [A, J]
Notes:
A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
B. The maintenance normally consists of 1 -2 annual service visits.
C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
D. Not considered relevant for small domestic turbines.
E. Based on information from manufacturers and resellers. The
F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
G. The service cost is assumed fixed to 100EUR/kW/y.
H. Domestic turbines have a maximum total height of 25 m according to Danish regulations.
J. No development in the capacity factor is expected, because no changing in the size limitation (legislation) is expected. And because location is crucial and one must expect the turbines is put up at the best positions already. But change in legislation i
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
NA. NA

## 4. Coal retrofitting
Technology |  | Coal power plant, supercritical - extraction - coal - medium
year |  | 2025 |  | 2025 | Ref | Ref | Average of 2020 and 2030 data in 2022 prices
est |  | ctrl |  | - | - | -
cat | par
Energy/technical data |  | wo CCS | with CCS
| Generating capacity for one unit [MW_e] | 500
| Electrical efficiency (net, name plate) [] | 50.25% | 37% | C | [8, 7, 9, 11] | [8, 7, 9, 11]
| Cb coefficient (50°C/100°C) | 0.925 |  | A
| Cv coefficient (50°C/100°C) | 0.15 |  |  | 1 | 1
| Technical lifetime [years] | 15 | 35 |  | 6 | 6
| Construction time [years] | 0.5 | 1 |  | [2, 3, 3] | [2, 3, 3]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% |  | D | 14 | 14
| Secondary regulation (of full load, per minute) [] | 4% |  | D | 14 | 14
| Minimum load (of full load) [] | 15% |  |  | [10, 14] | [10, 14]
Environment
| SO2 (degree of desulphuring) [] | 97% |  | B | 5 | 5
| NOX [g/GJ_i] | 35 |  | B | [12, 5, 5, 5] | [12, 5, 5, 5]
| CH4 [g/GJ_i] | 1.5 |  |  | [13, 5, 5, 5] | [13, 5, 5, 5]
| N2O [g/GJ_i] | 0.8 |  |  | [13, 5, 5, 5] | [13, 5, 5, 5]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.1731 | 3.9 | J | [17, 18, 19, 20, 21, 22] | [17, 18, 19, 20, 21, 22]
| Variable O&M (*total) [EUR/MWh_e] | 3.3174 | 18.828 | J | [17, 18, 19, 20, 21, 22] | [17, 18, 19, 20, 21, 22]
| Fixed O&M (*total) [EUR/MW_e/y] | 35459.8717 | 43000 | J | [17, 18, 19, 20, 21, 22] | [17, 18, 19, 20, 21, 22]
Technology-specific data
| Availability [] | 80% | 80% | E | 7 | 7
Notes:
A. The Cb values have been calculated from the electricity efficiencies in condensation mode, the Cv values and a total efficiency (electricity plus heat) in full back-pressure mode of 90%. Cf. Annex 1.
B. The data for SO2 and NOx emissions assume flue gas desulphurisation (wet gypsum) and DeNOx equipment of the "high dust" SCR type.
C. Supercritical in 2010 and ultra-supercritical from 2020.
D. Please refer to section 'Regulation ability' in the above qualitative description.
E. Outage rates are generally about 5% for plants that are 10-20 years old. Unless the plant is refurbished, the rate increases to 20% for plants that are 40 years old (ref. 7)
F. It is assumed that the cost is falling by 0.2 % p.a. Defaltor 2011-2015: 1.059
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Elsam, November 2003
2. Elsam's and Elkraft's update of the Danish Energy Agency's 'Teknologidata for el- og varmeproduktionsanlæg', December 1997
3. Eltra, September 2003
5. Danish Energy Agency, 2009.
6. "Projected costs of generating electricity", International Energy Agency (IEA), 2005.
7. "Energy technology perspectives 2008", International Energy Agency, 2008.
8. Danish Energy Agency, 2008. Measured data (1994-2006) from newest power plants in Denmark.
9. Own estimate by Danish Energy Agency and Energinet.dk, 2011.
10. Energinet.dk, 2009
11. www.ad700.dk
12. "En opdateret analyse af Danmarks muligheder for at reducere emissionerne af NOx" (Updated analysis of Denmark's options to reduce NOx emissions; in Danish), Danish Environmental Protection Agency, 2009.
13. National Environmental Research Institute, Denmark, 2009 (data from 2007).
14. DONG Energy, 2009.
15. "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
16. "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
17. The IEA World Energy Outlook 2014 coal fired Ultra-supercritical power plants in Europe. Values used are the projection for 2020.
18. The IEA Projected Cost of Generating Electricity 2015 for coal fired power plants. Here both the 'world median' is used, and data from recently commissioned plants in the Netherlands. The three units in the Netherlands are chosen because of the proximity to Denmark, because the socio-economic parameters (labour cost etc) are assumed to be similar and because the units are new (all from 2015).
19. EIA Updated Capital Cost Estimates for Utility Scale Electricity Generating Plants 2013 for pulverizes coal fired advanced single units.[1]
20. Aggregated data from different projects on existing units that Ea Energy Analyses have been working on since 2010. Data is used for estimating O&M costs.
21. IEA( 2016),Energy Technology Perspectives
22. E.S. Rubin et al. / Energy Policy 86 (2015) page 198-218, A review of learning rates for electricity supply technologies
Note on C10: Michael Clemens Bloch: Adjusted to the life time extension.
Note on C22: Michael Clemens Bloch: Adjusted to the cost of life time extension.
Note on J22: Michael Clemens Bloch: Adjusted to the cost of life time extension.

## 5.a. Bat, Li-Ion Utility scale
| Technology | Lithium-ion utility scale battery
|  | 2025 | 2025 |  | Note | Ref
| Energy/technical data |  | Lower | Upper
| Form of energy stored | Electricity
| Application | System, power- and energy-intensive
| Energy storage capacity for one unit (MWh) | 132 | 16 | 24 | A | [1, 2]
| Output capacity for one unit (MW) | 33 | 4 | 6 | A,B | [1,2]
| Input capacity for one unit (MW) | 5 | 4 | 6 | A,B | [1, 2]
| Electrical efficiency (net, name plate) [] | 91% | 0.9 | 0.92 | C | [3,6,7,9]
| Round trip efficiency (%) DC | 95% | 0.95 | 0.96 | C | [3,6,7,9]
| - Charge efficiency (%) | 98% | 0.98 | 0.985 | D | [4]
| - Discharge efficiency (%) | 97% | 0.97 | 0.98 | D | [4]
| Energy losses during storage (%/day) | 0.1 | 0.05 | 0.2 | E | [18,10,11]
| Forced outage (%) | 0.38 | 0.2 | 0.5 | F
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.25 | F
| Technical lifetime [years] | 20 | 15 | 25 | G | [3,5,8,14]
| Construction time (years) | 0.2 | 0.2 | 0.25 |  | [13]
Regulation ability
| Response time from idle to full-rated discharge (sec) | <0.08 | <0.08 | <0.08 | H | [12]
| Response time from full-rated charge to full-rated discharge (sec) | <0.08 | <0.08 | <0.08 | H | [12]
Financial data
| Nominal investment (*total) [MEUR/MWh] | 0.33432 | 0.30089 | 0.36776 |  | [1,2]
| Fixed O&M (*total) [EUR/MW_e/y] | 596.0844 | 0.45 | 0.54 | M | [7]
| Variable O&M (*total) [EUR/MWh_e] | 2.2077 | 0.4 | 5.6 | N | [14]
0.23872
0.24892
0.24892
** 1 € = 1.14 US$
Notes
A. One unit defined as a 20-MWh system, consisting of 5 4 MWh battery containers
B. Power input/output are set to 0.5/3 times the energy capacity as it is the standard grid-connected LIBs designed for power purposes [2,14]. It is noted that the power capacity is strongly dependent on the battery type and chemistry.
C. The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D. The C-rate is 0.5 during charge and up to 6 during discharge for the Samsung SDI batteries [2,14]. The presented conversion efficiencies assume average discharge C-rates in 2015-2020 around 3 and charge C-rates around 0.5.
E. Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0.05% and 0.20% a day in 2016 and are expected to stay flat to 2030.
F. It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
G. Current state-of-the-art NMC LIB has 20 years lifetime. The NMC lifetime is expected to reach LTO lifetime by 2020 and 30 years lifetime for grid-connected LIBs in 2040 and 2050 as photovoltaic power systems have today [3,5,8,14].
H. The response time is obtained from simulated response time experiments with hardware in the loop [53].
I. The system specific forecasts includes rack, TMS, BMS, EMS and PCS (Figure 5). The forecast is calculated as the sum of the PCS, the battery cell, and other costs. The system specific forecast is exclusive power cables to the site and entrepreneur work for installation of the containers [44,48]. The specific investment cost is the total cost of a 1MWh : 3MW (3C) battery, which is the typical grid scale battery defined in note A. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
J. The battery pack cost forecast is provided in Figure 8 and the related text [44].
K. Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references [54–56] and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. Inverter replacement is expected every 10 years. The bidirectional inverter given here has more or less the same charge and discharge capacity (MW).
L. Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature [22,40,54].
M. Fixed O&M is assumed to be constant, although the O&M may depend on the application [22].
N. Variable O&M is assumed to be 2.1 €/MWh in 2015 with a range of 0.4 – 5.6 [55].
O. Since multi-MWh LIB systems are scalar, the energy storage expansion cost is here estimated to be equal to the energy component plus the “other costs” [44,48].
P. Since multi-MW LIB systems are scalar, the capacity expansion cost equals the capacity component cost [54–56].
Q. The alternative investment cost in M€2015/MW is specified for a 4C, 0.25 h system as for the Laurel Mountain, West Virginia, USA grid-scale LIB storage system [41]. I.e. the alternative investment cost is 25% of the energy storage expansion cost plus the PCS cost [41,44,48,54–56].
R. Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
S. Specific power, power density, Specific energy and energy density is provided for discharge mode, starting with the values provided in the section “Typical characteristics and capacities”. A charge/discharge conversion factor of 12 can be derived from this section. For this datasheet, a discharge rate of 3C is assumed. The expected development depends on the successive R&D progress as indicated in the section “Research and development perspectives” [2,24].
References
[1] | https://www.nrel.gov/docs/fy23osti/85332.pdf
[2] | https://www.nrel.gov/docs/fy22osti/83586.pdf
[3] | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
[4] | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
[5] | StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
[6] | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
[7] | Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
[8] | Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
[9] | Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
[10] | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[11] | H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
[12] | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
[13] | Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
[14] | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011

## 5.b. Bat, Li-Ion community sca
| Technology | Lithium-ion NMC battery (Community-scale)
|  | 2025 | 2025 |  | Note | Ref
| Energy/technical data |  | Lower | Upper
| Form of energy stored | Electricity
| Application | System, power- and energy-intensive
| Energy storage capacity for one unit (MWh) | 1.2 | 1 | 9 | A | [1, 2]
| Output capacity for one unit (MW) | 0.3 | 0.3 | 3 | A,B | [1,2]
| Input capacity for one unit (MW) | 0.3 | 2.7 | 3.5 | A,B | [1, 2]
| Electrical efficiency (net, name plate) [] | 90% | 85% | 98% | C | [3,6,7,9]
| Round trip efficiency (%) DC | 95 | 95 | 96 | C | [3,6,7,9]
| - Charge efficiency (%) | 98% | 98 | 98.5 | D | [4]
| - Discharge efficiency (%) | 97% | 97 | 98 | D | [4]
| Energy losses during storage (%/day) | 0.1 | 0.05 | 0.2 | E | [18,10,11]
| Forced outage (%) | 0.38 | 0.2 | 0.5 | F
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.25 | F
| Technical lifetime [years] | 10 | 5 | 15 | G | [3,5,8,14]
| Construction time (years) | 0.2 | 0.2 | 0.25 |  | [13]
Regulation ability
| Response time from idle to full-rated discharge (sec) | <0.08 | <0.08 | <0.08 | H | [12]
| Response time from full-rated charge to full-rated discharge (sec) | <0.08 | <0.08 | <0.08 | H | [12]
Financial data
| Nominal investment (*total) [MEUR/MWh] | 0.41413 | 0.33131 | 0.49696 | I | [1,2,15]
| Fixed O&M (*total) [EUR/MW_e/y] | 744.4636 | 595.5709 | 893.3564
| Variable O&M (*total) [EUR/MWh_e] | 2.7573 | 2.2058 | 3.3087
| OPEX [kEUR/MWh/year] | 0.97 | 0.9 | 1.05 | M | [15]
Notes
A. One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values for 2015-2030 are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [2,14]. This unit of 3.2MWh/9.6MW (3C) is a typical size grid scale battery. The Specific investment cost under financial data is provided for a 1MWh : 3MW (3C) battery. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
B. Power input/output are set to 0.5/3 times the energy capacity as it is the standard grid-connected LIBs designed for power purposes [2,14]. It is noted that the power capacity is strongly dependent on the battery type and chemistry.
C. The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D. The C-rate is 0.5 during charge and up to 6 during discharge for the Samsung SDI batteries [2,14]. The presented conversion efficiencies assume average discharge C-rates in 2015-2020 around 3 and charge C-rates around 0.5.
E. Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0.05% and 0.20% a day in 2016 and are expected to stay flat to 2030.
F. It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
G. Current state-of-the-art NMC LIB has 20 years lifetime. The NMC lifetime is expected to reach LTO lifetime by 2020 and 30 years lifetime for grid-connected LIBs in 2040 and 2050 as photovoltaic power systems have today [3,5,8,14].
H. The response time is obtained from simulated response time experiments with hardware in the loop [53].
I. The system specific forecasts includes rack, TMS, BMS, EMS and PCS (Figure 5). The forecast is calculated as the sum of the PCS, the battery cell, and other costs. The system specific forecast is exclusive power cables to the site and entrepreneur work for installation of the containers [44,48]. The specific investment cost is the total cost of a 1MWh : 3MW (3C) battery, which is the typical grid scale battery defined in note A. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
J. The battery pack cost forecast is provided in Figure 8 and the related text [44].
K. Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references [54–56] and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. Inverter replacement is expected every 10 years. The bidirectional inverter given here has more or less the same charge and discharge capacity (MW).
L. Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature [22,40,54].
M. Fixed O&M is assumed to be constant, although the O&M may depend on the application [22].
N. Variable O&M is assumed to be 2.1 €/MWh in 2015 with a range of 0.4 – 5.6 [55].
O. Since multi-MWh LIB systems are scalar, the energy storage expansion cost is here estimated to be equal to the energy component plus the “other costs” [44,48].
P. Since multi-MW LIB systems are scalar, the capacity expansion cost equals the capacity component cost [54–56].
Q. The alternative investment cost in M€2015/MW is specified for a 4C, 0.25 h system as for the Laurel Mountain, West Virginia, USA grid-scale LIB storage system [41]. I.e. the alternative investment cost is 25% of the energy storage expansion cost plus the PCS cost [41,44,48,54–56].
R. Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
S. Specific power, power density, Specific energy and energy density is provided for discharge mode, starting with the values provided in the section “Typical characteristics and capacities”. A charge/discharge conversion factor of 12 can be derived from this section. For this datasheet, a discharge rate of 3C is assumed. The expected development depends on the successive R&D progress as indicated in the section “Research and development perspectives” [2,24].
references
[1] | https://www.nrel.gov/docs/fy23osti/85332.pdf
[2] | https://www.nrel.gov/docs/fy22osti/83586.pdf
[3] | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
[4] | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
[5] | StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
[6] | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
[7] | Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
[8] | Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
[9] | Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
[10] | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[11] | H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
[12] | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
[13] | Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
[14] | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
[15] | https://arena.gov.au/assets/2020/08/community-batteries-cost-benefit-analysis.pdf

## 7.a. Wood pellets, CHP medium
Technology |  | Biomass CHP - back pressure - wood pellets - medium
year |  | 2025 | 2025 | 2025 | Note | Ref
est |  | ctrl | lower | upper | - | -
cat | par | [5 empty] | Average 2020 and 2030 in 2022 prices
Energy/technical data
| Generating capacity for one unit [MW_e] | 24.715 | 23.84 | 33.36 | A
| Electrical efficiency (net, annual average) [] | 29.35% | 26% | 40% | [A, H, F] | 1
| Electrical efficiency (net, name plate) [] | 30.89% | 29% | 42% | [A, H, F] | 1
| Cb coefficient (40°C/80°C) | 0.46 | 0.44 | 0.62
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | I
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.514% | 1.915% | 2.942% |  | 1
| Forced outage [] | 3% | 3% | 3%
| Planned outage [weeks per year] | 3 | 2.55 | 3.45
| Technical lifetime [years] | 25 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.18 | 0.16 | 0.21
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15%
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 95.62% | 99.12% | F | [1, 2]
| NOX [g/GJ_i] | 45 | 40 | 50 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 3 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.1 | 2 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.1849 | 2.3887 | 3.9811 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.0327 | 1.5245 | 2.5409 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.1522 | 0.86417 | 1.4403 | K
| Variable O&M (*total) [EUR/MWh_e] | 2.0164 | 1.5123 | 2.5205 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 130983.8884 | 98237.9163 | 163729.8604 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 69.19% | 47% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 67.64% | 44% | 71% | [A, H, F] | 1
| Nominal investment (*total) [MEUR/MW_i] | 0.98374 | 0.8188 | 1.1591 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.62503 | 0.51042 | 0.74436 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.35328 | 0.30838 | 0.42535 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.61959 | 0.48915 | 0.70183 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 40490.87 | 34134.2642 | 47213.7487
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1% | 11% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent back pressure steam turbine. It is possible to pulverize wood pellets and use it for suspension firing but it has not been possible to find an appropriate reference. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. SNCR is assumed at NOx emissions at no less than 40 g/GJ. At lower NOx-levels it is chosen to include a tail-end SCR catalyst with slight adverse effect on electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 7.b. Wood pellets, CHP small
Technology |  | Biomass CHP - boiler - wood pellets - small
year |  | 2025 | 2025 | 2025 | Note | Ref
est |  | ctrl | lower | upper | - | -
cat | par | [5 empty] | Average 2020 and 2030 in 2022 prices
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.085 | 3 | 3.12 | A
| Electrical efficiency (net, annual average) [] | 14.66% | 13% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 15.43% | 15% | 16% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.185 | 0.18 | 0.19
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | I
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.291% | 1.744% | 2.503% |  | 1
| Forced outage [] | 3% | 3% | 3%
| Planned outage [weeks per year] | 3 | 2.55 | 3.45
| Technical lifetime [years] | 25 | 20 | 35 |  | 1
| Construction time [years] | 1 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.49 | 0.41 | 0.56
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 |  | 1
Environment |  | 0
| SO2 (degree of desulphuring) [] | 98.25% | 95.62% | 99.12% | F | 1
| NOX [g/GJ_i] | 45 | 40 | 70 | F | 1
| CH4 [g/GJ_i] | 0 | 0 | 0 | F | 1
| N2O [g/GJ_i] | 1 | 1 | 3 | F | 1
| Particles [g/GJ_i] | 0.3 | 0.1 | 2 | F | 1
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.6271 | 2.7203 | 4.5339 | [E, J, K, N] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 4.1904 | 3.1428 | 5.238 | K
| Nominal investment (installation) [MEUR/MW_e] | 2.2338 | 1.6753 | 2.7922 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.223 | 3.1673 | 5.2788 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 289142.8573 | 216857.143 | 361428.5716 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 84.18% | 74% | 86% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 83.41% | 72% | 85% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 0.98917 | 0.86133 | 1.1697 | [E, J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.64677 | 0.56359 | 0.76563 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.34241 | 0.29774 | 0.40408 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.6522 | 0.48915 | 0.72309 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 44567.1321 | 37962.406 | 51467.2395
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1% | 11% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the thermail input.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
N. Indications from interviewees indicate that straw boiler and ORC are equally priced and that an ORC unit is 1.6 MEUR/MW_e. Totals 3.2 MEUR/MW_e, we are adding a bit to cover transport costs for the ORC and for uncertainy but keeping same difference between straw and pellets as before. No consequential adjustments of other financial data made, yet.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 7.c. Wood Chips, CHP Medium
Technology |  | Biomass CHP - back pressure - wood chips - medium
year |  | 2025 | 2025 | 2025 | Note | Ref
est |  | ctrl | lower | upper | - | -
cat | par | [5 empty] | Average 2020 and 2030 in 2022 prices
Energy/technical data
| Generating capacity for one unit [MW_e] | 23.815 | 22.17 | 31.78 | A
| Electrical efficiency (net, annual average) [] | 28.28% | 24% | 38% | [A, H, F] | 1
| Electrical efficiency (net, name plate) [] | 29.77% | 27% | 40% | [A, H, F] | 1
| Cb coefficient (40°C/80°C) | 0.37 | 0.34 | 0.49
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | I
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.962% | 2.185% | 3.271% |  | 1
| Forced outage [] | 3% | 3% | 3%
| Planned outage [weeks per year] | 3 | 2.55 | 3.45
| Technical lifetime [years] | 25 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.21 | 0.18 | 0.24
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20%
| Warm start-up time [hours] | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 94.92% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 50 | 40 | 60 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 2 | 1 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 1 | 1 | 3 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.1 | 2 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.7502 | 2.8126 | 4.6877 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.511 | 1.8832 | 3.1387 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.2392 | 0.92939 | 1.549 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.8698 | 3.6523 | 6.0872 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 157071.9657 | 117803.9743 | 196339.9571 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.67% | 49% | 86% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 81.18% | 46% | 84% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.1142 | 0.93577 | 1.3186 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.75003 | 0.61676 | 0.8826 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.36958 | 0.31901 | 0.43598 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.4457 | 1.0102 | 1.5951 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 46849.8389 | 39663.8024 | 54763.695
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.010634 | 0.010634 | 0.021267 | K
| Steam reheat | 0 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.22 | 0 | 0.22 | [C, L]
| Flue gas condensation | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1% | 26% | C | 1
Notes:
A. The boiler in the plant is a grate fired boiler producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel. It is to be expected that it is necessary with a specific DeNOx plant (SNCR might not be sufficient). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. It is to be expected that necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 40 g/GJ in which case SCR is used with slight adverse effect on electricity efficiency. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 7.d. Wood Chips, CHP small
Technology
year |  | 2025 | 2025 | 2025 | Note | Ref
est |  | ctrl | lower | upper | - | -
cat | par | Biomass CHP - back pressure - wood chips - small |  |  |  |  | Average 2020 and 2030 in 2022 prices
Energy/technical data
| Generating capacity for one unit [MW_e] | 2.935 | 2.85 | 2.97 | A
| Electrical efficiency (net, annual average) [] | 13.96% | 12% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 14.69% | 14% | 15% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.15 | 0.15 | 0.15
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | I
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.735% | 2.08% | 2.989% |  | 1
| Forced outage [] | 3% | 3% | 3%
| Planned outage [weeks per year] | 3 | 2.55 | 3.45
| Technical lifetime [years] | 25 | 20 | 35 |  | 1
| Construction time [years] | 1 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.68 | 0.58 | 0.78
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 94.92% | 98.98% | F | [1, 2]
| NOX [g/GJ_i] | 50 | 40 | 80 | F | [1, 2]
| CH4 [g/GJ_i] | 9 | 4 | 16 | F | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 3 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.1 | 2 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.7684 | 2.8263 | 4.7105 | [E, J, K, N] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 4.1524 | 3.1143 | 5.1904 | K
| Nominal investment (installation) [MEUR/MW_e] | 2.5327 | 1.8995 | 3.1659 | K
| Variable O&M (*total) [EUR/MWh_e] | 10.0439 | 7.5329 | 12.5549 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 301099.8927 | 225824.9195 | 376374.8659 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 97.29% | 73% | 98% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 96.55% | 71% | 98% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 0.98374 | 0.86133 | 1.1591 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.61416 | 0.53169 | 0.72309 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.36958 | 0.32965 | 0.43598 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.4783 | 1.0102 | 1.627 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 44241.0311 | 37537.0569 | 50829.2159
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.021267 | 0.021267 | 0.021267 | K
| Steam reheat | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.25 | 0 | 0.25 | [C, L]
| Flue gas condensation | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1% | 26% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. Cv=1 describes turbine by-pass operation. During operation the turbine can be by-passed fully or partly for direct district heating production, at operator choice.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
N. Indications from interviewees indicate that straw boiler and ORC are equally priced and that an ORC unit is 1.6 MEUR/MW_e. Totals 3.2 MEUR/MW_e, we are adding a bit to cover transport costs for the ORC and for uncertainy but keeping same difference between straw and chips as before. No consequential adjustments of other financial data made, yet.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal model and evaluation based on either existing projects, supplier offers, or pre-project studies.
2. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 7.e. Straw, CHP Medium
Technology |  | Biomass CHP - back pressure - straw - medium
year |  | 2025 | 2025 | 2025 | Note | Ref | Average 2020 and 2030 in 2022 prices
est |  | ctrl | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 25.325 | 23.67 | 25.72 | A
| Electrical efficiency (net, annual average) [] | 30.12% | 26% | 31% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.71% | 29% | 33% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.46 | 0.43 | 0.47
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | I
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.849% | 2.091% | 3.168% |  | 1
| Forced outage [] | 4% | 4% | 4%
| Planned outage [weeks per year] | 4 | 3.4 | 4.6
| Technical lifetime [years] | 25 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.28 | 0.24 | 0.32
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.72% | 90.9% | 99.82% | F | [1, 2]
| NOX [g/GJ_i] | 60 | 20 | 90 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 3 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.1 | 2 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.7828 | 2.8371 | 4.7285 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.2881 | 1.7161 | 2.8602 | [J, K] | 1
| Nominal investment (installation) [MEUR/MW_e] | 1.4946 | 1.121 | 1.8683 | [J, K] | 1
| Variable O&M (*total) [EUR/MWh_e] | 2.2773 | 1.708 | 2.8466 | L | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 150549.9464 | 112912.4598 | 188187.433 | J | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.11% | 56% | 74% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 68.52% | 53% | 72% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.1957 | 1.0102 | 1.4462 | [J, K] | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.47285 | 0.41472 | 0.56359 | K
| Nominal investment (equipment) [MEUR/MW_i] | 0.72286 | 0.59549 | 0.89323 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.71742 | 0.54232 | 0.80816 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 47719.4415 | 40408.1633 | 56358.754 | J
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.069119 | 0.063802 | 0.08507 | K
| Steam reheat | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 7.f. Straw, CHP Small
Technology
year |  | 2025 | 2025 | 2025 | Note | Ref
est |  | ctrl | lower | upper | - | -
cat | par | [5 empty] | Average 2020 and 2030 in 2022 prices
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.055 | 2.97 | 3.09 | A
| Electrical efficiency (net, annual average) [] | 14.51% | 13% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 15.27% | 14% | 16% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.18 | 0.17 | 0.18
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | I
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.374% | 1.807% | 2.594% |  | 1
| Forced outage [] | 4% | 4% | 4%
| Planned outage [weeks per year] | 4 | 3.4 | 4.6
| Technical lifetime [years] | 25 | 20 | 35 |  | 1
| Construction time [years] | 1 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.98 | 0.84 | 1.13
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 50% | 50% | 50% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.72% | 90.9% | 99.82% | F | 1
| NOX [g/GJ_i] | 60 | 50 | 90 | F | 1
| CH4 [g/GJ_i] | 9.5 | 4 | 16 | F | 1
| N2O [g/GJ_i] | 1 | 1 | 3 | F | 1
| Particles [g/GJ_i] | 0.3 | 0.1 | 2 | F | 1
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 4 | 3 | 5 | [E, J, K,N] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 3.9947 | 2.9961 | 4.9934 | K
| Nominal investment (installation) [MEUR/MW_e] | 3.0817 | 2.3112 | 3.8521 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.9024 | 3.6768 | 6.128 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 334253.491 | 250690.1183 | 417816.8638 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 86.31% | 73% | 88% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 85.55% | 72% | 87% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.0816 | 0.9464 | 1.276 | [E, J, K] | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.46741 | 0.41472 | 0.55295 | K
| Nominal investment (equipment) [MEUR/MW_i] | 0.61416 | 0.53169 | 0.72309 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.75003 | 0.54232 | 0.82943 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 50980.4511 | 43385.6069 | 58804.5113 | J
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.079753 | 0.074436 | 0.095704 | K
| Steam reheat | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1% | 14% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
N. Indications from interviewees indicate that straw boiler and ORC are equally priced and that an ORC unit is 1.6 MEUR/MW_e. Totals 3.2 MEUR/MW_e, we are adding a bit to cover transport costs for the ORC and for uncertainy. No consequential adjustments of other financial data made, yet.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. NOTICE: There are to our knowledge no references on ORC plants running on straw.

## 8.a. Small hydro, RoR
| Technology | Hydro power plant - Medium (25-100 MW)
|  | 2025 | 2025 |  | Note | Ref
| Energy/technical data |  | Lower | Upper
| Generating capacity for one unit [MW_e] | 50 | 10 | 100 |  | 2
| Generating capacity for total power plant [MW_e] | 50 | 20 | 100 |  | 2
| Electrical efficiency (net, name plate) [] | 95% | 85 | 97 | A | 1
| Electricity efficiency, net (%), annual average | 95 | 85 | 97 | A | 1 |  | Type | Capacity (international classification)
| Forced outage (%) | 4 | 2 | 10 |  | 1 |  | Large hydropower | > 100 MW
| Planned outage (weeks per year) | 6 | 3 | 10 |  | 1 |  | Medium hydropower | 25 – 100 MW
| Technical lifetime [years] | 50 | 40 | 90 |  | 1 |  | Small hydropower | 1- 25 MW
| Construction time [years] | 2 | 2 | 6 |  | 1 |  | Mini/micro/pico hydropower | < 1000 kW
| Space requirement [1000 m2/MW_e] | 14 | 10.5 | 17.5 | B |  |  | Ref: 1. International Finance Corporation, Hydroelectric power, 2015
Additional data for non thermal plants
| Capacity factor (%), theoretical | 45.3333 | 30 | 95 |  | 8,9,11 |  | Table 8.5. Hydropower plant categories
| Capacity factor (%), incl. outages | 43.3333 | 50 | 95 |  | 8,9,11 |  | Micro | 1 kW to 100 kW
| Ramping configurations | [6 empty] | Mini | 100 kW to 1 MW
| Ramping (% per minute) | 50 | 30 | 100 |  | 3 |  | Small | 1 MW to 10–30 MW
| Minimum load (% of full load) | 0 | 0 | 0 |  | 3 |  | Large | Above 10–30 MW
| Warm start-up time [hours] | 0.1 | 0 | 0.3 |  | 3 |  | Source: UNDP/World Bank6
| Cold start-up time [hours] | 0.1 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0
| SO2 (degree of desulphuring, %) | 0
| NOX (g per GJ fuel) | 0
| CH4 (g per GJ fuel) | 0
| N2O (g per GJ fuel) | 0
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.302 | 1.3208 | 4.9057 | C,D,E | 4,5,6,7 | 3.0377
| - of which equipment | 30% | 20% | 50% |  | 7
| - of which installation | 70% | 50% | 80% |  | 7
| Fixed O&M (*total) [EUR/MW_e/y] | 60503.0095 | 45400 | 75600 | B,E | 4,5,7 | 55660.3774
| Variable O&M (*total) [EUR/MWh_e] | 0 | 0 | 0 | B,E | 1
| Start-up costs [EUR/MWe/start-up] | - | - | -
References:
1 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
2 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
5 | IEA, World Energy Outlook, 2015.
6 | IEA, Projected Costs of Generating Electricity, 2020.
7 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
8 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
9 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
11 | NLRE ATB 2024
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
E | Euro dollar conversion ratio: 0,94
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Knud Johansen Hej Knud, de her skal vel rettes op i forhold til størrelserne ? Data er taget direkte fra det indonesiske katalog- som måske er kopieret fra et andet katalog - vi så ikke på dem i forbindelse med opdateringen i 2023. Dog fik DEA nogle data fra PLN (Den Indonesiske el leverandør) og opdaterede lidt ..? Reply: Har vi data fra Ethiopien som passer meget godt med UA? Reply: Hej Rikke - lad os bruge de data du har fra PLN da jeg ikke har bedre data lige nu.
Note on L7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which classification to iuse for this report?
Note on I28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hvor kommer dette tal fra?
Note on C31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Knud Johansen tjek lower og upper er lavere end "bedste bud ( flyttet til I) Reply: Er ikke lige helt med på havd du spørger om? Reply: Data der står I celle E31 som er vurderest at være høje grænse I forhold til usikkerheden er lavere end middelskønnet I celle c31 Reply: Hvis der burges samme formel for Medium som for Micro hydro -0.25 /+0.25 så ser grænserne rigtige ud. Det er samme principper der er brugt i Ethiopian TC.
Note on I31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hvor kommer dette tal fra? Reply: Hej Knud, det var den forhenværende O&M som blev devideret med konverteringsfaktoren mellem Euro og Dollar. Reply: OK - tak for afklaringen

## 8.b. Micro hydro, RoR
| Technology | Hydro power plant - Mini/micro system (< 1 MW)
|  | 2025 | 2025 |  | Note | Ref
| Energy/technical data |  | Lower | Upper
| Generating capacity for one unit [MW_e] | 5 | 1 | 10 |  | 1,8
| Generating capacity for total power plant [MW_e] | 5 | 1 | 10 |  | 1,8
| Electrical efficiency (net, name plate) [] | 80% | 70 | 90 | A | 7 |  | Type | Capacity (international classification)
| Electricity efficiency, net (%), annual average | 80 | 70 | 90 | A | 7 |  | Large hydropower | > 100 MW
| Forced outage (%) | 4 | 2 | 10 |  |  |  | Medium hydropower | 25 – 100 MW
| Planned outage (weeks per year) | 6 | 3 | 10 |  |  |  | Small hydropower | 1- 25 MW
| Technical lifetime [years] | 50 | 40 | 90 | B |  |  | Mini/micro/pico hydropower | < 1000 kW
| Construction time [years] | 2 | 1.5 | 3 |  |  |  | Ref: 1. International Finance Corporation, Hydroelectric power, 2015
Space requirement [1000 m2/MW_e]
Additional data for non thermal plants
| Capacity factor (%), theoretical | 45.3333 | 30 | 95 |  | 2,10,11 |  | Table 8.5. Hydropower plant categories
| Capacity factor (%), incl. outages | 43.3333 | 50 | 95 |  | 2,10,11 |  | Micro | 1 kW to 100 kW
| Ramping configurations | [6 empty] | Mini | 100 kW to 1 MW
| Ramping (% per minute) | - | - | - | E |  |  | Small | 1 MW to 10–30 MW
| Minimum load (% of full load) | - | - | - | E |  |  | Large | Above 10–30 MW
| Warm start-up time [hours] | - | - | - | E |  |  | Source: UNDP/World Bank6
| Cold start-up time [hours] | - | - | - | E
Environment
| PM 2.5 (gram per Nm3) | 0
| SO2 (degree of desulphuring, %) | 0
| NOX (g per GJ fuel) | 0
| CH4 (g per GJ fuel) | 0
| N2O (g per GJ fuel) | 0
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.7688 | 1.2 | 4 | D,F,G | 1,5,9 | 2.5472
| - of which equipment | 30% | 20% | 50% |  | 9
| - of which installation | 70% | 50% | 80% |  | 9
| Fixed O&M (*total) [EUR/MW_e/y] | 54350.1611 | 40800 | 67900 | C,G | 1,5,9 | 50000
| Variable O&M (*total) [EUR/MWh_e] | 0.51274 | 0.38455 | 0.64092 | C,G | 1,5 | 0.4717
| Start-up costs [EUR/MWe/start-up] | - | - | -
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IEA, World Energy Outlook, 2015.
5 | Learning curve approach for the development of financial parameters.
6 | IEA, Projected Costs of Generating Electricity, 2020.
7 | IFC, 2015, "Hydroelectric Power - A guide for developers and investers".
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
9 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
10 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
11 | NLRE ATB 2024
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properbly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive and the uncertainty can be even more extreme than listed. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | It is assumed that micro and mini hydro do not have a reservior (run-of-river) and therefor is not capable of regulation. The possibility of a turbine bypass could give the possibility of down regulation.
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
G | Euro dollar conversion ratio: 0,94
Note on C28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Knud Johansen undre mig at micro er billigere pr MW end small? Kan være pga af den lavere effektivitet? Reply: Hej Rikke - ja, det lyder rigtigt. Reply: micro anlæg er primært asynkrone - dvs. der benyttes billigere mekaniske og elektriske komponenter

## 8.c Retrf Hydro power,dams+PHS
Technology | Retrofit Hydro power (dams) incl. pumped hydro storage (>100 MW)
| 2023 | 2023 |  | Note | Ref
Energy/technical data |  | Lower | Upper
Generating capacity for one unit [MW_e] | 100 | 30 | 200 |  | 2
Generating capacity for total power plant [MW_e] | 600 | 100 | 1200 |  | 2 |  | Type | Capacity (international classification)
Electrical efficiency (net, name plate) [] | 35 | 20 | 40 |  | 1 |  | Large hydropower | > 100 MW
Electricity efficiency, net (%), annual average | 30 | 20 | 40 |  | 1 |  | Medium hydropower | 25 – 100 MW
Forced outage (%) | 3 | 1 | 5 |  | 1 |  | Small hydropower | 1- 25 MW
Planned outage (weeks per year) | 6 | 3 | 10 |  | 1 |  | Mini/micro/pico hydropower | < 1000 kW
Technical lifetime [years] | 60 | 40 | 90 |  | 1 |  | Ref: 1. International Finance Corporation, Hydroelectric power, 2015
Construction time [years] | 2 | 1 | 3 |  | 1
Space requirement [1000 m2/MW_e] | 15 | 10 | 20
Additional data for non thermal plants | [6 empty] | Table 8.5. Hydropower plant categories
Capacity factor (%), theoretical | 50 | 30 | 95 |  | 8,9 |  | Micro
Capacity factor (%), incl. outages | 48 | 30 | 93 |  | 8,9 |  | Mini
Ramping configurations | [6 empty] | Small
Ramping (% per minute) | 60 | 50 | 100 |  | 3 |  | Large | 1 kW to 100 kW
Minimum load (% of full load) | 8 | 0 | 10 |  | 3 |  | Source: UNDP/World Bank6 | 100 kW to 1 MW
Warm start-up time [hours] | 0.3 | 0 | 0,4 |  | 3 |  |  | 1 MW to 10–30 MW
Cold start-up time [hours] | 0.3 | 0 | 0,4 |  | 3 |  |  | Above 10–30 MW
Environment
PM 2.5 (gram per Nm3) | 0 | 0
SO2 (degree of desulphuring, %) | 0 | 0
NOX (g per GJ fuel) | 0 | 0
CH4 (g per GJ fuel) | 0 | 0
N2O (g per GJ fuel) | 0 | 0
Financial data
Nominal investment (*total) [MEUR/MWh] | 2 | 1.3208 | 4.9057 | C,D,E | 4,5,6,7 | Data are for newbuild - no data for retrofit avaiable
- of which equipment | 40 | 20% | 50% |  | 7
- of which installation | 70 | 50% | 80% |  | 7
Fixed O&M (*total) [EUR/MW_e/y] | 50 | 45 | 75 | B,E | 4,5,7
Variable O&M (*total) [EUR/MWh_e] | 20 | 15 | 25 | B,E | 1
Start-up costs [EUR/MWe/start-up] | - | - | -
References:
1 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
2 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
5 | IEA, World Energy Outlook, 2015.
6 | IEA, Projected Costs of Generating Electricity, 2020.
7 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
8 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
9 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
E | Euro dollar conversion ratio: 0,94
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Knud Johansen Hej Knud, der er vist sket et eller andet ved de her data ? Eller er det for at indikere at det er "dummy" data ? Reply: Hej Rikke - det er rækkenumre som stod i tabellen. Jeg har ikke data for 2023, men flere af dem kan jeg måske finde - skal jeg forsøge at finde dem? Reply: skal jeg forsøge at finde data for 2023? Reply: så har jeg lagt mit estimat på 2023 data ind Reply: Hov nu er der "rigtige data igen ?