## 111 1 el Main distri50-60kVcabl
Table 1: Main distribution, 50/60 kV electricity
| Technology | Energy Transport Electricity Main distribution, electricity cables
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines 1-20 MW (%) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | A,B | 1,2,3,4
| Energy losses, lines 20-100 MW (%) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | A,B | 1,2,3,4
| Energy losses, lines above 100 MW (%) | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.5 | 0.15 | 0.5 | A,B | 1,2,3,4
| Energy losses, stations [Type 1] (%) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 | A,B | 1,2,3,4
| Energy losses, stations [Type 2] (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | A,B,S
| Auxiliary electricity consumption (% energy transmitted) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | A,B,S | 4
| Technical life time (years) | 40 | 40 | 40 | 40 | 35 | 40 | 40 | 50 | C | 5
| Typical load profile (-) | 45% | 45% | 45% | 45% | 45% | 45% | 42.3% | 54% | D
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 5 | 1 | 5 | E
Financial data
| Investment costs; single line, 0 - 50 MW (EUR/MW/m) | 6 | 6 | 6 | 6 | 5.4 | 6 | 4.86 | 6 | F,G | 6.7
| Investment costs; single line, 50-100 MW (EUR/MW/m) | 3.9 | 3.9 | 3.9 | 3.9 | 3.51 | 3.9 | 3.159 | 3.9 | H,G | 6.7
| Investment costs; single line, 100 - 250 MW (EUR/MW/m) | 3.1 | 3.1 | 3.1 | 3.1 | 2.79 | 3.1 | 2.511 | 3.1 | I,G | 6.7
| Investment costs; single line, 250-500 MW (EUR/MW/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 6
| Investment costs; single line, 500-1000 MW (EUR/MW/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 7
| Investment costs; single line, above 1000 MW (EUR/MW/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 8
| Reinforcement costs (EUR/MW) | 15800 | 15800 | 15800 | 15800 | 15073.2 | 15800 | 14379.8328 | 15800 | K,O | 6
| Investment costs; [type 1] station (EUR/MW) | 76000 | 76000 | 76000 | 76000 | 72504 | 76000 | 69168.816 | 76000 | L,O | 8
| Investment costs; [type 2] station (EUR/MW) | 4476 | 4476 | 4476 | 4476 | 4270.104 | 4476 | 4073.6792 | 4476 | M,O
| Investments, percentage installation | 42% | 42% | 42% | 42% | 37.37% | 42% | 32.96% | 42% | P | 6
| Investments, percentage materials | 58% | 58% | 58% | 58% | 58% | 62.63% | 58% | 67.04% | P | 6
| Fixed O&M (EUR/MW/km/year) | 22.1 | 21.7906 | 21.4855 | 21.1847 | 21.7022 | 22.1 | 20.928 | 22.1 | Q | 9
| Variable O&M (EUR/MWh/km) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | R
Technology specific data
References:
1 | U.S. Energy Information Administration (http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3)
2 | energinet.dk (http://www.energinet.dk/DA/KLIMA-OG-MILJOE/Energinetdks-miljoepaavirkninger/Miljoepaavirkninger-ved-transport-af-el/Sider/Tab-i-elnettet.aspx)
3 | Svenska Kraftnät, Nätuvecklingsplan 2016 – 2025, Oktober 2015 (http://www.svk.se/siteassets/om-oss/rapporter/natutvecklingsplan-2016-2025.pdf)
4 | International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
5 | Svenska Kraftnät, Technology (http://www.svk.se/en/grid-development/the-construction-process/technology/)
6 | EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7 | PEX Guiden, Ericsson
8 | Standard value list for the Swedish Energy Markets Inspectorate (2015 value) (http://ei.se/sv/el/Elnat-och-natprisreglering/forhandsreglering-av-elnatstariffer-ar-2016-2019/dokument-elnatsreglering/normvardeslista-elnat-2016-2019/)
9 | Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A | Energy losses are estimated from total energy loss on transmission levels in the voltage range 20kV to 130 kV in Sweden. Transmission lines/cables accounts for approximately 60% of the losses and transformers accounts for approximately 40%.
B | Development of energy loss over time depends on several factors. Today, transmission losses typically range between 1% to 3% in Denmark. The variation in transmission losses depends mainly on the amount of power transfer to neighboring countries. The trend in Denmark is towards increasing transfer and thus increasing losses. The uncertainty span for 2020 mainly takes changes in power transfer into account, where the lower bound corresponds to a reduction of power transfer to a 1998 level, and the upper bound corresponds to a continued increase in losses stemming from increased power transfer. Technology development with introduction of e.g. super conducting transformers and super conducting power lines could lead to reduced losses on transmission level. Other factors, such as load control/optimization could also reduce losses in generators due to increased load factor. This technology development is not anticipated to have effect before 2020, but is possible in a second upgrade of electricity system in 2050.
C | Cable life length depends on material characteristics and the thermal loading of the cable. Increasing cable area and thus reducing cable temperature leads to longer life length. Today, up to 40 years are realistic life length of a cable with moderate thermal loading. Technological development on cable materials is anticipated to give an increase in cable life length. This in combination with low thermal loadings could give life length of up to 50 years in the future.
D | Load profile varies significantly between different stations and cables and a general figure is given. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 20%.
E | Construction time ranges normally from 1 to 2 years. In technically complex projects and for long cable stretches, the construction time increases and could stretch up to 5 years.
F | Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2. For power range 0 - 50 MW the costs is calculated as the average cost of two cables types with cross section areas 240 mm2 and 630 mm2,, corresponding to power levels of 20-35 MW and 50-60 MW respectively. The cost per MV decreases with increasing power level. The interval 20-35 MW has a cost of 6,7 EUR/MW/m and the interval 50-60 MW a cost of 4,2 EUR/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9. Power level below 20MW is not considered for this voltage level.
G | Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
H | Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2.For power range 50-100 MW the costs is calculated as the average cost for three cables with cross section areas 630 mm2, 800mm2 and 1000 mm2, corresponding to power levels of 50-60 MW, 69 MW and 76 MW respectively. The cost per MV decreases with increasing power level. The power interval 50-60 MW has a cost of 4,2 EUR/MW/m, at power level of 69 MW the cost is 3,6 EUR/MW/m and at the power level 76 the cost is 3,4 EUR/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9.
I | Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 60 kV. Cost is calculated as the average cost between dense populated areas and city areas. Adjusting factors for each area are: dense populated: 0,94, and city: 1,06. For power range 100-250 MW the costs is given for a cable with cross section area of 1200 mm2, corresponding to a power level of 100 MW. Power levels above 100 MW are not considered for this voltage level.
J | Power levels above 100 MW are normally transported at higher voltage levels. In cases where it is motivated to transport higher power levels at 50/60 kV, this is done in parallele cable budles in the same shaft. The cost of two parallel cables can be calculated as the double cost of one cable reduced with 60 800 EUR per kilometer.
K | Reinforcement costs depends on where bottlenecks are situated in the grid. Here the reinforcement cost is given for an upgrade of transformer capacity by 40 MVA. Reinforcement of line/cable capacity is in parity with the investment cost in described in row 18 - 20 and depends on power level and cable length.
L | Station cost is based on a 40 MW station with 2 x 20 MVA transformers (72/12 kV). Station cost depends on a number of factors, such as power rating, redundancy on transformers etc. Station cost have an almost linear relation to the power rating and following relation holds for the power span 20 - 126 MW: Station cost (EUR) = 16 000 (EUR/MW) x Power rating (MW) + 2 350 000 (EUR). Using a single transformer instead of two reduces the cost by a factor 0,86 - 0,87.
M | Station cost is based on average cost for capacity banks and inductor with a design voltage of 72 kV. It is assumed that the equipment is installed in a existing station.
O | Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
P | The percentage of the investment cost allocated to material cost and installation cost varies depending on area type (rural or city) and power level. An average is given here. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
Q | The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost multiplied by the average cost of cables per MW and km given in row 18 to 20. It should be noted that the O&M cost in distribution system mainly is attributed to stations since there is practically no maintenaince on cables. The O&M cost is assumed to be reduced over time by an annual factor of 1 - 1,8% due to increased efficiency. Upper uncertainty bounds for 2020 and 2050 corresponds to no efficiency increase in O&M and lower bounds corresponds to a continuous annual efficiency increase of 1,8%
R | Variable O&M cost is in very low for electric transmission systems and considered to be negligible
S | Energy losses and auxiliary electricity consumption can be considered negligible

## 111 2 el distri Rural
Table 2: Electricity distribution, Rural
| Technology | Energy Transport Electricity Distribution, Rural
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 4.5 | 5.25 | A | 1
| Energy losses, stations (%) | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption (% of energy delivered) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time (years) | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | 4, 5
| Typical load profile (-) | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D | 1, 5
| - Residential | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D
| - Commercial | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D
| Construction time (years) | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs (EUR/MWh/year) Rural | 173 | 173 | 173 | 173 | 155.7 | 173 | 131.7222 | 205.87 | E,F | 1, 6
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 524 | 524 | 524 | 524 | 471.6 | 524 | 424.44 | 524 | G,F | 6
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 1412 | 1412 | 1412 | 1412 | 1270.8 | 1412 | 1143.72 | 1412 | G,F | 6
| Investment costs; service line, 50-100 kW (EUR/unit) | 1583 | 1583 | 1583 | 1583 | 1424.7 | 1583 | 1282.23 | 1583 | G,F | 6
| Investment costs; service line, above 100 kW (EUR/unit) | 3745 | 3745 | 3745 | 3745 | 3370.5 | 3745 | 3033.45 | 3745 | G,F | 6
| Investment costs; single line, 0-50 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 50-250 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 100-250 kW (EUR/m) | 36 | 36 | 36 | 36 | 32 | 36 | 28.8 | 36 | H,F | 6
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 36 | 36 | 36 | 36 | 32 | 36 | 28.8 | 36 | H,F | 6
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 41 | 41 | 41 | 41 | 37 | 41 | 33.3 | 41 | H,F | 6
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 88 | 88 | 88 | 88 | 85 | 88 | 76.5 | 88 | H,F | 6
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Reinforcement costs (EUR/MW) (Station) | 11500 | 11500 | 11500 | 11500 | 10994 | 11500 | 10510.264 | 11500 | I,F,J | 6
| Investment costs; [type 1] station (EUR/MW) | 67500 | 67500 | 67500 | 67500 | 64530 | 67500 | 61690.68 | 67500 | J | 6
| Investment costs; [type 2] station (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investments, percentage installation (cables) | 62% | 62% | 62% | 62% | 57.35% | 62% | 52.56% | 62% | K | 6
| Investments, percentage materials (cables) | 38% | 38% | 38% | 38% | 38% | 42.65% | 42% | 38% | K | 6
| Investments, percentage installation (stations) | 22% | 22% | 22% | 22% | 18.86% | 22% | 16.61% | 19% | K | 6
| Investments, percentage materials (stations) | 78% | 78% | 78% | 78% | 78% | 81% | 78% | 81% | K | 6
| Fixed O&M (EUR/MW/year) | 1627.8093 | 1605.02 | 1582.5497 | 1560.394 | 1598.5087 | 1627.8093 | 1541.4803 | 1627.8093 | L | 7
| Variable O&M (EUR/MWh) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology specific data
References:
1 | Särskilda rapporten - teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2 | The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3 | International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4 | Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5 | Sweco, Project data
6 | EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7 | Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A | The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B | Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C | According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D | Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 19%.
E | The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F | Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G | Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW - 20 m, 20-100 kW - 50 m, Above 100 kW -100 m.
H | Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I | Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacing the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 EUR/MW for a 800 kVA or 1250 kVA transformer.
J | The cost in EUR/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
K | The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
L | The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1 - 1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M | Variable O&M cost is in very low for electric transmission systems and considered to be negligeable
N | Auxiliary electricity consumption can be considered negligible

## 111 3 el distri suburban
Table 3: Electricity distribution, Suburban
| Technology | Energy Transport Electricity Distribution, Suburban
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 3 | 3 | 3 | 3 | 3 | 3 | 2.25 | 3 | A | 1
| Energy losses, stations (%) | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption (% of energy delivered) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time (years) | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | 4, 5
| Typical load profile (-) | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D | 1, 5
| - Residential | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| - Commercial | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| Construction time (years) | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs (EUR/MWh/year) Suburban | 385 | 385 | 385 | 385 | 346.5 | 385 | 311.85 | 487.025 | E,F | 1, 6
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 1436 | 1436 | 1436 | 1436 | 1292.4 | 1436 | 1163.16 | 1436 | G,F | 6
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 4031 | 4031 | 4031 | 4031 | 3627.9 | 4031 | 3265.11 | 4031 | G,F | 6
| Investment costs; service line, 50-100 kW (EUR/unit) | 4243 | 4243 | 4243 | 4243 | 3818.7 | 4243 | 3436.83 | 4243 | G,F | 6
| Investment costs; service line, above 100 kW (EUR/unit) | 9066 | 9066 | 9066 | 9066 | 8159.4 | 9066 | 7343.46 | 9066 | G,F | 6
| Investment costs; single line, 0-50 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 50-250 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 100-250 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F | 6
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 75 | 75 | 75 | 75 | 65 | 75 | 58.5 | 75 | H,F | 6
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 80 | 80 | 80 | 80 | 70 | 80 | 63 | 80 | H,F | 6
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 128 | 128 | 128 | 128 | 118 | 128 | 106.2 | 128 | H,F | 6
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Reinforcement costs (EUR/MW) (Station) | 11500 | 11500 | 11500 | 11500 | 10994 | 11500 | 10510.264 | 11500 | I,F,J | 6
| Investment costs; [type 1] station (EUR/MW) | 38000 | 38000 | 38000 | 38000 | 36328 | 38000 | 34729.568 | 38000 | J | 6
| Investment costs; [type 2] station (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investments, percentage installation (cables) | 80% | 80% | 80% | 80% | 78% | 80% | 78% | 80% | K | 6
| Investments, percentage materials (cables) | 20% | 20% | 20% | 20% | 22% | 20% | 22% | 20% | K | 6
| Investments, percentage installation (stations) | 14% | 14% | 14% | 14% | 13% | 14% | 13% | 14% | K | 6
| Investments, percentage materials (stations) | 86% | 86% | 86% | 86% | 87% | 86% | 87% | 86% | K | 6
| Fixed O&M (EUR/MW/year) | 2681.3387 | 2643.8 | 2606.7868 | 2570.2918 | 2633.0746 | 2681.3387 | 2539.137 | 2681.3387 | L | 7
| Variable O&M (EUR/MWh) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology specific data
References:
1 | Särskilda rapporten - teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2 | The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3 | International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4 | Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5 | Sweco, Project data
6 | EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7 | Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A | The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B | Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C | According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D | Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 26%.
E | The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F | Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G | Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW - 20 m, 20-100 kW - 50 m, Above 100 kW -100 m.
H | Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I | Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 EUR/MW for a 800 kVA or 1250 kVA transformer.
J | The cost in EUR/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K | The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decrease the installation costs.
L | The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1 - 1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M | Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N | Auxiliary electricity consumption can be considered negligible

## 111 4 el distri city
Table 4: Electricity distribution, city
| Technology | Energy Transport Electricity Distribution, City
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 1.5 | 2.25 | A | 1
| Energy losses, stations (%) | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption (% of energy delivered) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time (years) | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | 4, 5
| Typical load profile (-) | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D | 1, 5
| - Residential | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D
| - Commercial | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D
| Construction time (years) | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs (EUR/MWh/year) City | 365 | 365 | 365 | 365 | 328.5 | 365 | 277.911 | 441.65 | E,F | 1, 6
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 2149 | 2149 | 2149 | 2149 | 1934.1 | 2149 | 1740.69 | 2149 | G,F | 6
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 5618 | 5618 | 5618 | 5618 | 5056.2 | 5618 | 4550.58 | 5618 | G,F | 6
| Investment costs; service line, 50-100 kW (EUR/unit) | 5774 | 5774 | 5774 | 5774 | 5196.6 | 5774 | 4676.94 | 5774 | G,F | 6
| Investment costs; service line, above 100 kW (EUR/unit) | 12131 | 12131 | 12131 | 12131 | 10917.9 | 12131 | 9826.11 | 12131 | G,F | 6
| Investment costs; single line, 0-50 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 50-250 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 100-250 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F | 6
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 115 | 115 | 115 | 115 | 100 | 115 | 90 | 115 | H,F | 6
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 120 | 120 | 120 | 120 | 104 | 120 | 93.6 | 120 | H,F | 6
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 169 | 169 | 169 | 169 | 154 | 169 | 138.6 | 169 | H,F | 6
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Reinforcement costs (EUR/MW) (Station) | 11500 | 11500 | 11500 | 11500 | 10994 | 11500 | 10510.264 | 11500 | I,F,J | 6
| Investment costs; [type 1] station (EUR/MW) | 38000 | 38000 | 38000 | 38000 | 36328 | 38000 | 34729.568 | 38000 | J | 6
| Investment costs; [type 2] station (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investments, percentage installation (cables) | 86% | 86% | 86% | 86% | N/A | N/A | N/A | N/A | K | 6
| Investments, percentage materials (cables) | 14% | 14% | 14% | 14% | N/A | N/A | N/A | N/A | K | 6
| Investments, percentage installation (stations) | 5% | 5% | 5% | 5% | 4% | 5% | 4% | 5% | K | 6
| Investments, percentage materials (stations) | 95% | 95% | 95% | 95% | 96% | 95% | 96% | 95% | K | 6
| Fixed O&M (EUR/MW/year) | 2865.7303 | 2825.61 | 2786.0515 | 2747.0468 | 2814.1471 | 2865.7303 | 2713.7496 | 2865.7303 | L | 7
| Variable O&M (EUR/MWh) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology specific data
References:
1 | Särskilda rapporten - teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2 | The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3 | International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4 | Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5 | Sweco, Project data
6 | EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7 | Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A | The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B | Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C | According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D | Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 21%.
E | The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F | Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G | Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW - 20 m, 20-100 kW - 50 m, Above 100 kW -100 m.
H | Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I | Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 EUR/MW for a 800 kVA or 1250 kVA transformer.
J | The cost in EUR/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K | The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decrease the installation costs.
L | The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintenance on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1 - 1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M | Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N | Auxiliary electricity consumption can be considered negligible

## 111 5 el distri new area
Table 5: Electricity distribution, New developed area
| Technology | Energy Transport Electricity Distribution, New developed areas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 3 | 3 | 3 | 3 | 2.25 | 3 | 2.25 | 3 | A | 1
| Energy losses, stations (%) | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption (% of energy delivered) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time (years) | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | 4, 5
| Typical load profile (-) | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D | 1, 5
| - Residential | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| - Commercial | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| Construction time (years) | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs (EUR/MWh/year) New developed area | 173 | 173 | 173 | 173 | 155.7 | 173 | 131.7222 | 205.87 | E,F | 1, 6
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 524 | 524 | 524 | 524 | 471.6 | 524 | 424.44 | 524 | G,F | 6
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 1412 | 1412 | 1412 | 1412 | 1270.8 | 1412 | 1143.72 | 1412 | G,F | 6
| Investment costs; service line, 50-100 kW (EUR/unit) | 1583 | 1583 | 1583 | 1583 | 1424.7 | 1583 | 1282.23 | 1583 | G,F | 6
| Investment costs; service line, above 100 kW (EUR/unit) | 3745 | 3745 | 3745 | 3745 | 3370.5 | 3745 | 3033.45 | 3745 | G,F | 6
| Investment costs; single line, 0-50 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 50-250 kW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Investment costs; single line, 100-250 kW (EUR/m) | 36 | 36 | 36 | 36 | 32 | 36 | 28.8 | 36 | H,F | 6
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 36 | 36 | 36 | 36 | 32 | 36 | 28.8 | 36 | H,F | 6
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 41 | 41 | 41 | 41 | 37 | 41 | 33.3 | 41 | H,F | 6
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 88 | 88 | 88 | 88 | 85 | 88 | 76.5 | 88 | H,F | 6
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | H,F
| Reinforcement costs (EUR/MW) (Station) | 11500 | 11500 | 11500 | 11500 | 10994 | 11500 | 10510.264 | 11500 | I,F,J | 6
| Investment costs; [type 1] station (EUR/MW) | 38000 | 38000 | 38000 | 38000 | 36328 | 38000 | 34729.568 | 38000 | J | 6
| Investment costs; [type 2] station (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investments, percentage installation (cables) | 80% | 80% | 80% | 80% | 78% | 80% | 78% | 80% | K | 6
| Investments, percentage materials (cables) | 20% | 20% | 20% | 20% | 22% | 20% | 22% | 20% | K | 6
| Investments, percentage installation (stations) | 14% | 14% | 14% | 14% | 13% | 14% | 13% | 14% | K | 6
| Investments, percentage materials (stations) | 86% | 86% | 86% | 86% | 87% | 86% | 87% | 86% | K | 6
| Fixed O&M (EUR/MW/year) | 1358.2776 | 1339.2617 | 1320.5121 | 1302.0249 | 1333.8286 | 1358.2776 | 1286.243 | 1358.2776 | L | 7
| Variable O&M (EUR/MWh) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology specific data
References:
1 | Särskilda rapporten - teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2 | The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3 | International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4 | Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5 | Sweco, Project data
6 | EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7 | Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A | The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B | Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C | According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D | Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an increase in peak load of 15 % without the use of smart grid leading to a corresponding decrease in load factor.
E | The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F | Price projections are based on an extrapolation of price development over the years 2000 - 2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G | Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW - 20 m, 20-100 kW - 50 m, Above 100 kW -100 m.
H | Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I | Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 EUR/MW for a 800 kVA or 1250 kVA transformer.
J | The cost in EUR/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K | The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decreace the installation costs.
L | The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1 - 1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M | Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N | Auxiliary electricity consumption can be considered negligible

## 112 6 gas Main distri line
Table 6: Natural gas main distribution line
| Technology | Energy Transport, Natural Gas Main distribution line
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines 1-20 MW (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A | 1
| Energy losses, lines 20-100 MW (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A
| Energy losses, lines above 100 MW (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A
| Energy losses, stations [Type 1] (%) | - | - | - | - | - | - | - | - | B
| Energy losses, stations [Type 2] (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.12 | 0 | 0.12 | C | 2
| Auxiliary electricity consumption (% energy transmitted) | 0.005 | 0.005 | 0.005 | 0.005 | 0.00425 | 0.00575 | 0.00425 | 0.00575 |  | 2
| Technical life time (years) | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
| Typical load profile (-) | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.4 | 0.05 | 0.4 |  | 2
| Construction time (years) | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.7 | 1.5 | D | 2
Financial data
Investment costs
| Investment costs; single line, 0 - 50 MW (EUR/MW/m) | 10.8 | 10.8 | 10.8 | 10.8 | 8.64 | 12.96 | 8.64 | 12.96 | E, F | 2
| Investment costs; single line, 50-100 MW (EUR/MW/m) | 4.2 | 4.2 | 4.2 | 4.2 | 3.36 | 5.04 | 3.36 | 5.04 | E, G | 2
| Investment costs; single line, 100 - 250 MW (EUR/MW/m) | 2.24 | 2.24 | 2.24 | 2.24 | 1.792 | 2.688 | 1.792 | 2.688 | E, G | 2
| Investment costs; single line, 250-500 MW (EUR/MW/m) | 1.17 | 1.17 | 1.17 | 1.17 | 0.936 | 1.404 | 0.936 | 1.404 | E, G | 2
| Investment costs; single line, 500-1000 MW (EUR/MW/m) | 0.68 | 0.68 | 0.68 | 0.68 | 0.544 | 0.816 | 0.544 | 0.816 | E, G | 1
| Investment costs; single line, above 1000 MW (EUR/MW/m) | - | - | - | - | - | - | - | - | i
| Reinforcement costs (EUR/MW) | - | - | - | - | - | - | - | - | H
| Investment costs; [type 1] station (EUR/MW) | - | - | - | - | - | - | - | - | B, J
| Investment costs; [type 2] station (EUR/MW) | 27000 | 27000 | 27000 | 27000 | 7000 | 45000 | 0 | 0 | C, K | 2
| Investments, percentage installation | 75 | 75 | 75 | 75 | 65 | 85 | 65 | 85 |  | 2
| Investments, percentage materials | 25 | 25 | 25 | 25 | 15 | 35 | 15 | 35 |  | 2
| Fixed O&M (EUR/MW/km/year) | 0.12099 | 0.12099 | 0.12099 | 0.12099 | 0.096789 | 0.14518 | 0.096789 | 0.14518 |  | 2
| Variable O&M (EUR/MWh/km) | 1.1255e-05 | 1.1255e-05 | 1.1255e-05 | 1.1255e-05 | 9.0037e-06 | 1.3506e-05 | 9.0037e-06 | 1.3506e-05 |  | 2
Technology specific data
References:
1 | Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2 | HMN Naturgas
Notes:
A | There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B | Type 1 MR stations supplying the transmission system level 2 - not part of the scope
C | Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
D | Includes enginering, tender, and construction.
E | Rates include VVM review, landowner compensation and archaeological screening. Based on 20 km, of which 8 % is based on drilling.
F | Data given is for a 50 MW capacity
G | Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H | Not possible to give general numbers. Depends on kind of reinforcement. Can be calculated based on the other numbers given.
I | Capacity not relevant - too high
J | Type 1 MR stations supplying the transmission system level 2 - not part of the scope
K | Type 1 MR stations supplying the transmission system level 2 .The stated costs are the average cost for a 40/4 bar MR station where reheating after expansion is required and a 19/4 bar MR station where reheating is not necessary. The cost is only modestly size dependent. A 40/4 bar station capacity of 10.000 m3/h is 20 % higher than a similar station with a capacity of 5.000 m3/h.

## 112 7 gas Rural
Table 7: Gas Distribution, rural
| Technology | Energy Transport Natural Gas Distribution, New distribution in existing rual areas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
| Energy losses, stations (%) | - | - | - | - | - | - | - | - | B
| Auxiliary electricity consumption (% of energy delivered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time (years) | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
| Typical load profile (-) | [8 empty] | D
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | N/A | N/A | N/A | N/A |  |  |  |  | D
| Construction time (years) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs (EUR/MWh/year), Rural | 140 | 140 | 140 | 140 | 130 | 150 | 130 | 150 |  | 2
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 1600 | 1600 | 1600 | 1600 | 1400 | 1800 | 1400 | 1800 |  | 2
| Investment costs; service line, 20 - 50 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; service line, 50-100 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; service line, above 100 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; single line, 0-50 kW (EUR/m) | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | F
| Investment costs; single line, 50-250 kW (EUR/m) | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | F
| Investment costs; single line, 100-250 kW (EUR/m) | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | F
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | F
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 53.3333 | 53.3333 | 53.3333 | 53.3333 | 48 | 58.6667 | 48 | 58.6667 | G
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 68.3333 | 68.3333 | 68.3333 | 68.3333 | 61.5 | 75.1667 | 61.5 | 75.1667 | G
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | - | - | - | - | - | - | - | -
| Reinforcement costs (EUR/MW) | - | - | - | - | - | - | - | - | H
| Type 1 station (EUR/MW) | - | - | - | - | - | - | - | - | I
| Type 2 station (EUR/MW) | - | - | - | - | - | - | - | - | I
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% |  | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% |  | 2
| Fixed O&M (EUR/MW/year) | 750 | 750 | 750 | 750 | 600 | 900 | 600 | 900 |  | 2
| Variable O&M (EUR/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
Technology specific data
References:
1 | Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2 | HMN Naturgas
Notes:
A | There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B | As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C | There is no power consuming parts in the distribution system
D | Based on given case
E | Capacity range not relevant for given case
F | Stated number is for Ø40 pipes - the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G | Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
H | Reinforcement not relevant
I | No station will be installed for the distribution network

## 112 8 gas Suburban
Table 8: Gas distribution, suburban
| Technology | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
| Energy losses, stations (%) | - | - | - | - | - | - | - | - | B
| Auxiliary electricity consumption (% of energy delivered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time (years) | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
| Typical load profile (-) | - | - | - | - | - | - | - | -
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | N/A | N/A | N/A | N/A |  |  |  |  | D
| Construction time (years) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs (EUR/MWh/year) Suburban | 150 | 150 | 150 | 150 | 140 | 170 | 140 | 170 |  | 2
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 1600 | 1600 | 1600 | 1600 | 1400 | 1800 | 1400 | 1800 |  | 2
| Investment costs; service line, 20 - 50 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; service line, 50-100 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; service line, above 100 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; single line, 0-50 kW (EUR/m) | 53.3333 | 53.3333 | 53.3333 | 53.3333 | 48 | 58.6667 | 48 | 58.6667 | F
| Investment costs; single line, 50-250 kW (EUR/m) | 53.3333 | 53.3333 | 53.3333 | 53.3333 | 48 | 58.6667 | 48 | 58.6667 | F
| Investment costs; single line, 100-250 kW (EUR/m) | 53.3333 | 53.3333 | 53.3333 | 53.3333 | 48 | 58.6667 | 48 | 58.6667 | F
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 53.3333 | 53.3333 | 53.3333 | 53.3333 | 48 | 58.6667 | 48 | 58.6667 | F
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 60 | 60 | 60 | 60 | 54 | 66 | 54 | 66 | G
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 78 | 95.3333 | 78 | 95.3333 | G
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | - | - | - | - | - | - | - | -
| Reinforcement costs (EUR/MW) | - | - | - | - | - | - | - | - | H
| Type 1 station (EUR/MW) | - | - | - | - | - | - | - | - | I
| Type 2 station (EUR/MW) | - | - | - | - | - | - | - | - | I
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% |  | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% |  | 2
| Fixed O&M (EUR/MW/year) | 310 | 310 | 310 | 310 | 250 | 370 | 250 | 370 |  | 2
| Variable O&M (EUR/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
Technology specific data
References:
1 | Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2 | HMN Naturgas
Notes:
A | There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B | As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C | There is no power consuming parts in the distribution system
D | Based on given case
E | Capacity range not relevant for given case
F | Stated number is for a Ø40 pipes - the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G | Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H | Reinforcement not relevant
I | No station will be installed for the distribution network

## 112 9 gas City
Table 9: Gas distribution, city
| Technology | Energy Transport Natural Gas Distribution, New distribution in existing city areas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | - | - | - | - | - | - | - | - | A | 1
| Energy losses, stations (%) | - | - | - | - | - | - | - | - | B | 1
| Auxiliary electricity consumption (% of energy delivered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C | 1
| Technical life time (years) | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 1
| Typical load profile (-) | [8 empty] | D
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | D
| Construction time (years) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 1
Financial data
| Distribution network costs (EUR/MWh/year) City | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 1
| Investment costs; service line, 0 - 20 kW (EUR/unit) | - | - | - | - | - | - | - | -
| Investment costs; service line, 20 - 50 kW (EUR/unit) | - | - | - | - | - | - | - | -
| Investment costs; service line, 50-100 kW (EUR/unit) | - | - | - | - | - | - | - | -
| Investment costs; service line, above 100 kW (EUR/unit) | 15000 | 15000 | 15000 | 15000 | 12000 | 18000 | 12000 | 18000 | E | 1
| Investment costs; single line, 0-50 kW (EUR/m) | 64 | 64 | 64 | 64 | 57.6 | 70.4 | 57.6 | 70.4 |  | 1
| Investment costs; single line, 50-250 kW (EUR/m) | 64 | 64 | 64 | 64 | 57.6 | 70.4 | 57.6 | 70.4 |  | 1
| Investment costs; single line, 100-250 kW (EUR/m) | 64 | 64 | 64 | 64 | 57.6 | 70.4 | 57.6 | 70.4 |  | 1
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 64 | 64 | 64 | 64 | 57.6 | 70.4 | 57.6 | 70.4 |  | 1
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 72 | 72 | 72 | 72 | 64.8 | 79.2 | 64.8 | 79.2 |  | 1
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 104 | 104 | 104 | 104 | 93.6 | 114.4 | 93.6 | 114.4 |  | 1
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | - | - | - | - | - | - | - | - | F
| Reinforcement costs (EUR/MW) | - | - | - | - | - | - | - | - | F
| Type 1 station (EUR/MW) | - | - | - | - | - | - | - | - | F
| Type 2 station (EUR/MW) | - | - | - | - | - | - | - | - | F
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% |  | 1
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% |  | 1
| Fixed O&M (EUR/MW/year) | 20 | 20 | 20 | 20 | 16 | 24 | 16 | 24 |  | 1
| Variable O&M (EUR/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1
Technology specific data
References:
1 | HMN Naturgas
Notes:
A | For the defined case "New distribution in existing densely populated areas, city centres etc." it is assessed the natural gas based heating will be designed with one boiler and heat is distributied to the endusers by a locel district heating sytem. This means that the local natural gas system will only consist of a A service line with a capacity of 1.5 MW supplying a boiler aswell a meter and a pressure regulator. Therefore losses are neglegted
B | As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C | There is no power consuming parts in the distribution system
D | Based on given case
E | Stated number is for a service line supplying 1,5 MW.
F | Not relavant, see note A

## 112 1 gas New area
Table 10: Gas distribution, new developed area
| Technology | Energy Transport Natural Gas Distribution, New developed residential areas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
| Energy losses, stations (%) | - | - | - | - | - | - | - | - | B
| Auxiliary electricity consumption (% of energy delivered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time (years) | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
| Typical load profile (-) | - | - | - | - | - | - | - | -
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | N/A | N/A | N/A | N/A |  |  |  |  | D
| Construction time (years) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs (EUR/MWh/year) City | 270 | 270 | 270 | 270 | 240 | 300 | 240 | 300 |  | 2
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 1600 | 1600 | 1600 | 1600 | 1400 | 1800 | 1400 | 1800 |  | 2
| Investment costs; service line, 20 - 50 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; service line, 50-100 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; service line, above 100 kW (EUR/unit) | - | - | - | - | - | - | - | - | E
| Investment costs; single line, 0-50 kW (EUR/m) | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 42 | 51.3333 | 42 | 51.3333 | F
| Investment costs; single line, 50-250 kW (EUR/m) | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 42 | 51.3333 | 42 | 51.3333 | F
| Investment costs; single line, 100-250 kW (EUR/m) | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 42 | 51.3333 | 42 | 51.3333 | F
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 46.6667 | 46.6667 | 46.6667 | 46.6667 | 42 | 51.3333 | 42 | 51.3333 | F
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | G
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 63.3333 | 63.3333 | 63.3333 | 63.3333 | 57 | 69.6667 | 57 | 69.6667 | G
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | - | - | - | - | - | - | - | -
| Reinforcement costs (EUR/MW) | - | - | - | - | - | - | - | - | H
| Type 1 station (EUR/MW) | - | - | - | - | - | - | - | - | I
| Type 2 station (EUR/MW) | - | - | - | - | - | - | - | - | I
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% |  | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% |  | 2
| Fixed O&M (EUR/MW/year) | 920 | 920 | 920 | 920 | 740 | 1100 | 740 | 1100 |  | 2
| Variable O&M (EUR/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
Technology specific data
References:
1 | Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2 | HMN Naturgas
Notes:
A | No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B | As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C | There are no power consuming parts in the distribution system
D | Based on given case
E | Capacity range not relevant for given case
F | Stated number is for Ø40 pipes - the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G | Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H | Reinforcement not relevant
I | No station will be installed for the distribution network

## 113_11 DH transmission
| Technology | Energy Transport District Heating Transmission
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines 1-20 MW (%) | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 1, 2
| Energy losses, lines 20-100 MW (%) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | A | 1, 2
| Energy losses, lines above 100 MW (%) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 | A | 1, 2
| Energy losses, Heat exchanger stations (%) | 5 | 5 | 5 | 5 | 2 | 7 | 2 | 7 |  | 1
| Energy losses, Pumping stations (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | G | 1
| Auxiliary electricity consumption (% energy transmitted) | 2 | 2 | 2 | 2 | 0.5 | 5 | 0.5 | 5 |  | 1, 4
| Technical life time (years) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | B | 1, 2
| Typical load profile (-) | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.6 |  | 1
| Construction time (years) | 4 | 4 | 4 | 4 | 3 | 5 | 3 | 5 |  | 1
Financial data
Investment costs
| Investment costs; single line, 0 - 50 MW (EUR/MW/m) | 25 | 25 | 25 | 25 | See Note | See Note | See Note | See Note | C, D | 1, 3
| Investment costs; single line, 50-100 MW (EUR/MW/m) | 12 | 12 | 12 | 12 | See Note | See Note | See Note | See Note | C, D | 1, 3
| Investment costs; single line, 100 - 250 MW (EUR/MW/m) | 9 | 9 | 9 | 9 | See Note | See Note | See Note | See Note | C, D | 1, 3
| Investment costs; single line, 250-500 MW (EUR/MW/m) | 6 | 6 | 6 | 6 | See Note | See Note | See Note | See Note | C, D | 1, 3
| Investment costs; single line, 500-1000 MW (EUR/MW/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, above 1000 MW (EUR/MW/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Reinforcement costs (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | E
| Investment costs; [type 1] station (EUR/MW) | 115000 | 115000 | 115000 | 115000 | 92000 | 138000 | 92000 | 138000 |  | 1
| Investment costs; [type 2] station (EUR/MW) | 105000 | 105000 | 105000 | 105000 | 84000 | 126000 | 84000 | 126000 |  | 1
| Investments, percentage installation | 60% | 60% | 60% | 60% | 50% | 75% | 50% | 75% | C | 1, 3
| Investments, percentage materials | 40% | 40% | 40% | 40% | 25% | 50% | 25% | 50% | C | 1, 3
| Fixed O&M (EUR/MW/km/year) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Variable O&M (EUR/MWh/km) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 1.5 | 0.05 | 1.5 |  | 1, 4
Technology specific data
References:
1 | Based on Sweco experience figures
2 | LOGSTOR A/S
3 | Consolidated with data from Svensk Fjärrvärme
4 | Consolidated with data from Dansk Fjernvarmes Årsstatistik 2016
Notes:
A | The loss is per km of transmission line
B | The technical life time of a district heating pipe is minimum 30 years. However the life time can be substatialy longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
C | An unpaved area is asumed
D | Two district heating pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
E | Depends on the scale of the transmission grid and supply strategy of reserve capacity. Therefore, it is not possible to generalize these costs.
G | Energy losses in pumping stations can be considered negligible

## 113_12 DH_Distribu Rural
Table 12: District heating distribution, rural
| Technology | Energy Transport District Heating Distribution, Rural
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 | A, B | 1
| Energy losses, Heat exchanger stations (%) | 5 | 5 | 5 | 5 | 2 | 7 | 2 | 7 | C | 2
| Auxiliary electricity consumption (% of energy delivered) | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 2
| Technical life time (years) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | D | 1
Typical load profile (-)
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
Financial data
| Distribution network costs (EUR/MWh/year), Rural | 720 | 720 | 720 | 720 | See Note | See Note | See Note | See Note | E, F | 2, 3
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 3785 | 3785 | 3785 | 3785 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 4135 | 4135 | 4135 | 4135 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 50-100 kW (EUR/unit) | 4735 | 4735 | 4735 | 4735 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, above 100 kW (EUR/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, 0-50 kW (EUR/m) | 279.5 | 279.5 | 279.5 | 279.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 50-250 kW (EUR/m) | 354.5 | 354.5 | 354.5 | 354.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 100-250 kW (EUR/m) | 369.5 | 369.5 | 369.5 | 369.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 460 | 460 | 460 | 460 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 640 | 640 | 640 | 640 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 1185 | 1185 | 1185 | 1185 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Reinforcement costs (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat exchanger station (EUR/MW) | 100000 | 100000 | 100000 | 100000 | 80000 | 120000 | 80000 | 120000 | I | 2
| Pumping station (EUR/MW) | 90000 | 90000 | 90000 | 90000 | 72000 | 108000 | 72000 | 108000 | I | 2
| Investments, percentage installation | 85% | 85% | 85% | 85% | 80% | 90% | 80% | 90% | F | 2
| Investments, percentage materials | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | F | 2
| Fixed O&M (EUR/MW/year) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Variable O&M (EUR/MWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2, 4
Technology specific data
| Heat exchanger station below 1 MW(EUR/MW) | 265000 | 265000 | 265000 | 265000 | 212000 | 318000 | 212000 | 318000 |  | 2
| Pumping station below 1 MW (EUR/MW) | 240000 | 240000 | 240000 | 240000 | 192000 | 288000 | 192000 | 288000 |  | 2
References:
1 | LOGSTOR A/S
2 | Based on Sweco experience figures
3 | Consolidated with data from Svensk Fjärrvärme
4 | Consolidated with data from Dansk Fjernvarmes Årsstatistik 2016
Notes:
A | For entire distribution network
B | Use of single pipes would lead to a higher heat loss
C | For heat exchanger stations the heat loss is below 5 % and varies depending on the level of thermal insulation. For pump stations the heat loss is negligible.
D | The technical life time of a district heating pipe is minimum 30 years. However the life time can be substatialy longer depending on operation conditions e.g. temperature variation, soil conditions etc.
E | The distribution network costs are based on the total cost for the area type case divided by the yearly heat demand. An unpaved area is assumed for all economic values
F | An paved area is assumed for the distribution network. For service lines 50 % unpaved and 50 % paved area is asumed.
G | Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. Service lines above 100 kW are not relevant in the specific area type.
H | Two district heating pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. The cost is per trench meter. Power levels above 25 MW are not relevant in the specific area type.
I | The value stated is for stations above 1 MW. Investment costs per MW for stations below 1 MW are very different compared to stations above 1 MW as specified under Technology specific data.

## 113_13 DH_Distribu Suburb
Table 13: District heating distribution, suburban
| Technology | Energy Transport District Heating Distribution, Suburban
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 14 | 14 | 14 | 14 | 10 | 17 | 10 | 17 | A, B | 1
| Energy losses, Heat exchanger stations (%) | 5 | 5 | 5 | 5 | 2 | 7 | 2 | 7 | C | 2
| Auxiliary electricity consumption (% of energy delivered) | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 2
| Technical life time (years) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | D | 1
Typical load profile (-)
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| - Commercial | N/A | N/A | N/A | N/A
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
Financial data
| Distribution network costs (EUR/MWh/year) Suburban | 655 | 655 | 655 | 655 | See Note | See Note | See Note | See Note | E, F | 2, 3
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 3785 | 3785 | 3785 | 3785 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 4135 | 4135 | 4135 | 4135 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 50-100 kW (EUR/unit) | 4735 | 4735 | 4735 | 4735 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, above 100 kW (EUR/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, 0-50 kW (EUR/m) | 279.5 | 279.5 | 279.5 | 279.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 50-250 kW (EUR/m) | 354.5 | 354.5 | 354.5 | 354.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 100-250 kW (EUR/m) | 369.5 | 369.5 | 369.5 | 369.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 460 | 460 | 460 | 460 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 640 | 640 | 640 | 640 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 1185 | 1185 | 1185 | 1185 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Reinforcement costs (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat exchanger station (EUR/MW) | 100000 | 100000 | 100000 | 100000 | 80000 | 120000 | 80000 | 120000 | I | 2
| Pumping station (EUR/MW) | 90000 | 90000 | 90000 | 90000 | 72000 | 108000 | 72000 | 108000 | I | 2
| Investments, percentage installation | 85% | 85% | 85% | 85% | 80% | 90% | 80% | 90% | F | 2
| Investments, percentage materials | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | F | 2
| Fixed O&M (EUR/MW/year) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Variable O&M (EUR/MWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2, 4
Technology specific data
| Heat exchanger station below 1 MW(EUR/MW) | 265000 | 265000 | 265000 | 265000 | 212000 | 318000 | 212000 | 318000 |  | 2
| Pumping station below 1 MW (EUR/MW) | 240000 | 240000 | 240000 | 240000 | 192000 | 288000 | 192000 | 288000 |  | 2
References:
1 | LOGSTOR A/S
2 | Based on Sweco experience figures
3 | Consolidated with data from Svensk Fjärrvärme
4 | Consolidated with data from Dansk Fjernvarmes Årsstatistik 2016
Notes:
A | For entire distribution network
B | Use of single pipes would lead to a higher heat loss
C | For heat exchanger stations the heat loss is below 5 % and varies depending on the level of thermal insulation. For pump stations the heat loss is negligible.
D | The technical life time of a district heating pipe is minimum 30 years. However the life time can be substatialy longer depending on operation conditions e.g. temperature variation, soil conditions etc.
E | The distribution network costs are based on the total cost for the area type case divided by the yearly heat demand. An unpaved area is assumed for all economic values
F | An paved area is assumed for the distribution network. For service lines 50 % unpaved and 50 % paved area is asumed.
G | Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. Service lines above 100 kW are not relevant in the specific area type.
H | Two district heating pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. The cost is per trench meter. Power levels above 25 MW are not relevant in the specific area type.
I | The value stated is for stations above 1 MW. Investment costs per MW for stations below 1 MW are very different compared to stations above 1 MW as specified under Technology specific data.

## 113_14 DH_Distribu City
Table 14: District heating distribution, city
| Technology | Energy Transport District Heating Distribution, City
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 5 | 5 | 5 | 5 | 3 | 8 | 3 | 8 | A, B | 1
| Energy losses, Heat exchanger stations (%) | 5 | 5 | 5 | 5 | 2 | 7 | 2 | 7 | C | 2
| Auxiliary electricity consumption (% of energy delivered) | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 2
| Technical life time (years) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | D | 1
Typical load profile (-)
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
Financial data
| Distribution network costs (EUR/MWh/year) City | 150 | 150 | 150 | 150 | See Note | See Note | See Note | See Note | E, F | 2, 3
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 4645 | 4645 | 4645 | 4645 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 5025 | 5025 | 5025 | 5025 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 50-100 kW (EUR/unit) | 5685 | 5685 | 5685 | 5685 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, above 100 kW (EUR/unit) | 6195 | 6195 | 6195 | 6195 | See Note | See Note | See Note | See Note | F, G, H | 2, 3
| Investment costs; single line, 0-50 kW (EUR/m) | 279.5 | 279.5 | 279.5 | 279.5 | See Note | See Note | See Note | See Note | F, I | 2, 3
| Investment costs; single line, 50-250 kW (EUR/m) | 354.5 | 354.5 | 354.5 | 354.5 | See Note | See Note | See Note | See Note | F, I | 2, 3
| Investment costs; single line, 100-250 kW (EUR/m) | 369.5 | 369.5 | 369.5 | 369.5 | See Note | See Note | See Note | See Note | F, I | 2, 3
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 460 | 460 | 460 | 460 | See Note | See Note | See Note | See Note | F, I | 2, 3
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 640 | 640 | 640 | 640 | See Note | See Note | See Note | See Note | F, I | 2, 3
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 1185 | 1185 | 1185 | 1185 | See Note | See Note | See Note | See Note | F, I | 2, 3
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Reinforcement costs (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat exchanger station (EUR/MW) | 100000 | 100000 | 100000 | 100000 | 80000 | 120000 | 80000 | 120000 | J | 2
| Pumping station (EUR/MW) | 90000 | 90000 | 90000 | 90000 | 72000 | 108000 | 72000 | 108000 | J | 2
| Investments, percentage installation | 85% | 85% | 85% | 85% | 80% | 90% | 80% | 90% | F | 2
| Investments, percentage materials | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | F | 2
| Fixed O&M (EUR/MW/year) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Variable O&M (EUR/MWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2, 4
Technology specific data
| Heat exchanger station below 1 MW(EUR/MW) | 265000 | 265000 | 265000 | 265000 | 212000 | 318000 | 212000 | 318000 |  | 2
| Pumping station below 1 MW (EUR/MW) | 240000 | 240000 | 240000 | 240000 | 192000 | 288000 | 192000 | 288000 |  | 2
References:
1 | LOGSTOR A/S
2 | Based on Sweco experience figures
3 | Consolidated with data from Svensk Fjärrvärme
4 | Consolidated with data from Dansk Fjernvarmes Årsstatistik 2016
Notes:
A | For entire distribution network
B | Use of single pipes would lead to a higher heat loss
C | For heat exchanger stations the heat loss is below 5 % and varies depending on the level of thermal insulation. For pump stations the heat loss is negligible.
D | The technical life time of a district heating pipe is minimum 30 years. However the life time can be substatialy longer depending on operation conditions e.g. temperature variation, soil conditions etc.
E | The distribution network costs are based on the total cost for the area type case divided by the yearly heat demand. An unpaved area is assumed for all economic values
F | An paved area is assumed for the distribution network as well as service lines
G | Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H | The value stated is for a DN40 twin pipe. This pipe size is able to deliver up to around 230 kW. If a higher capacity is needed the price will increase.
I | Two district heating pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. The cost is per trench meter. Power levels above 25 MW are not relevant in the specific area type.
J | The value stated is for stations above 1 MW. Investment costs per MW for stations below 1 MW are very different compared to stations above 1 MW as specified under Technology specific data.

## 112_15 DH_Distribu New area
Table 15: District heating distribution, new developed area
| Technology | Energy Transport District Heating Distribution, New Area
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 18 | 18 | 18 | 18 | 10 | 25 | 10 | 25 | A, B | 1
| Energy losses, Heat exchanger stations (%) | 5 | 5 | 5 | 5 | 2 | 7 | 2 | 7 | C | 2
| Auxiliary electricity consumption (% of energy delivered) | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 2
| Technical life time (years) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | D | 1
Typical load profile (-)
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
Financial data
| Distribution network costs (EUR/MWh/year) New developed residential area | 655 | 655 | 655 | 655 | See Note | See Note | See Note | See Note | E, F | 2, 3
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 2925 | 2925 | 2925 | 2925 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 3375 | 3375 | 3375 | 3375 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 50-100 kW (EUR/unit) | 3775 | 3775 | 3775 | 3775 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, above 100 kW (EUR/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, 0-50 kW (EUR/m) | 180 | 180 | 180 | 180 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 50-250 kW (EUR/m) | 234.5 | 234.5 | 234.5 | 234.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 100-250 kW (EUR/m) | 250 | 250 | 250 | 250 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 320 | 320 | 320 | 320 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 455 | 455 | 455 | 455 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 900 | 900 | 900 | 900 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Reinforcement costs (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat exchanger station (EUR/MW) | 100000 | 100000 | 100000 | 100000 | 80000 | 120000 | 80000 | 120000 | I | 2
| Pumping station (EUR/MW) | 90000 | 90000 | 90000 | 90000 | 72000 | 108000 | 72000 | 108000 | I | 2
| Investments, percentage installation | 75% | 75% | 75% | 75% | 65% | 80% | 65% | 80% | F | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 20% | 35% | 20% | 35% | F | 2
| Fixed O&M (EUR/MW/year) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Variable O&M (EUR/MWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2, 4
Technology specific data
| Heat exchanger station below 1 MW(EUR/MW) | 265000 | 265000 | 265000 | 265000 | 212000 | 318000 | 212000 | 318000 |  | 2
| Pumping station below 1 MW (EUR/MW) | 240000 | 240000 | 240000 | 240000 | 192000 | 288000 | 192000 | 288000 |  | 2
References:
1 | LOGSTOR A/S
2 | Based on Sweco experience figures
3 | Consolidated with data from Svensk Fjärrvärme
4 | Consolidated with data from Dansk Fjernvarmes Årsstatistik 2016
Notes:
A | For entire distribution network
B | Use of single pipes would lead to a higher heat loss
C | For heat exchanger stations the heat loss is below 5 % and varies depending on the level of thermal insulation. For pump stations the heat loss is negligible.
D | The technical life time of a district heating pipe is minimum 30 years. However the life time can be substatialy longer depending on operation conditions e.g. temperature variation, soil conditions etc.
E | The distribution network costs are based on the total cost for the area type case divided by the yearly heat demand. An unpaved area is assumed for all economic values
F | An unpaved area is assumed
G | Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. Service lines above 100 kW are not relevant in the specific area type.
H | Two district heating pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. The cost is per trench meter. Power levels above 25 MW are not relevant in the specific area type.
I | The value stated is for stations above 1 MW. Investment costs per MW for stations below 1 MW are very different compared to stations above 1 MW as specified under Technology specific data.

## 113_16 DH_Distr New area LTDH
Table 16: District heating distribution, new developed area with low temperature district heating
| Technology | Energy Transport District Heating Distribution, New Area Low Temperature
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Energy losses, lines (%) | 10 | 10 | 10 | 10 | 8 | 12 | 8 | 12 | A, B | 1
| Energy losses, Heat exchanger stations (%) | 5 | 5 | 5 | 5 | 2 | 7 | 2 | 7 | C | 2
| Auxiliary electricity consumption (% of energy delivered) | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 2
| Technical life time (years) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | D | 1
Typical load profile (-)
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
Financial data
| Distribution network costs (EUR/MWh/year) new developed residential area - Low temperature district heating | 680 | 680 | 680 | 680 | See Note | See Note | See Note | See Note | E, F | 2, 3
| Investment costs; service line, 0 - 20 kW (EUR/unit) | 3200 | 3200 | 3200 | 3200 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 20 - 50 kW (EUR/unit) | 3375 | 3375 | 3375 | 3375 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, 50-100 kW (EUR/unit) | 3850 | 3850 | 3850 | 3850 | See Note | See Note | See Note | See Note | F, G | 2, 3
| Investment costs; service line, above 100 kW (EUR/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, 0-50 kW (EUR/m) | 180 | 180 | 180 | 180 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 50-250 kW (EUR/m) | 234.5 | 234.5 | 234.5 | 234.5 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 100-250 kW (EUR/m) | 250 | 250 | 250 | 250 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 250 kW - 1 MW (EUR/m) | 370 | 370 | 370 | 370 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 1 MW - 5 MW (EUR/m) | 540 | 540 | 540 | 540 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 5 MW - 25 MW (EUR/m) | 955 | 955 | 955 | 955 | See Note | See Note | See Note | See Note | F, H | 2, 3
| Investment costs; single line, 25 MW - 100 MW (EUR/m) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Reinforcement costs (EUR/MW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat exchanger station (EUR/MW) | 100000 | 100000 | 100000 | 100000 | 80000 | 120000 | 80000 | 120000 | I | 2
| Pumping station (EUR/MW) | 90000 | 90000 | 90000 | 90000 | 72000 | 108000 | 72000 | 108000 | I | 2
| Investments, percentage installation | 75% | 75% | 75% | 75% | 65% | 80% | 65% | 80% | F | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 20% | 35% | 20% | 35% | F | 2
| Fixed O&M (EUR/MW/year) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Variable O&M (EUR/MWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2, 4
Technology specific data
| Heat exchanger station below 1 MW(EUR/MW) | 265000 | 265000 | 265000 | 265000 | 212000 | 318000 | 212000 | 318000 |  | 2
| Pumping station below 1 MW (EUR/MW) | 240000 | 240000 | 240000 | 240000 | 192000 | 288000 | 192000 | 288000 |  | 2
References:
1 | LOGSTOR A/S
2 | Based on Sweco experience figures
3 | Consolidated with data from Svensk Fjärrvärme
4 | Consolidated with data from Dansk Fjernvarmes Årsstatistik 2016
Notes:
A | For entire distribution network
B | Use of single pipes would lead to a higher heat loss
C | For heat exchanger stations the heat loss is below 5 % and varies depending on the level of thermal insulation. For pump stations the heat loss is negligible.
D | The technical life time of a district heating pipe is minimum 30 years. However the life time can be substatialy longer depending on operation conditions e.g. temperature variation, soil conditions etc.
E | The distribution network costs are based on the total cost for the area type case divided by the yearly heat demand. An unpaved area is assumed for all economic values
F | An unpaved area is assumed
G | Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. Service lines above 100 kW are not relevant in the specific area type.
H | Two district heating pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table. The cost is per trench meter. Power levels above 25 MW are not relevant in the specific area type.
I | The value stated is for stations above 1 MW. Investment costs per MW for stations below 1 MW are very different compared to stations above 1 MW as specified under Technology specific data.