## Index
INDEX | Technology Data for Energy Plants Updated chapters, August 2016 and later
01 Coal CHP | All cost data is in 2015€, unless stated otherwise
02 LTE existing plant
03a Coal to wood pellets exi bo
03b Coal to wood chips n. boile
03c coal to wood chips exi. boi
03d coal to wood chips exi. boi
04 Gas turb. simple cycle, L
04 Gas turb. simple cycle Sm-Me
04 Gas turb. simple cycle Micro
05 Gas turb. CC, steam extract.
05 Gas turb. CC, Back-pressure
06 Gas engines, natural gas
06 Gas engines, biogas
07 Carbon Capture and Storage
08 WtE CHP, Large, 40 degree
08 WtE CHP, Large, 50 degree
08 WtE CHP, Medium
08 WtE CHP, Small
08 WtE HOP
09a Wood Chips, Large 40 degree
09a Wood Chips, Large 50 degree
09a Wood Chips, Medium
09a Wood Chips, Small
09b Wood Pellets, Large 40 degr
09b Wood Pellets, Large 50 degr
09b Wood Pellets, Medium
09b Wood Pellets, Small
09c Straw, Large, 40 degree
09c Straw, Large, 50 degree
09c Straw, Medium
09c Straw, Small
09a Wood Chips HOP, small
09a Wood Chips HOP, medium
09a Wood Chips HOP, large
09b Wood Pellets HOP
09c Straw HOP
09a Wood Chips extract. plant
09b Wood Pellets extract. plant
10 Stirling
11 SOFC-CHP
12 LT-PEMFC CHP
20 Onshore turbines
20 Domestic turbines
21 Offshore turbines
21 Near shore turbines
22 Residential rooftop Photovoltaics
22 Commercial/industrial rooftop Photovoltaics
22 Utility-scale ground mounted Photovoltaics
22 Utility-scale ground mounted Photovoltaics (single axis tracking)
23 Wave Energy
40 Comp. hp, airsource 1 MW
40 Comp. hp, airsource 3 MW
40 Comp. hp, airsource 10 MW
40 Comp. hp, excess heat 1 MW
40 Comp. hp, excess heat 3 MW
40 Comp. hp, excess heat 10 MW
40 Comp. hp, seawater 20 MW
40 Absorption heat pump, DH
41 Electric Boilers
44 Natural Gas DH Only
45.1.a Geothermal DH, 1200m, E
45.1.b Geothermal DH, 2000m, E
45.2.a Geothermal DH, 1200m, A
45.2.b Geothermal DH, 2000m, A
45.3.a Geoth. DH, 1200m, E (LT)
45.3.b Geoth DH, 2000m, E (LT)
46 Solar District Heating
50 Diesel engine farm
51 Natural gas engine plant
52 OCGT - Natural gas
52 OCGT - Light fuel oil
This file contains the technology data sheets related to the updated technology data catalogue from August 2016. The data sheets is continuously updated as technologies evolve, if the data changes significantly or if errors are found. The date for the latest update is listed in the index below and also indicated in the specific datasheets.
INDEX:
01 Supercritical Pulverized Fuel Power Plant - Coal CHP (updated November 2017)
02 Life time extension of coal fired power plants
03 Rebuilding large coal power plants to biomass (updated June 2019)
- Coal power plant to wood pellets (existing boiler)
- Coal power plants to wood chips (existing boiler)
- Coal power plant to wood chips (new boiler)
04 Gas turbines, single cycle (updated January 2018)
05 Gas turbines, combined cycle (updated January 2018)
06 Gas engines (updated January 2018)
07 Carbon Capture and Storage (Transfered from previous catalogue October 2018)
08 WtE plants (updated March 2018)
- WtE CHP, Large, medium and small
- WtE HOP
09 Biomass plants (updated January 2020, minor updates March 2020)
- Wood Chips CHP, Large, medium and small
- Wood Pellets CHP, Large, medium and small
- Straw CHP, Large, medium and small
- Wood Chips HOP
- Wood Pellets HOP
- Straw HOP
- Wood chips extraction plant added
- Wood pellets extraction plant added - Wood chips medium and large HOP added (added March 2020)
10 Stirling Engines (transferred from previous catalogue October 2018)
11 Solid oxide fuel cell (SOFC) CHP, natural gas/biogas (added January 2018)
12 Low temperature proton exchange membrane fuel cell (LT-PEMFC) CHP, hydrogen (added January 2018)
20 Wind turbines, onshore (updated May 2019)
- On-shore turbines
- Domestic turbines
21 Wind turbines, offshore (updated March 2022 - cost data in 2020-€)
- Offshore turbines
- Near shore turbines
22 Photovoltaics (updated February 2022 - cost data in 2020-€)
- Residential rooftop PV (small system)
- Commercial/industrial rooftop PV (medium sized system)
- Utility-scale ground mounted PV, fixed axis (large system)
- Utility-scale ground mounted PV, single-axis tracking (large system)
23 Wave Energy (Transfered from previous catalogue October 2018)
40 Heat pumps (updated April 2020)
- Compression heat pumps (electric) updated. Datasheets now divided in 3 types and different plant sizes.
41 Electric Boiler (added June 2017 and updated january 2018)
44 District heating boilers, Gas fired (updated January 2018)
45 Geothermal (updated April 2020) -Data updated. -Datasheets now divided in 1200 m and 2000 m depth, electric- and absorption heat pumps and 2 different district heating temperatures.
46 Solar District Heating (updated October 2018)
50 Diesel engine farm (added november 2018)
51 Natural gas engine plant (added november 2018)
52 Open cycle gas turbine (added november 2018)

## 01 Coal CHP
| Technology | Pulverized coal fired, Supercritical steam process, extraction plant
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 400 - 700
| Electricity efficiency, condensation mode, net (%) | 44-48 | 46-51 | 52 | 52-55 | C | 8;7;9;11
| Cb coefficient (50oC/100oC) | 0.75 | 0.84 | 1.01 |  | A
| Cv coefficient (50oC/100oC) | 0.15 | 0.15 | 0.15 |  |  | 1
| Availability (%) | 95 | 95 | 95 |  | E | 7
| Technical lifetime (years) | 25 | 25 | 25 | 25 |  | 6
| Construction time (years) | 4.5 | 4.5 | 4.5 |  |  | 2;3;3
Environment
| SO2 (degree of desulphuring, %) | 97 | 97 | 97 | 97 | B | 5
| NOX (g per GJ fuel) | 38 | 35 | 35 | 35 | B | 12;5;5;5
| CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 |  | 13;5;5;5
| N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 |  | 13;5;5;5
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1.93 | 1.9 | 1.8605 | 1.7839 | J | 17,18,19,20,21,22
| Fixed O&M (€/MW/year) | 31500 | 31000 | 30355.1176 | 29105.3196 | J | 17,18,19,20,21,22
| Variable O&M (€/MWh) | 2.95 | 2.9 | 2.8397 | 2.7228 | J | 17,18,19,20.21,22
Regulation ability
| Primary load support (% per 30 seconds) | 5 | 5 | 5 | 5 | D | 14
| Secondary load support (% per minute) | 4 | 4 | 4 | 4 | D | 14
| Minimum load (% of full load) | 18 | 15 | 15 | 10 |  | 10+14
References:
1 | Elsam, November 2003
2 | Elsam's and Elkraft's update of the Danish Energy Agency's 'Teknologidata for el- og varmeproduktionsanlæg', December 1997
3 | Eltra, September 2003
5 | Danish Energy Agency, 2009.
6 | "Projected costs of generating electricity", International Energy Agency (IEA), 2005.
7 | “Energy technology perspectives 2008”, International Energy Agency, 2008.
8 | Danish Energy Agency, 2008. Measured data (1994-2006) from newest power plants in Denmark.
9 | Own estimate by Danish Energy Agency and Energinet.dk, 2011.
10 | Energinet.dk, 2009
11 | www.ad700.dk
12 | "En opdateret analyse af Danmarks muligheder for at reducere emissionerne af NOx" (Updated analysis of Denmark's options to reduce NOx emissions; in Danish), Danish Environmental Protection Agency, 2009.
13 | National Environmental Research Institute, Denmark, 2009 (data from 2007).
14 | DONG Energy, 2009.
15 | "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
16 | "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
17 | The IEA World Energy Outlook 2014 coal fired Ultra-supercritical power plants in Europe. Values used are the projection for 2020.
18 | The IEA Projected Cost of Generating Electricity 2015 for coal fired power plants. Here both the ‘world median’ is used, and data from recently commissioned plants in the Netherlands. The three units in the Netherlands are chosen because of the proximity to Denmark, because the socio-economic parameters (labour cost etc) are assumed to be similar and because the units are new (all from 2015).
19 | EIA Updated Capital Cost Estimates for Utility Scale Electricity Generating Plants 2013 for pulverizes coal fired advanced single units.[1]
20 | Aggregated data from different projects on existing units that Ea Energy Analyses have been working on since 2010. Data is used for estimating O&M costs.
21 | IEA( 2016),Energy Technology Perspectives
22 | E.S. Rubin et al. / Energy Policy 86 (2015) page 198–218, A review of learning rates for electricity supply technologies
Notes:
A | The Cb values have been calculated from the electricity efficiencies in condensation mode, the Cv values and a total efficiency (electricity plus heat) in full back-pressure mode of 90%. Cf. Annex 1.
B | The data for SO2 and NOx emissions assume flue gas desulphurisation (wet gypsum) and DeNOx equipment of the “high dust” SCR type.
C | Supercritical in 2010 and ultra-supercritical from 2020.
D | Please refer to section 'Regulation ability' in the above qualitative description.
E | Outage rates are generally about 5% for plants that are 10-20 years old. Unless the plant is refurbished, the rate increases to 20% for plants that are 40 years old (ref. 7)
F | It is assumed that the cost is falling by 0.2 % p.a.
Defaltor 2011-2015: 1.059

## 02 LTE existing plant
| Technology | 01a Life time extension of coal power plant, extraction plant
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 300 | 300 | 300 |  | 200 | 400 | 200 | 400
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | +0 | +0 | +0 |  | -1 | +1 |  |  | EF | 7
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | +0 | +0 | +0 |  | -1 | +1 |  |  | EF | 7
| Cb coefficient (50oC/100oC) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Cv coefficient (50oC/100oC) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Forced outage (%) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Planned outage (weeks per year) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Technical lifetime (years) | 15 | 15 | 15 | [6 empty] | 4, 5, 6, 7
| Construction time (years) | 0.5 | 0.5 | 0.5 | [6 empty] | 7
| Space requirement (1000m2/MW) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF
Regulation ability
| Primary regulation (% per 30 seconds) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Secondary regulation (% per minute) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Minimum load (% of full load) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Warm start-up time (hours) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
| Cold start-up time (hours) | +0 | +0 | +0 |  | +0 | +0 |  |  | AF | 7
Environment
| SO2 (degree of desulphuring, %) | +0 | +0 | +0 |  | +0 | +0 |  |  | AFG | 8
| NOX (g per GJ fuel) | +0 | +0 | +0 |  | +0 | +0 |  |  | AFG | 8
| CH4 (g per GJ fuel) | +0 | +0 | +0 |  | +0 | +0 |  |  | AFG | 8
| N2O (g per GJ fuel) | +0 | +0 | +0 |  | +0 | +0 |  |  | AFG | 8
Financial data (in 2015€)
| Nominal investment (M€/MW) | 0.23577 | 0.23577 | 0.23577 |  | 0.14825 | 0.33693 |  |  | CF | 4, 5, 6, 7
| - of which equipment | - | - | - |  | - | -
| - of which installation | - | - | - |  | - | -
| Fixed O&M (€/MW/year) | +0 | +0 | +0 |  | +0 | +8,000 |  |  | ABF | 7
| Variable O&M (€/MWh) | +0 | +0 | +0 |  | +0 | +0 |  |  | ADF | 7
Technology specific data
References:
4 | Projected Costs of Generating electricity edition 2015, IEA, NEA and OECD 2015
5 | Baggrundsnotat omhandlende metode for Energinet.dk's forventninger til kraftværksudviklingen i Danmark, Energinet.dk, 27. august 2014 (Background note concerning method for Energinet.dk's expectations for power plant development in Denmark , Energinet.dk , August 27, 2014)
6 | Studstrupværket kører videre på kul frem til 2015, Ingeniøren, 10. maj 2012,( Studstrupværket continues to run on coal until 2015, Engineer , May 10, 2012, )
7 | Ea Energy Analysis, based on experience from various commercial projects.
8 | It is assumed by Ea Energy Analyses that plants emissions prior to the LTE is within the legal limits.
Notes:
A | Values will generally be similar to those of the plant prior to Life Time Extention (LTE).
B | Values will depend on those of the plant prior to LTE, however the average fixed O&M cost may increase slightly for the extension period compared with the original life time to accomodate the necessary reinvestments during the extended life time.
C | Investment costs will vary largely, depending on the necessary scope of work. The indicated range represents typical cases where 20-25 years Danish coal power CHP plants have been life time extended to obtain additional 15 years life time (based mainly on budgetted values).
D | Variable O&M costs will in general be similar or a bit smaller to those of the plant prior to LTE. The reason for the small improvement is when you compare it to just before the LTE. When compared to the average over the lifetime the O&M costs will be similar.
E | Values will generally be similar to those of the plant prior to LTE. Average efficiencies over the lifetime will be similar to the plant prior to LTE, but the efficiencies just after the LTE will be better than that of the plant just before the LTE.
F | Values for year 2050 are not considered relevant since new coal fired power plants are not expected to be built
G | It is assumed that plants emissions prior to the LTE is within the legal limits.

## 03a Coal to wood pellets exi bo
| Technology | 03 Rebuilding power plants from coal to biomass a) Wood pellets, existing boiler, extraction plant
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 300 | 300 | 300 |  | 200 | 400
| Electricity efficiency (condensation mode for extraction plants). net (%). name plate | -1 | -1 | -1 |  | -0 | -2 |  |  | ABCI | 10
| Electricity efficiency (condensation mode for extraction plants). net (%). annual average | -1 | -1 | -1 |  | -0 | -2 |  |  | ABCI | 10
| Cb coefficient (50oC/100oC) | -0.02 | -0.02 | -0.02 |  | -0 | -0.05 |  |  | ABCI | 10
| Cv coefficient (50oC/100oC) | +0 | +0 | +0 |  | -0.01 | +0.01 |  |  | AC | 10
| Forced outage (%) | +0 | +0 | +0 |  | -1 | +1 |  |  | A | 10
| Planned outage (weeks per year) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Technical lifetime (years) | 15 | 15 | 15 | [5 empty] | C | 10
| Construction time (years) | 2 | 2 | 2 |  | 1.5 | 2.5 |  |  | C | 10
| Space requirement (1000m2/MW) | +0 | +0 | +0 |  | +0 | +0 |  |  | AD
Regulation ability
| Primary regulation (% per 30 seconds) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Secondary regulation (% per minute) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Minimum load (% of full load) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Warm start-up time (hours) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Cold start-up time (hours) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
Environment
| SO2 (degree of desulphuring. %) | N.A. | N.A. | N.A. |  | - | - |  |  | J
| NOX (g per GJ fuel) | 20 | 21 | 18 |  | 19 | 53 |  |  | G
| CH4 (g per GJ fuel) | 0 | 0 | 0 |  | 3.1 | 3.1 |  |  | G
| N2O (g per GJ fuel) | 1 | 1 | 1 |  | 0.8 | 0.8 |  |  | G
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3
Financial data (in 2015€)
| Nominal investment (M€/MWe) | 0.5 | 0.5 | 0.5 |  | 0.35 | 0.8 |  |  | CEK | 10, 11, 12
| - of which equipment | - | - | - |  | - | -
| - of which installation | - | - | - |  | - | -
| Fixed O&M (€/MWe/year) | +3350 | +3350 | +3350 |  | +1350 | +5350 |  |  | AFK | 10
| Variable O&M (€/MWhe) | +0.9 | +0.9 | +0.9 |  | +0.4 | +1.4 |  |  | AFK | 10
Technology specific data
| Fixed O&M (€/MWinput/year) | +1350 | +1350 | +1350 |  | +550 | +2150 |  |  | AFK | 10
| Variable O&M (€/MWhinput) | +0.36 | +0.36 | +0.36 |  | +0.16 | +0.56 |  |  | AFK | 10
References:
10 | Ea Energy Analysis, based on experience from various commercial projects.
11 | Government response to the consultation on proposals for the levels of banded support under the Renewables Obligation for the period 2013-17 and the Renewables Obligation Order 2012, UK Department of Energy and Climate Change, July 2012.
12 | A strategy for converting coal fueled power plants to biomass, Future Metrics, September 2014
Notes:
A | Value depend on the original plant. Value indicate the estimated change from the original value (unit is the same as the paramter).
B | Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency is typically unchanged, thus the Cb value decreases, meaning more heat is produced compared to electricity.
C | Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D | Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
E | The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F | The variable O&M costs will be similar to those of the original plant, however fixed O&M costs are likely to increase by 10-20%
G | Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
I | It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.556. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
J | It is assumed that that Flue Gas Desulphurization plant is bypassed (stopped) due to low Sulphur content in wood pellet fuel
K | O&M cost and CAPEX has been estimated by Ramboll in April 2019 based on input from DE/Ørsted and data from UK Department for Business, Energy & Industry strategy (BEIS) in their Electricity Generation Cost report from 2016.

## 03b Coal to wood chips n. boile
| Technology | 03 Rebuilding power plants from coal to biomass b) Wood chips. new boiler, extraction plant
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 300 | 300 | 300 |  | 200 | 400
| Electricity efficiency (condensation mode for extraction plants). net (%). name plate | -1 | -1 | -1 |  | -0 | -2 |  |  | ABJ | 10
| Electricity efficiency (condensation mode for extraction plants). net (%). annual average | -1 | -1 | -1 |  | -0 | -2 |  |  | ABJ | 10
| Cb coefficient (50oC/100oC) | -0.07 | -0.07 | -0.07 |  | -0.02 | -0.1 |  |  | ABJ | 10
| Cv coefficient (50oC/100oC) | +0 | +0 | +0 |  | -0.01 | +0.01 |  |  | A | 10
| Forced outage (%) | +0 | +0 | +0 |  | -1 | +1 |  |  | A | 10
| Planned outage (weeks per year) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Technical lifetime (years) | 15 | 15 | 15 | [5 empty] | C | 10
| Construction time (years) | 2.5 | 2.5 | 2.5 |  | 2 | 3 |  |  | C | 10
| Space requirement (1000m2/MW) | +0.03 | +0.03 | +0.03 |  | +0.02 | +0.05 |  |  | AD | 10
Regulation ability
| Primary regulation (% per 30 seconds) | -2 | -0 | -0 |  | -0 | -5 |  |  | AI | 10
| Secondary regulation (% per minute) | -2 | -0 | -0 |  | -0 | -5 |  |  | AI | 10
| Minimum load (% of full load) | +0.05 | +0.05 | +0 |  | +0 | +0.1 |  |  | A | 10
| Warm start-up time (hours) | +0.5 | +0.5 | +0 |  | +0 | +2 |  |  | AI | 10
| Cold start-up time (hours) | +1 | +1 | +1 |  | +0 | +2 |  |  | AI | 10
Environment
| SO2 (degree of desulphuring. %) | 98 | 98 | 98 |  | - | -
| NOX (g per GJ fuel) | 30 | 24 | 20 |  | 19 | 53 |  |  | G
| CH4 (g per GJ fuel) | 3 | 2 | 2 |  | 0 | 0.5 |  |  | G
| N2O (g per GJ fuel) | 10 | 8 | 6 |  | 2 | 20 |  |  | G
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1.6107 | 1.6107 | 1.6107 |  | 1.3423 | 2.1477 |  |  | CE | 10. 12
| - of which equipment | - | - | - |  | - | -
| - of which installation | - | - | - |  | - | -
| Fixed O&M (€/MWe/year) | 73750 | 73750 | 73750 |  | 61250 | 86250 |  |  | FK | 10
| Variable O&M (€/MWhe) | 2.75 | 2.75 | 2.75 |  | 1.75 | 3.75 |  |  | FK | 10
Technology specific data
| Fixed O&M (€/MWe/year) | 29500 | 29500 | 29500 |  | 24500 | 34500 |  |  | FK | 10
| Variable O&M (€/MWhe) | 1.1 | 1.1 | 1.1 |  | 0.7 | 1.5 |  |  | FK | 10
References:
10 | Ea Energy Analysis. based on experience from various commercial projects.
12 | A strategy for converting coal fueled power plants to biomass. Future Metrics. September 2014
Notes:
A | Value depend on the original plant.
B | Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency will typically increase to around 105%. thus the Cb value decreases. meaning more heat is produced compared to electricity. This is mainly due to implementation of exhaust gas condenser.
C | Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D | Some additional space will be required for storage of chips (estimated 50%-100% extra).
E | The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F | The fixed O&M costs are likely to increase by 10-20%. whereas the variable O&M costs are likely to increase approx. 50%.
G | Emission values from the datasheet of new CFB biomass plants. See references and notes in the datasheet 'Large Biomass Circulating Fluidized Bed Combustion Systems (CFBC) for wood'.
I | The regulation time of the boiler will often increase due to slower burning of chips compared to pulverized fuel. Depending of the other thermal limitations in the cycle (e.g. in the turbines) this will have no change or an increase in the regulation time.
J | It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.56. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
K | O&M cost are copied from 09 Large Wood Chip CHP corrected with efficiency. Note that all financial data are absolute values and not relative to coal.

## 03c coal to wood chips exi. boi
| Technology | 03 Rebuilding power plants from coal to biomass c) Wood chips, existing boiler, extraction plant
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 300 | 300 | 300 |  | 200 | 400
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | -3 | -3 | -3 |  | -2 | -4 |  |  | ABI | 10
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | -3 | -3 | -3 |  | -2 | -4 |  |  | ABI | 10
| Cb coefficient (50oC/100oC) | -0.07 | -0.07 | -0.07 |  | -0.02 | -0.1 |  |  | ABI | 10
| Cv coefficient (50oC/100oC) | +0 | +0 | +0 |  | -0.01 | +0.01 |  |  | A | 10
| Forced outage (%) | +0 | +0 | +0 |  | -1 | +1 |  |  | A | 10
| Planned outage (weeks per year) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Technical lifetime (years) | 15 | 15 | 15 | [5 empty] | C | 10
| Construction time (years) | 2 | 2 | 2 |  | 1.5 | 2.5 |  |  | C | 10
| Space requirement (1000m2/MW) | +0.04 | +0.04 | +0.04 |  | +0.03 | +0.06 |  |  | AD | 10
Regulation ability
| Primary regulation (% per 30 seconds) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Secondary regulation (% per minute) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Minimum load (% of full load) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Warm start-up time (hours) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
| Cold start-up time (hours) | +0 | +0 | +0 |  | +0 | +0 |  |  | A | 10
Environment
| SO2 (degree of desulphuring, %) | 98 | 98 | 98 |  | - | - |  |  | G
| NOX (g per GJ fuel) | 30 | 24 | 20 |  | 19 | 53 |  |  | G
| CH4 (g per GJ fuel) | 3 | 2 | 2 |  | 3.1 | 3.1 |  |  | G
| N2O (g per GJ fuel) | 10 | 8 | 6 |  | 0.8 | 0.8 |  |  | G
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | [5 empty] | G
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1.6107 | 1.6107 | 1.6107 |  | 1.3423 | 2.1477 |  |  | CE | 10
| - of which equipment | - | - | - |  | - | -
| - of which installation | - | - | - |  | - | -
| Fixed O&M (€/MW/year) | +14,175 | +14,175 | +14,175 |  | +12,600 | +15,750 |  |  | F | 10
| Variable O&M (€/MWh) | +1,5 | +1,5 | +1,5 |  | +1 | +2 |  |  | F | 10
References:
10 | Ea Energy Analysis, based on experience from various commercial projects.
Notes:
A | Value depend on the original plant.
B | Typically the electricity efficiency will be 3-4 % point lower than that of the plant prior to conversion. The thermal efficiency is increased to approximately 100% because of flue gas condensation in drying process, thus the Cb value decreases, meaning more heat is produced compared to electricity.
C | Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D | Some additional space will be required for storage of chips (estimated 50%-100% extra) and for the drying plant.
E | The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F | Both variable and fixed O&M costs are likely to increase by 40-50% from the original plant.
G | Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
I | It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.57. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.

## 03d coal to wood chips exi. boi
| Technology | 03 Rebuilding power plants from coal to biomass d) Wood chips, conversion small coal boiler
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 70 |  |  |  | 50 | 90 |  |  | A, E | 13
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | N/A | [8 empty] | 13
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 27% | [7 empty] | B | 13
| Cb coefficient (50oC/100oC) | 0.35 | [7 empty] | B | 13
| Cv coefficient (50oC/100oC) | N/A | [8 empty] | 13
| Forced outage (%) | 3% | [7 empty] | C | 13
| Planned outage (weeks per year) | 3% | [7 empty] | C | 13
| Technical lifetime (years) | 15
| Construction time (years) | N/A
| Space requirement (1000m2/MW) | N/A
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | [7 empty] | C | 13
| Secondary regulation (% per minute) | 3 | [7 empty] | C | 13
| Minimum load (% of full load) | 45 | [7 empty] | C | 13
| Warm start-up time (hours) | 2 | [7 empty] | C | 13
| Cold start-up time (hours) | 12 | [7 empty] | C | 13
Environment
| SO2 (degree of desulphuring, %) | N/A
| NOX (g per GJ fuel) | 30 | [7 empty] | C | 13
| CH4 (g per GJ fuel) | 3 | [7 empty] | C | 13
| N2O (g per GJ fuel) | 10 | [7 empty] | C | 13
| Particles (g per GJ fuel) | 0.3 | [7 empty] | C | 13
Financial data (in 2015€)
| Nominal investment (M€/MW) | N/A
| - of which equipment | N/A
| - of which installation | N/A
| Fixed O&M (€/MWe/year) | 109259.2593 | [7 empty] | D
| Variable O&M (€/MWhe) | 4.0741 | [7 empty] | D
Technology specific data
| Fixed O&M (€/MW_input/year) | 29500 | [7 empty] | D
| Variable O&M (€/MWh_input) | 1.1 | [7 empty] | D
References:
13 | Ramboll, internal assessment
Notes:
A | Based on existing converted coal plant 50-90 MW capacity
B | The estimated electrcial efficiency is 27 %. It is assumed that plants are equipped with Flue Gas Condensation having total efficiency of 105 %
C | Values are based on Data sheet for Wood Chips CHP, Large
D | O&M data are based data sheet 09 Wood chips CHP, Large, the specific values based on electricity has been corrected base on efficiency
E | Uncertainty estimate applies for 2015 value

## 04 Gas turb. simple cycle, L
| Technology | 04 Gas turbine, simple cycle (large), back pressure
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 40 - 125 | [7 empty] | F
| Electricity efficiency (condensation mode for extraction plants), net (%) | 41 | 42 | 43 | 45 | 38 | 42 | 40 | 44 |  | 6, 12
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 39 | 40 | 41 | 43 | 36 | 40 | 38 | 42 |  | 6, 11
| Cb coefficient (50oC/100oC) | 0.95 | 0.96 | 1 | 1 | 0.8 | 1.2 | 0.8 | 1.2 |  | 6, 12
| Cv coefficient (50oC/100oC) | - | - | - | - | - | - | - | - | J
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 3 |  | 6
| Planned outage (weeks per year) | 3 | 3 | 2.5 | 2.5 | 2 | 3.5 | 1.5 | 3 |  | 6
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | E | 6, 7
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 6
| Space requirement (1000m2/MW) | 0.02 | 0.02 | 0.02 | 0.02 | 0.015 | 0.03 | 0.015 | 0.03 | G | 7
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I
| Secondary regulation (% per minute) | 20 | 20 | 20 | 20 | 20 | 50 | 20 | 50 | C | 6
| Minimum load (% of full load) | 25 | 23 | 20 | 20 | 20 | 25 | 20 | 25 | A | 6
| Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 |  | 5, 6, 8
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1 |  | 5, 6, 8
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 20 | 15 | 10 | 10 | 10 | 30 | 7.5 | 20 | D | 7, 9
| CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 9
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 9
Financial data (in 2015€)
| Nominal investment (M€/MW) | 0.6 | 0.59 | 0.56 | 0.52 | 0.4 | 0.9 | 0.35 | 0.85 |  | 6, 10
| - of which equipment | NA | NA | NA | NA | NA | NA | NA | NA | K
| - of which installation | NA | NA | NA | NA | NA | NA | NA | NA | K
| Fixed O&M (€/MW/year) | 20000 | 19500 | 18600 | 18000 | NA | NA | NA | NA | B | 6
| Variable O&M (€/MWh) | 4.5 | 4.4 | 4.2 | 4 | 4 | 6 | 3 | 5 |  | 6
Technology specific data
References:
5 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6 | Wärtsila Technical Journal "in detail" 02-2014
7 | Data specs from maufacturers (Web) 2015
8 | Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9 | Danish Gas Technology Centre, environmental survey 2012
10 | Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11 | IEA: Projected cost of generating electricity, 2010
12 | COWI 2015 input
13 | The Omes Project results (2005)
14 | WBDG-Publication, B. L. Capehart, Microtubines, 2014
Notes:
A | Very low efficiency at low loads and often increased Nox emisison
B | Insurance excluded, unknown. Daily start assumed
C | Power related
D | Based on Dry Low NOx (DLN) techniques
E | Technical- and design life most often > 25 years
F | Electrical output
G | Combined with DGC assumptions, CHP configuration
H | GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I | No data available, no known use
J | Not relevant for this CHP configuration
K | No data available
L | DGC Estimate
M | Air preheating by internal recuperation included

## 04 Gas turb. simple cycle Sm-Me
| Technology | 04 Gas turbine, simple cycle (small and medium), back pressure
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 5 - 40 | [7 empty] | F
| Electricity efficiency (condensation mode for extraction plants), net (%) | 36 | 37 | 39 | 40 | 32 | 40 | 34 | 42 | G, H | 6, 12
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 34 | 35 | 37 | 38 | 30 | 38 | 32 | 40 |  | 6, 11
| Cb coefficient (50oC/100oC) | 0.71 | 0.73 | 0.8 | 0.8 | 0.61 | 0.8 | 0.7 | 0.9 |  | 6, 12
| Cv coefficient (50oC/100oC) | - | - | - | - | - | - | - | - | J
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 3 |  | 6
| Planned outage (weeks per year) | 3 | 2.8 | 2.5 | 2.5 | 2 | 3.5 | 1.5 | 3 |  | 6
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | E | 6, 7
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 1.5 | 1 | 1.5 |  | 6
| Space requirement (1000m2/MW) | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.07 | 0.03 | 0.07 | G | 7
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I
| Secondary regulation (% per minute) | 20 | 20 | 20 | 20 | 20 | 50 | 20 | 50 | C | 6
| Minimum load (% of full load) | 25 | 23 | 20 | 20 | 20 | 25 | 20 | 25 | A | 6
| Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 |  | 5, 6, 8
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1 |  | 5, 6, 8
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 20 | 15 | 10 | 10 | 10 | 30 | 8 | 20 | D | 7, 9
| CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 |  | 9
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 |  | 9
Financial data (in 2015€)
| Nominal investment (M€/MW) | 0.75 | 0.73 | 0.7 | 0.68 | 0.6 | 1 | 0.55 | 0.95 |  | 6, 10
| - of which equipment | NA | NA | NA | NA | NA | NA | NA | NA | K
| - of which installation | NA | NA | NA | NA | NA | NA | NA | NA | K
| Fixed O&M (€/MW/year) | 20000 | 19500 | 18600 | 18000 | NA | NA | NA | NA | B | 6
| Variable O&M (€/MWh) | 5.5 | 5.4 | 5.1 | 4.6 | 5 | 7 | 4 | 6 |  | 6
Technology specific data
References:
5 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6 | Wärtsila Technical Journal "in detail" 02-2014
7 | Data specs from maufacturers (Web) 2015
8 | Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9 | Danish Gas Technology Centre, environmental survey 2012
10 | Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11 | IEA: Projected cost of generating electricity, 2010
12 | COWI 2015 input
13 | The Omes Project results (2005)
14 | WBDG-Publication, B. L. Capehart, Microtubines, 2014
Notes:
A | Very low efficiency at low loads and often increased Nox emisison
B | Insurance excluded, unknown. Daily start assumed
C | Power related
D | Based on Dry Low NOx (DLN) techniques
E | Technical- and design life most often > 25 years
F | Electrical output
G | Combined with DGC assumptions, CHP configuration
H | GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I | No data available, no known use
J | Not relevant for this CHP configuration
K | No data available
L | DGC Estimate
M | Air preheating by internal recuperation included

## 04 Gas turb. simple cycle Micro
| Technology | Gas turbine, simple cycle (micro), back pressure
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 0.015 - 0.200
| Electricity efficiency (condensation mode for extraction plants), net (%), | 30 | 30 | 30 | 30 | 23 | 32 | 25 | 35 | M | 7
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 28 | 28 | 28 | 28 | 21 | 29 | 23 | 33
| Cb coefficient (50oC/100oC) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.85 | 0.4 | 0.85 |  | 7, 13
| Cv coefficient (50oC/100oC) | - | - | - | - | - | - | - | - | J
| Forced outage (%) | 5 | 5 | 5 | 5 | NA | NA | NA | NA
| Planned outage (weeks per year) | NA | NA | NA | NA | NA | NA | NA | NA
| Technical lifetime (years) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 | L
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.8 | 0.2 | 0.7 | L | 13
| Space requirement (1000m2/MW) | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.15 | 0.05 | 0.15 |  | 7
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary regulation (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 30 | 50 | 25 | 50 | L | 7, 13
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | NA | NA | NA | (NA)
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | NA | NA | NA | (NA)
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13
| NOX (g per GJ fuel) | 10 | 10 | 10 | 10 | 6 | 15 | 6 | 15 |  | 7, 13
| CH4 (g per GJ fuel) | 6 | 6 | 6 | 6 | NA | NA | NA | NA |  | 13
| N2O (g per GJ fuel) | NA | NA | NA | NA | NA | NA | NA | NA |  | 13
Financial data
| Nominal investment (M€/MW) | 1.2 | 1.2 | 1.1 | 1 | NA | NA | NA | NA |  | 13, 14
| - of which equipment | 0.85 | 0.85 | 0.8 | 0.7 | NA | NA | NA | NA |  | 13, 14
| - of which installation | 0.35 | 0.35 | 0.3 | 0.3 | NA | NA | NA | NA |  | 13, 14
| Fixed O&M (€/MW/year) | NA | NA | NA | NA | NA | NA | NA | NA
| Variable O&M (€/MWh) | 15 | 15 | 14 | 13 | 10 | 15 | 8 | 15 |  | 13
References:
5 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6 | Wärtsila Technical Journal "in detail" 02-2014
7 | Data specs from maufacturers (Web) 2015
8 | Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9 | Danish Gas Technology Centre, environmental survey 2012
10 | Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11 | IEA: Projected cost of generating electricity, 2010
12 | COWI 2015 input
13 | The Omes Project results (2005)
14 | WBDG-Publication, B. L. Capehart, Microtubines, 2014
Notes:
A | Very low efficiency at low loads and often increased Nox emisison
B | Insurance excluded, unknown. Daily start assumed
C | Power related
D | Based on Dry Low NOx (DLN) techniques
E | Technical- and design life most often > 25 years
F | Electrical output
G | Combined with DGC assumptions, CHP configuration
H | GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I | No data available, no known use
J | Not relevant for this CHP configuration
K | No data available
L | DGC Estimate
M | Air preheating by internal recuperation included

## 05 Gas turb. CC, steam extract.
| Technology | 05 Gas turbine, combined cycle, extraction plant
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 100 - 500 | [7 empty] | F
| Electricity efficiency (condensation mode for extraction plants), net (%), | 58 | 59 | 61 | 63 | 55 | 61 | 58 | 65 |  | 5
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 55 | 56 | 58 | 60 | 52 | 58 | 55 | 62 |  | 5, 9
| Cb coefficient (50oC/100oC) | 1.7 | 1.8 | 2 | 2.2 | 1.5 | 2.2 | 1.5 | 2.4
| Cv coefficient (50oC/100oC) | 0.15 | 0.15 | 0.15 | 0.15 | N.A | N.A | N.A | N.A | J
| Forced outage (%) | 3 | 3 | 3 | 3 | 2 | 4 | 2 | 4 |  | 5
| Planned outage (weeks per year) | 2.5 | 2.3 | 2 | 2 | 2 | 4 | 2 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | E | 5, 3
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 5
| Space requirement (1000m2/MW) | 0.02 | 0.02 | 0.02 | 0.02 | 0.015 | 0.03 | 0.015 | 0.03 | G | 3
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | - | - | - | - | - | - | - | - | K
| Secondary regulation (% per minute) | 15 | 15 | 15 | 15 | 5 | 15 | 5 | 15 |  | 5, 3, 11
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | A | 5, 3, 11
| Warm start-up time (hours) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | H | 5, 6, 1, 11
| Cold start-up time (hours) | 2.5 | 2.5 | 2.5 | 2 | 2 | 5 | 1.5 | 5 |  | 5, 6, 1, 11
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 20 | 15 | 10 | 8 | 10 | 30 | 5 | 15 | D | 3, 7
| CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 7
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 7
Financial data (in 2015€)
| Nominal investment (M€/MW) | 0.9 | 0.88 | 0.83 | 0.8 | 0.8 | 1.2 | 0.7 | 1.1 |  | 5, 8
| - of which equipment | 0.7 | 0.68 | 0.64 | 0.61 | 0.65 | 1.02 | 0.6 | 0.95 |  | 10
| - of which installation | 0.2 | 0.2 | 0.19 | 0.19 | 0.15 | 0.18 | 0.1 | 0.15 |  | 10
| Fixed O&M (€/MW/year) | 30000 | 29300 | 27800 | 26000 | 25000 | 35000 | 20000 | 30000 | B | 5
| Variable O&M (€/MWh) | 4.5 | 4.4 | 4.2 | 4 | 3 | 7 | 3 | 7 |  | 5
Technology specific data
References:
1 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
3 | Data specs from maufacturers (Web) 2015
5 | Wärtsila Technical Journal "in detail" 02-2014
6 | Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
7 | Danish Gas Technology Centre, environmental survey 2012
8 | Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
9 | IEA: Projected cost of generating electricity, 2010
10 | UK Electricity Generation Costs Update, M.M. Donald, June 2010
11 | Siemens : Data on GT-CC (2010)
Notes:
A | Low efficiency at low loads and often increased NOx emission
B | Limited availability of data
C | Power related
D | Based on Dry Low NOx (DLN) techniques
E | Technical- and design life most often > 25 years
F | Electrical output
G | CHP configuration, Including DGC assumptions
H | Manufacturers says down to 30 minute
I | No data available
J | Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
K | No known use
L | No Relevance for Back Pressure Lay Out
M | Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min

## 05 Gas turb. CC, Back-pressure
| Technology | 05 Gas turbine, combined cycle, back pressure
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 10 -100 | [7 empty] | F
| Electricity efficiency (condensation mode for extraction plants), net (%), | 50 | 51 | 53 | 55 | 42 | 55 | 45 | 58 |  | 5
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 47 | 48 | 50 | 52 | 39 | 52 | 42 | 55 |  | 5, 9
| Cb coefficient (50oC/100oC) | 1.2 | 1.3 | 1.4 | 1.55 | 0.9 | 1.6 | 1.1 | 1.7
| Cv coefficient (50oC/100oC) | - | - | - | - | - | - | - | - | L
| Forced outage (%) | 3 | 3 | 3 | 3 | 2 | 4 | 2 | 4 |  | 5
| Planned outage (weeks per year) | 2.5 | 2.3 | 2 | 2 | 2 | 4 | 1.5 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | E | 5 ,3
| Construction time (years) | 2.5 | 2 | 2 | 2 | 2 | 3 | 2 | 3 |  | 5
| Space requirement (1000m2/MW) | 0.025 | 0.025 | 0.025 | 0.025 | 0.019 | 0.038 | 0.019 | 0.038 | G | 3
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | - | - | - | - | - | - | - | - | I
| Secondary regulation (% per minute) | 15 | 15 | 15 | 15 | 5 | 15 | 5 | 15 | C, M | 5, 3, 11
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | A | 5, 3, 11
| Warm start-up time (hours) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | H | 5, 6, 1, 11
| Cold start-up time (hours) | 2.5 | 2.5 | 2.5 | 2 | 2 | 5 | 1.5 | 5 |  | 5, 6, 1, 11
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 20 | 15 | 10 | 8 | 10 | 30 | 5 | 15 | D | 3, 7
| CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 7
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 7
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1.3 | 1.3 | 1.2 | 1.1 | 1.1 | 1.8 | 0.9 | 1.6 |  | 5, 9
| - of which equipment | 1 | 1 | 0.9 | 0.8 | 0.8 | 1.4 | 0.65 | 1.25 |  | 10
| - of which installation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.25 | 0.35 |  | 10
| Fixed O&M (€/MW/year) | 30000 | 29300 | 27800 | 26000 | 25000 | 35000 | 20000 | 30000 | B | 5
| Variable O&M (€/MWh) | 4.5 | 4.4 | 4.2 | 4 | 3 | 7 | 3 | 7 |  | 5
Technology specific data
References:
1 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
3 | Data specs from maufacturers (Web) 2015
5 | Wärtsila Technical Journal "in detail" 02-2014
6 | Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
7 | Danish Gas Technology Centre, environmental survey 2012
8 | Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
9 | IEA: Projected cost of generating electricity, 2010
10 | UK Electricity Generation Costs Update, M.M. Donald, June 2010
11 | Siemens : Data on GT-CC (2010)
Notes:
A | Low efficiency at low loads and often increased NOx emission
B | Limited availability of data
C | Power related
D | Based on Dry Low NOx (DLN) techniques
E | Technical- and design life most often > 25 years
F | Electrical output
G | CHP configuration, Including DGC assumptions
H | Manufacturers says down to 30 minute
I | No data available
J | Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
K | No known use
L | No Relevance for Back Pressure Lay Out
M | Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min

## 06 Gas engines, natural gas
| Technology | 06 Spark ignition engine, natural gas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 1 -10 MWe
| Electricity efficiency (condensation mode for extraction plants), net (%) | 46 | 47 | 48 | 50 | 40 | 48 | 44 | 52 | A | 3, 4
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 44 | 45 | 47 | 48 | 38 | 46 | 42 | 50 | A | 3, 4, 7
| Cb coefficient (50oC/100oC) | 0.9 | 0.95 | 0.99 | 1.04 | 0.65 | 1.02 | 0.65 | 1.15 |  | 3, 4, 7
| Cv coefficient (50oC/100oC) | - | - | - | - | - | - | - | - | G
| Forced outage (%) | 3 | 3 | 3 | 3 | 2 | 5 | 2 | 5 |  | 5, 6
| Planned outage (weeks per year) | 0.8 | 0.8 | 0.8 | 0.8 | N.A | N.A | N.A | N.A | H | 5, 6
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | D | 4, 5, 7
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | B | 3, 6
| Space requirement (1000m2/MW) | 0.04 | 0.04 | 0.035 | 0.03 | 0.03 | 0.05 | 0.025 | 0.04
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | 25 | 30 | 35 | 50 | 10 | 40 | 25 | 100 |  | 12
| Secondary regulation (% per minute) | 25 | 30 | 40 | 50 | 20 | 100 | 25 | 100 | C | 6, 12, 13
| Minimum load (% of full load) | 50 | 50 | 50 | 50 | 30 | 50 | 25 | 50 |  | 6
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | 0.05 | 0.015 | 0.15 | 0.015 | 0.15 | C | 6, 10
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.4 | 0.2 | 0.4 | E | 6, 10
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4
| NOX (g per GJ fuel) | 75 | 60 | 60 | 60 | 50 | 100 | 50 | 100 |  | 4
| CH4 (g per GJ fuel) | 315 | 315 | 280 | 250 | 300 | 400 | 250 | 350 |  | 4
| N2O (g per GJ fuel) | 0.6 | 0.6 | 0.6 | 0.6 | N.A | N.A | N.A | N.A | H
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1 | 0.95 | 0.9 | 0.85 | 0.9 | 1.1 | 0.8 | 1.1 |  | 3, 5, 11
| - of which equipment | 0.65 | 0.6 | 0.55 | 0.55 | N.A | N.A | N.A | N.A | H | 3, 5
| - of which installation | 0.35 | 0.35 | 0.35 | 0.3 | N.A | N.A | N.A | N.A | H | 3, 5
| Fixed O&M (€/MW/year) | 10000 | 9750 | 9300 | 8500 | 7000 | 20000 | 6000 | 15000 | F | 5
| Variable O&M (€/MWh) | 5.4 | 5.4 | 5.1 | 4.9 | 4 | 12 | 4 | 10 | F | 3, 5, 11
References:
3 | ASUE BHKW Kenndata 2014/2015
4 | DGC Efficiency and emission test reports
5 | DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6 | Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7 | Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8 | Ongoing Sulpur research project at DGC (MUDP)
10 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11 | Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12 | Suppliers association information etc.
13 | MAN Turbo Presentation of Gas Engine with fuel switch, 2012
Notes:
A | Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B | The construction time given is for a medium size installation; small installations can be erected in a shorter period
C | Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D | Technical- and design life most often > 25 years
E | For a medium size engine; small engines with less thermal mass might be faster
F | When operating 4000 hours a year
G | Only relevant for steam based CHP
H | No data available
I | DGC estimate for years 2030, 2050
J | No known use, data from n-gas engines
K | Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water

## 06 Gas engines, biogas
| Technology | 06 Spark ignition engine, biogas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 1-10 MWe
| Electricity efficiency (condensation mode for extraction plants), net (%), | 42 | 43 | 45 | 47 | 38 | 44 | 42 | 48 | A | 3, 4
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 40 | 41 | 43 | 45 | 36 | 42 | 40 | 46 | A | 3, 4, 7
| Cb coefficient (50oC/100oC) | 0.82 | 0.86 | 0.92 | 1 | 0.59 | 0.96 | 0.75 | 1.1 |  | 3, 4, 7
| Cv coefficient (50oC/100oC) | - | - | - | - | - | - | - | - | G
| Forced outage (%) | 3 | 3 | 3 | 3 | 2 | 5 | 2 | 5 |  | 5, 6
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | N.A | N.A | N.A | N.A | H | 5, 6
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | D | 4, 5, 7
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | B | 3, 6
| Space requirement (1000m2/MW) | 0.04 | 0.04 | 0.035 | 0.03 | 0.03 | 0.05 | 0.025 | 0.05
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | 25 | 30 | 40 | 50 | 10 | 40 | 25 | 100 | J | 8
| Secondary regulation (% per minute) | 25 | 30 | 40 | 50 | 20 | 100 | 25 | 100 | C | 6, 8, 13
| Minimum load (% of full load) | 50 | 50 | 50 | 50 | 30 | 50 | 25 | 50 |  | 6
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | 0.05 | 0.015 | 0.15 | 0.015 | 0.15 | C | 6, 10
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.4 | 0.2 | 0.4 | E | 6, 10
Environment
| SO2 (degree of desulphuring, %) | (I) | (I) | (I) | (I) | 0 | 99.9 | 0 | 99.9 | K | 8
| NOX (g per GJ fuel) | 100 | 100 | 100 | 100 | 90 | 120 | 90 | 120 |  | 4
| CH4 (g per GJ fuel) | 300 | 300 | 300 | 300 | 300 | 400 | 300 | 400 |  | 4
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | N.A | N.A | N.A | N.A | J
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1 | 0.95 | 0.9 | 0.85 | 0.8 | 1.2 | 0.8 | 1.2 |  | 3, 5, 11
| - of which equipment | 0.65 | 0.6 | 0.55 | 0.55 | N.A | N.A | N.A | N.A |  | 3, 5
| - of which installation | 0.35 | 0.35 | 0.35 | 0.3 | N.A | N.A | N.A | N.A |  | 3, 5
| Fixed O&M (€/MW/year) | 10000 | 9750 | 9300 | 8500 | 7000 | 20000 | 6000 | 15000 | F | 5
| Variable O&M (€/MWh) | 8 | 7.5 | 7 | 6 | 6 | 13 | 4 | 12 | F | 3, 5, 11
References:
3 | ASUE BHKW Kenndata 2014/2015
4 | DGC Efficiency and emission test reports
5 | DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6 | Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7 | Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8 | Ongoing Sulpur research project at DGC (MUDP)
10 | Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11 | Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12 | Suppliers association information etc.
13 | MAN Turbo Presentation of Gas Engine with fuel switch, 2012
Notes:
A | Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B | The construction time given is for a medium size installation; small installations can be erected in a shorter period
C | Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D | Technical- and design life most often > 25 years
E | For a medium size engine; small engines with less thermal mass might be faster
F | When operating 4000 hours a year
G | Only relevant for steam based CHP
H | No data available
I | DGC estimate for years 2030, 2050
J | No known use, data from n-gas engines
K | Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water

## 07 Carbon Capture and Storage
| Technology | CO2 capture (post-combustion), pulverized coal power plant
|  | 2010 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one unit (MW) | 500 - 740 |  |  |  |  | 1+2+3+4
| Capture efficiency (%) | 90 | 90 | 90 | 90 | A | 1
| Generation efficiency decrease (%-points) | 8-10% | 8-10% | 8-10% | 8-10% | B | 1+2+3
Financial data
Capture, post-combustion
| Nominal investment (M€/MW) | 2.3-4.3 | 3.07 | 3.00 | 2.86 | C | 1+2+3+4;2;2;2
| Fixed O&M (€/MW/year) | 72000-87000 | 72000-87000 | 72000-87000 | 72000-87000 | D | 1+2
| Variable O&M (€/MWh) | 3.4-4.1 | 3.4-4.1 | 3.4-4.1 | 3.4-4.1 | D | 1+2
References:
1 | "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
2 | "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
3 | "Energy Technology Perspectives", IEA 2010
4 | "ProjectCosts of generating Electricity", IEA & NEA, 2010
Notes:
A | The non-captured CO2 is released into the atmosphere.
B | Some of the electricity consumption may be regained as useful heat. The displayed efficiency decreases do most probably take the usage of heat into account.
C | The nominal investment is per net generating capacity, i.e. after deducting the power consumed for CO2 capture. If you compare two power plants, with CCS (this element) and without CCS (element 01), and with the same net power generating capacity, the difference in nominal investment (e.g. 3.07-2.03 = 1.04 M€/MW in 2020) is the value of the capture equipment. If CO2 capture is added on to an existing power plant, the loss in generating capacity shall be taken into account.
D | The O&M costs are per net generating capacity and net generation, i.e. after deducting the power consumer for CO2 capture.
This sheet has been moved from a previous datasheet and
does therefore not follow the same guideline as the remainder
of the data sheets in the file.

## 08 WtE CHP, Large, 40 degree
| Technology | Large Waste to Energy CHP, Back pressure turbine, 220 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 51.7747 | 51.7747 | 52.9998 | 54.9114 | 46.9803 | 56.4429 | 46.9803 | 60.6511 | A, B
| Electricity efficiency, net (%), name plate | 23.5339 | 23.5339 | 24.0908 | 24.9597 | 21 | 26 | 21 | 28 | A, B
| Electricity efficiency, net (%), annual average | 22.3572 | 22.3572 | 22.8863 | 23.7118 | 19 | 25 | 19 | 27 | A, B,C
| Auxiliary electricity consumption (% of thermal input) | 2.9099 | 2.9099 | 2.9215 | 2.911 | 2.1471 | 3.1962 | 1.7177 | 3.2382 | A, B
| Cb coefficient (40°C/80°C) | 0.29787 | 0.29787 | 0.30618 | 0.3187 | 0.27028 | 0.32472 | 0.27267 | 0.35201 | A, B
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B
| Forced outage (%) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1
| Planned outage (weeks per year) | 2.5 | 2.3775 | 2.1501 | 1.7586 | 2.0209 | 2.7341 | 1.319 | 2.1983 | E | 1
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.77258 | 0.77258 | 0.75472 | 0.72845 | 0.65669 | 0.88847 | 0.54633 | 0.91056 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | F
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | F, G
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | F, G
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | F, G
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | F, G
Environment
| SO2 (degree of desulphuring, %) | 99.7923 | 99.7923 | 99.7923 | 99.7923 | 98.9617 | 99.8962 | 99.4808 | 99.8962 | H | 1
| NOX (g per GJ fuel) | 80 | 60 | 20 | 10 | 10 | 60 | 10 | 60 | I | 2;3;5
| CH4 (g per GJ fuel) | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (M€/MWe) | 7.9525 | 7.7557 | 7.3755 | 6.4553 | 6.5923 | 9.0926 | 4.7188 | 8.0283 | N | 1
| - of which equipment | 4.794 | 4.6754 | 4.5135 | 3.9564 | 3.9741 | 5.5502 | 2.8446 | 4.9046 | N | 1
| - of which installation | 3.1585 | 3.0803 | 2.862 | 2.4989 | 2.6183 | 3.5424 | 1.8742 | 3.1236 | M | 1
| Fixed O&M (€/MWe/year) | 229000 | 186000 | 174000 | 148000 | 158000 | 218000 | 109000 | 184000 | L | 1
| Variable O&M (€/MWh_e) | 24.991 | 24.991 | 24.427 | 23.5998 | 21.2641 | 28.8025 | 17.7371 | 29.4858 | K | 1
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | D
| Combustion air humidification | No | No | No | No | No | Yes | No | Yes | D
| Incineration capacity (Fuel input) (tonnes/h) | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | A, B
| Output of recovered condensate (tonne/MWh_input) | 0.10999 | 0.10999 | 0.11329 | 0.11906 | 0.098605 | 0.14127 | 0.098605 | 0.14535 | D, K
| Nominal investment (M€/MW fuel input) | 1.8715 | 1.8252 | 1.7768 | 1.6112 | 1.5514 | 2.1398 | 1.1778 | 2.0038 | N | 1
| - of which equipment | 1.1282 | 1.1003 | 1.0873 | 0.98752 | 0.93525 | 1.3062 | 0.71001 | 1.2242 | N | 1
| - of which installation | 0.74333 | 0.72493 | 0.68949 | 0.62372 | 0.61619 | 0.83367 | 0.46779 | 0.77965 | M | 1
| Fixed O&M (€/MW input/year) | 54000 | 43900 | 41900 | 37000 | 37300 | 51300 | 27100 | 46000 | L | 1
| Variable O&M (€/MWh input) * | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Nominal investment (€/(tonne/year)) | 690 | 670 | 650 | 590 | 570 | 790 | 430 | 740 | N | 1
| Fixed O&M (€/tonne) | 19.8682 | 16.1483 | 15.4302 | 13.6148 | 13.726 | 18.8713 | 9.9855 | 16.9433 | L | 1;4
| Variable O&M (€/tonne) | 17.324 | 17.324 | 17.3337 | 17.3507 | 14.7404 | 19.9661 | 13.0404 | 21.6781 | K | 1;4
| Heat efficiency, net (%), name plate | 79.0087 | 79.0087 | 78.6831 | 78.3178 | 74 | 84 | 71 | 86 | A, B
| Heat efficiency, net (%), annual average | 80.1854 | 80.1854 | 79.8876 | 79.5658 | 76 | 85 | 73 | 87 | A, B, C
| Additional heat potential with heat pumps (% of thermal input) | 4.1506 | 4.1506 | 4.0149 | 3.7398 | 1 | 6 | 1 | 6 | A, B, D
References:
1 | Rambøll present work, range of WtE-projects
2 | Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.
Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants
2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and
emission inventory for decentralised CHP production. National Environmental Research Institute,
Aarhus University. 113 pp. – NERI Technical report No. 786.
http://www.dmu.dk/Pub/FR786.pdf.
3 | Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013,"
http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4 | Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5 | Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019
https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf
Notes:
A | Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B | With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 40°C and flow 80°C.
C | Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E | Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F | Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G | The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H | Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I | Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
J | N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L | Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M | Installation includes civils works (including waste bunker) and project cost.
N | Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.

## 08 WtE CHP, Large, 50 degree
| Technology | Large Waste to Energy CHP, Back pressure turbine, 220 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 46.8131 | 46.8131 | 48.1977 | 50.1453 | 42.0581 | 51.6062 | 42.0581 | 55.8832 | A, B
| Electricity efficiency, net (%), name plate | 21.2787 | 21.2787 | 21.908 | 22.7933 | 19 | 24 | 19 | 26 | A, B
| Electricity efficiency, net (%), annual average | 20.2148 | 20.2148 | 20.8126 | 21.6537 | 17 | 23 | 17 | 25 | A, B,C
| Auxiliary electricity consumption (% of thermal input) | 2.9566 | 2.9566 | 2.9667 | 2.9534 | 2.1847 | 3.2244 | 1.7478 | 3.2647 | A, B
| Cb coefficient (50°C/100°C) | 0.28264 | 0.28264 | 0.29176 | 0.30345 | 0.25393 | 0.31158 | 0.25451 | 0.33817 | A, B
| Cv coefficient (50°C/100°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B
| Forced outage (%) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1
| Planned outage (weeks per year) | 2.5 | 2.3775 | 2.1501 | 1.7586 | 2.0209 | 2.7341 | 1.319 | 2.1983 | E | 1
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.85446 | 0.85446 | 0.82992 | 0.79768 | 0.72629 | 0.98263 | 0.59826 | 0.9971 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | F
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | F, G
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | F, G
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | F, G
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | F, G
Environment
| SO2 (degree of desulphuring, %) | 99.7923 | 99.7923 | 99.7923 | 99.7923 | 98.9617 | 99.8962 | 99.4808 | 99.8962 | H | 1
| NOX (g per GJ fuel) | 80 | 60 | 20 | 10 | 10 | 60 | 10 | 60 | I | 2;3;5
| CH4 (g per GJ fuel) | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (M€/MWe) | 8.7954 | 8.5777 | 8.1104 | 7.0689 | 7.291 | 10.0563 | 5.1673 | 8.7913 | N | 1
| - of which equipment | 5.3021 | 5.1709 | 4.9632 | 4.3325 | 4.3952 | 6.1384 | 3.115 | 5.3708 | N | 1
| - of which installation | 3.4933 | 3.4068 | 3.1472 | 2.7364 | 2.8958 | 3.9178 | 2.0523 | 3.4205 | M | 1
| Fixed O&M (€/MWe/year) | 254000 | 206000 | 191000 | 162000 | 175000 | 241000 | 119000 | 202000 | L | 1
| Variable O&M (€/MWh_e) | 27.2767 | 27.2767 | 26.5199 | 25.5378 | 23.1118 | 31.6963 | 19.0439 | 32.151 | K | 1
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | D
| Combustion air humidification | No | No | No | No | No | Yes | No | Yes | D
| Incineration capacity (Fuel input) (tonnes/h) | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | 74.6885 | A, B
| Output of recovered condensate (tonne/MWh_input) | 0.032747 | 0.032747 | 0.03862 | 0.049538 | 0.012212 | 0.10746 | 0.012212 | 0.11405 | D, K
| Nominal investment (M€/MW fuel input) | 1.8715 | 1.8252 | 1.7768 | 1.6112 | 1.5514 | 2.1398 | 1.1778 | 2.0038 | N | 1
| - of which equipment | 1.1282 | 1.1003 | 1.0873 | 0.98752 | 0.93525 | 1.3062 | 0.71001 | 1.2242 | N | 1
| - of which installation | 0.74333 | 0.72493 | 0.68949 | 0.62372 | 0.61619 | 0.83367 | 0.46779 | 0.77965 | M | 1
| Fixed O&M (€/MW input/year) | 54000 | 43900 | 41900 | 37000 | 37300 | 51300 | 27100 | 46000 | L | 1
| Variable O&M (€/MWh input) * | 5.8 | 5.8 | 5.81 | 5.82 | 4.92 | 6.74 | 4.34 | 7.33 | K | 1
| Nominal investment (€/(tonne/year)) | 690 | 670 | 650 | 590 | 570 | 790 | 430 | 740 | N | 1
| Fixed O&M (€/tonne) | 19.8682 | 16.1483 | 15.4302 | 13.6148 | 13.726 | 18.8713 | 9.9855 | 16.9433 | L | 1;4
| Variable O&M (€/tonne) | 17.0965 | 17.0965 | 17.1138 | 17.1459 | 14.486 | 19.8665 | 12.786 | 21.5859 | K | 1;4
| Heat efficiency, net (%), name plate | 75.2853 | 75.2853 | 75.0896 | 75.1144 | 70 | 84 | 68 | 85 | A, B
| Heat efficiency, net (%), annual average | 76.3492 | 76.3492 | 76.185 | 76.254 | 72 | 85 | 70 | 86 | A, B, C
| Additional heat potential with heat pumps (% of thermal input) | 10.0383 | 10.0383 | 9.7086 | 9.0423 | 4 | 12 | 4 | 12 | A, B, D
References:
1 | Rambøll present work, range of WtE-projects
2 | Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.
Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants
2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and
emission inventory for decentralised CHP production. National Environmental Research Institute,
Aarhus University. 113 pp. – NERI Technical report No. 786.
http://www.dmu.dk/Pub/FR786.pdf.
3 | Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013,"
http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4 | Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5 | Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019
https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf
Notes:
A | Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B | With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 50°C and flow 100°C.
C | Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E | Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F | Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G | The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H | Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I | Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
J | N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L | Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M | Installation includes civils works (including waste bunker) and project cost.
N | Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.

## 08 WtE CHP, Medium
| Technology | Medium Waste to Energy CHP, Back pressure turbine, 80 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 18.6104 | 18.6104 | 19.0304 | 19.6913 | 16.9079 | 20.2436 | 16.9079 | 21.6627 | A, B
| Electricity efficiency, net (%), name plate | 23.263 | 23.263 | 23.788 | 24.6141 | 21 | 26 | 21 | 28 | A, B,C
| Electricity efficiency, net (%), annual average | 22.0999 | 22.0999 | 22.5986 | 23.3834 | 19 | 25 | 19 | 26 | A, B,C
| Auxiliary electricity consumption (% of thermal input) | 2.9101 | 2.9101 | 2.9217 | 2.9112 | 2.1472 | 3.1965 | 1.7178 | 3.2684 | A, B
| Cb coefficient (40°C/80°C) | 0.29513 | 0.29513 | 0.30295 | 0.31481 | 0.26813 | 0.32103 | 0.27031 | 0.34633 | A, B
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B
| Forced outage (%) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1
| Planned outage (weeks per year) | 3 | 2.853 | 2.5802 | 2.1103 | 2.425 | 3.2809 | 1.5828 | 2.6379 | E | 1
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 1.612 | 1.612 | 1.5764 | 1.5235 | 1.3702 | 1.8538 | 1.1426 | 1.9044 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | F
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | F, G
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | F, G
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | F, G
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | F, G
Environment
| SO2 (degree of desulphuring, %) | 99.7923 | 99.7923 | 99.7923 | 99.7923 | 98.9617 | 99.8962 | 99.4808 | 99.8962 | H | 1
| NOX (g per GJ fuel) | 80 | 60 | 40 | 10 | 10 | 60 | 10 | 60 | I | 2;3;5
| CH4 (g per GJ fuel) | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (M€/MWe) | 9.2503 | 9.0213 | 8.6011 | 7.5389 | 7.6681 | 10.5894 | 5.5018 | 9.3728 | N | 1
| - of which equipment | 5.6232 | 5.484 | 5.311 | 4.6625 | 4.6614 | 6.5215 | 3.3445 | 5.7773 | N | 1
| - of which installation | 3.6271 | 3.5373 | 3.2901 | 2.8764 | 3.0067 | 4.0679 | 2.1573 | 3.5955 | M | 1
| Fixed O&M (€/MWe/year) | 298000 | 262000 | 245000 | 209000 | 223000 | 306000 | 154000 | 260000 | L | 1
| Variable O&M (€/MWh_e) | 25.2821 | 25.2821 | 24.7381 | 23.9312 | 21.5118 | 29.138 | 17.9863 | 29.8916 | K | 1
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | D
| Combustion air humidification | No | No | No | No | No | Yes | No | Yes | D
| Incineration capacity (Fuel input) (tonnes/h) | 27.1594 | 27.1594 | 27.1594 | 27.1594 | 27.1594 | 27.1594 | 27.1594 | 27.1594 | A, B
| Output of recovered condensate (tonne/MWh_input) | 0.11001 | 0.11001 | 0.11331 | 0.11907 | 0.098624 | 0.14129 | 0.098624 | 0.14332 | D, K
| Nominal investment (M€/MW fuel input) | 2.1519 | 2.0986 | 2.046 | 1.8556 | 1.7838 | 2.4634 | 1.3542 | 2.307 | N | 1
| - of which equipment | 1.3081 | 1.2757 | 1.2634 | 1.1476 | 1.0844 | 1.5171 | 0.82322 | 1.422 | N | 1
| - of which installation | 0.84377 | 0.82288 | 0.78265 | 0.70799 | 0.69945 | 0.94631 | 0.531 | 0.88499 | M | 1
| Fixed O&M (€/MW input/year) | 69300 | 61000 | 58200 | 51400 | 51900 | 71200 | 37800 | 64000 | L | 1
| Variable O&M (€/MWh input) * | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Nominal investment (€/(tonne/year)) | 790 | 770 | 750 | 680 | 660 | 910 | 500 | 850 | N | 1
| Fixed O&M (€/tonne) | 25.5114 | 22.4605 | 21.4186 | 18.9197 | 19.0915 | 26.1978 | 13.9136 | 23.5576 | L | 1;4
| Variable O&M (€/tonne) | 17.324 | 17.324 | 17.3338 | 17.3507 | 14.7405 | 19.9662 | 13.0405 | 21.6721 | K | 1;4
| Heat efficiency, net (%), name plate | 78.8227 | 78.8227 | 78.5214 | 78.1873 | 74 | 84 | 71 | 86 | A, B
| Heat efficiency, net (%), annual average | 79.9858 | 79.9858 | 79.7108 | 79.418 | 76 | 85 | 73 | 88 | A, B, C
| Additional heat potential with heat pumps (% of thermal input) | 4.1506 | 4.1506 | 4.0149 | 3.7398 | 1 | 6 | 1 | 6 | A, B, D
References:
1 | Rambøll present work, range of WtE-projects
2 | Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.
Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants
2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and
emission inventory for decentralised CHP production. National Environmental Research Institute,
Aarhus University. 113 pp. – NERI Technical report No. 786.
http://www.dmu.dk/Pub/FR786.pdf.
3 | Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013,"
http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4 | Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5 | Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019
https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf
Notes:
A | Assumed lower heating value 10.6 MJ/kg, waste input 27.2 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 80 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, restpectively. Efficiencies refer to lower heating value.
B | With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C | Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E | Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F | Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G | The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H | Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I | Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J | N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L | Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M | Installation includes civils works (including waste bunker) and project cost
N | Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O | Through a turbine by-pass all the produced steam energy can be used for District Heat production. It can be assumed that all electricity production is converted into heat production in by-pass.

## 08 WtE CHP, Small
| Technology | Small Waste to Energy CHP, Back pressure turbine, 35 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 7.9551 | 7.9551 | 8.1163 | 8.342 | 7.2451 | 8.6182 | 7.2451 | 9.1851 | A, B
| Electricity efficiency, net (%), name plate | 22.7288 | 22.7288 | 23.1894 | 23.8344 | 20 | 25 | 20 | 27 | A, B,C
| Electricity efficiency, net (%), annual average | 21.5924 | 21.5924 | 22.0299 | 22.6426 | 18 | 24 | 18 | 25 | A, B,C
| Auxiliary electricity consumption (% of thermal input) | 2.9099 | 2.9099 | 2.9216 | 2.9389 | 2.1471 | 3.2286 | 1.7177 | 3.2998 | A, B
| Cb coefficient (40°C/80°C) | 0.28712 | 0.28712 | 0.29381 | 0.30055 | 0.26149 | 0.31105 | 0.26103 | 0.33093 | A, B
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B
| Forced outage (%) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1
| Planned outage (weeks per year) | 3.5 | 3.3285 | 3.0102 | 2.4621 | 2.8292 | 3.8277 | 1.8466 | 3.0776 | E | 1
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 2.5141 | 2.5141 | 2.4642 | 2.3975 | 2.137 | 2.8912 | 1.7981 | 2.9969 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA | F
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | F, G
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | F, G
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | F, G
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | F, G
Environment
| SO2 (degree of desulphuring, %) | 99.7923 | 99.7923 | 99.7923 | 99.7923 | 98.9617 | 99.8962 | 99.4808 | 99.8962 | H | 1
| NOX (g per GJ fuel) | 80 | 60 | 40 | 20 | 10 | 60 | 10 | 60 | I | 2;3;5
| CH4 (g per GJ fuel) | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (M€/MWe) | 10.6511 | 10.3875 | 9.9377 | 8.7701 | 8.8293 | 12.2051 | 6.392 | 10.9008 | N | 1
| - of which equipment | 6.6251 | 6.4611 | 6.2775 | 5.5487 | 5.4919 | 7.6898 | 3.9759 | 6.8739 | N | 1
| - of which installation | 4.026 | 3.9264 | 3.6602 | 3.2215 | 3.3374 | 4.5153 | 2.4161 | 4.0269 | M | 1
| Fixed O&M (€/MWe/year) | 425000 | 411000 | 382000 | 328000 | 349000 | 478000 | 242000 | 408000 | L | 1
| Variable O&M (€/MWh_e) | 25.8766 | 25.8766 | 25.3769 | 24.7023 | 22.0177 | 29.8137 | 18.5749 | 30.8609 | K | 1
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | D
| Combustion air humidification | No | No | No | No | No | Yes | No | Yes | D
| Incineration capacity (Fuel input) (tonnes/h) | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | A, B
| Output of recovered condensate (tonne/MWh_input) | 0.11006 | 0.11006 | 0.11336 | 0.11625 | 0.098681 | 0.13921 | 0.098681 | 0.14126 | D, K
| Nominal investment (M€/MW fuel input) | 2.4209 | 2.3609 | 2.3045 | 2.0903 | 2.0068 | 2.7741 | 1.5235 | 2.5981 | N | 1
| - of which equipment | 1.9022 | 1.4685 | 1.4557 | 1.3225 | 1.2482 | 1.7478 | 0.94762 | 1.6384 | N | 1
| - of which installation | 1.1559 | 0.89242 | 0.84879 | 0.76782 | 0.75855 | 1.0263 | 0.57587 | 0.95978 | M | 1
| Fixed O&M (€/MW input/year) | 96500 | 93400 | 88600 | 78100 | 79400 | 108500 | 57700 | 97300 | L | 1
| Variable O&M (€/MWh input) * | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Nominal investment (€/(tonne/year)) | 890 | 870 | 850 | 770 | 740 | 1020 | 560 | 960 | N | 1
| Fixed O&M (€/tonne) | 35.5467 | 34.3726 | 32.6072 | 28.7411 | 29.2167 | 39.9629 | 21.23 | 35.8178 | L | 1;4
| Variable O&M (€/tonne) | 17.3242 | 17.3242 | 17.3339 | 17.3424 | 14.7407 | 19.96 | 13.0407 | 21.6661 | K | 1;4
| Heat efficiency, net (%), name plate | 79.1624 | 79.1624 | 78.9274 | 79.3015 | 75 | 85 | 72 | 86 | A, B
| Heat efficiency, net (%), annual average | 80.2988 | 80.2988 | 80.0869 | 80.4933 | 77 | 86 | 74 | 88 | A, B, C
| Additional heat potential with heat pumps (% of thermal input) | 4.1506 | 4.1506 | 4.0149 | 3.8774 | 1 | 6 | 1 | 6 | A, B, D
References:
1 | Rambøll present work, range of WtE-projects
2 | Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.
Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants
2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and
emission inventory for decentralised CHP production. National Environmental Research Institute,
Aarhus University. 113 pp. – NERI Technical report No. 786.
http://www.dmu.dk/Pub/FR786.pdf
3 | Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013,"
http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4 | Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5 | Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019
https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf
Notes:
A | Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B | With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C | Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E | Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F | Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G | The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H | Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I | Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J | N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L | Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M | Installation includes civils works (including waste bunker) and project cost
N | Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..

## 08 WtE HOP
| Technology | Waste to Energy, DH only, 35 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 36.9496 | 36.9496 | 37.0376 | 37.2147 | 36.2641 | 37.9162 | 36.2641 | 38.0804 | A, B
| Total heat efficiency, net (%), ref. LHV, name plate | 105.5703 | 105.5703 | 105.8217 | 106.3278 | 103 | 109 | 103 | 109 | A, B, C
| Total heat efficiency , net (%), ref. LHV, annual average | 105.5703 | 105.5703 | 105.8217 | 106.3278 | 103 | 109 | 103 | 109 | A, B, C
| Auxiliary electricity consumption (% of heat gen) | 2.5848 | 2.5848 | 2.5501 | 2.4842 | 1.9033 | 2.7727 | 1.4903 | 2.7608 | A, B, C
| Forced outage (%) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1
| Planned outage (weeks per year) | 3 | 2.853 | 2.5802 | 2.1103 | 2.425 | 3.2809 | 1.5828 | 2.6379 | E | 1
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1 | -
| Construction time (years) | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement (1000 m2/MWth heat output) | 0.54128 | 0.54128 | 0.53999 | 0.53742 | 0.46009 | 0.62247 | 0.40307 | 0.67178 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | G
| Minimum load (% of full load) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | G
| Warm start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | G
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | G
Environment
| SO2 (degree of desulphuring, %) | 99.7923 | 99.7923 | 99.7923 | 99.7923 | 98.9617 | 99.8962 | 99.4808 | 99.8962 | H | 1
| NOX (g per GJ fuel) | 80 | 60 | 40 | 20 | 10 | 60 | 10 | 60 | I | 2;3;5 | -
| CH4 (g per GJ fuel) | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (M€/MWth - heat output) | 1.784 | 1.7399 | 1.7066 | 1.5418 | 1.5164 | 2.1075 | 1.2323 | 2.1092 | P
| - of which equipment | 1.0239 | 0.99858 | 1.0033 | 0.90852 | 0.87034 | 1.2334 | 0.70725 | 1.2342 | P |  | -
| - of which installation | 0.76008 | 0.74127 | 0.70335 | 0.63323 | 0.64607 | 0.87409 | 0.525 | 0.87501 | P
| Fixed O&M (€/MWth/year), heat output | 80700 | 78000 | 73900 | 64700 | 66800 | 91500 | 49400 | 83500 | P
| Variable O&M (€/MWh) heat output | 7.2223 | 7.3773 | 8.159 | 8.4688 | 6.3156 | 8.3842 | 6.8578 | 10.2104 | K, P
| - of which is electricity costs (€/MWh-heat) | 1.6284 | 1.7835 | 2.5756 | 2.9065 | 1.6747 | 1.8185 | 2.7674 | 3.0835 | K, P
| - of which is other O&M costs (€/MWh-heat) | 5.5938 | 5.5938 | 5.5834 | 5.5624 | 4.6408 | 6.5657 | 4.0904 | 7.1268 | K, P
Technology specific data
| Flue gas condensation | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | D
| Combustion air humidification | No | No | No | No | No | Yes | No | Yes | D
| Output of recovered condensate (tonne/MWh_input) | 0.13406 | 0.13406 | 0.13702 | 0.14295 | 0.12183 | 0.16575 | 0.12183 | 0.16999 | D, K
| Incineration capacity (Fuel input) (tonnes/h) | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | 11.8823 | A, B
| Nominal investment (M€/MW fuel input) | 1.8834 | 1.8368 | 1.806 | 1.6393 | 1.6009 | 2.2249 | 1.3102 | 2.2427 | N | 1
| - of which equipment | 1.081 | 1.0542 | 1.0617 | 0.96601 | 0.91882 | 1.3021 | 0.752 | 1.3123 | N | 1
| - of which installation | 0.80242 | 0.78256 | 0.7443 | 0.6733 | 0.68206 | 0.92278 | 0.55822 | 0.93037 | M | 1
| Fixed O&M (€/MW input/year) | 85200 | 82300 | 78200 | 68800 | 70500 | 96600 | 52600 | 88800 | L | 1
| Variable O&M including electricity (€/MWh input) | 7.62 | 7.79 | 8.63 | 9 | 6.84 | 8.69 | 7.46 | 10.58 | K | 1
| Nominal investment (€/(tonne/year)) | 690 | 680 | 660 | 600 | 590 | 820 | 480 | 830 | N | 1
| Fixed O&M (€/tonne) | 31.3534 | 30.3043 | 28.7767 | 25.3409 | 25.9712 | 35.5719 | 19.3503 | 32.6849 | L | 1;4
| Variable O&M (€/tonne) | 22.4587 | 22.9409 | 25.4319 | 26.524 | 20.1529 | 25.5882 | 21.9778 | 31.1615 | K | 1;4
| - of which electricity costs (€/tonne) | 5.0638 | 5.5461 | 8.0283 | 9.103 | 5.3441 | 5.5499 | 8.869 | 9.4108 | K | 1;4
| - of which other O&M costs (€/tonne) | 17.3949 | 17.3949 | 17.4036 | 17.4211 | 14.8088 | 20.0382 | 13.1088 | 21.7507 | K | 1;4
| Additional heat potential with heat pumps (% of thermal input) | 4.1506 | 4.1506 | 4.0149 | 3.7398 | 1 | 6 | 1 | 6 | A, B, D
References:
1 | Rambøll present work, range of WtE-projects
2 | Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.
Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants
2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and
emission inventory for decentralised CHP production. National Environmental Research Institute,
Aarhus University. 113 pp. – NERI Technical report No. 786.
http://www.dmu.dk/Pub/FR786.pdf.
3 | Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013,"
http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4 | Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5 | Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019
https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf
Notes:
A | Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Efficiencies refer to lower heating value.
B | With flue gas condensation (condensation through heat exchange with DH-water, only), DH return temperature 40°C and flow 80°C.
C | The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E | Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F
G | The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (instead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H | Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream of the flue gas treatment system. Sulphur content in fuel 270 g/GJ
I | Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J | N2O is expected to be related primarily to the use of SNCR. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
L | Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M | Installation includes civils works (including waste bunker) and project cost .
N | Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
P | Reference to heat output because of the lack of electricity production.

## 09a Wood Chips, Large 40 degree
| Technology | Large Wood Chips CHP, 600 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 182.2401 | 182.6228 | 183.2811 | 180.083 | 166.3174 | 242.8899 | 174.3983 | 251.008 | A
| Electricity efficiency, net (%), name plate | 30.3734 | 30.4371 | 30.5469 | 30.0138 | 27 | 41 | 29 | 42 | A, H | 1
| Electricity efficiency, net (%), annual average | 28.8547 | 28.9153 | 29.0195 | 28.5131 | 24 | 39 | 26 | 40 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.9624 | 2.941 | 2.9426 | 2.935 | 2.1813 | 3.2721 | 1.7993 | 3.4321 |  | 1
| Cb coefficient (40°C/80°C) | 0.37316 | 0.37325 | 0.37512 | 0.36611 | 0.33993 | 0.49643 | 0.35455 | 0.5103
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.082309 | 0.082137 | 0.081841 | 0.083295 | 0.069816 | 0.094457 | 0.062471 | 0.10412 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E+G | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 94.925 | 98.985 | 97.97 | 98.985 | F | 1,2,3
| NOX (g per GJ fuel) | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | 1,2,3
| CH4 (g per GJ fuel) | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | 1,2,3
| N2O (g per GJ fuel) | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | 1,2,3
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2,3
Financial data
| Nominal investment (M€/MWe) | 3.3778 | 3.2873 | 3.1153 | 2.935 | 2.7934 | 3.9422 | 2.3185 | 4.0301 | J, K | 1
| - of which equipment | 2.1875 | 2.1289 | 2.0176 | 1.9243 | 1.7838 | 2.5763 | 1.4805 | 2.6336 | K
| - of which installation | 1.1902 | 1.1584 | 1.0978 | 1.0107 | 1.0096 | 1.3659 | 0.83794 | 1.3966 | K
| Fixed O&M (€/MWe/year) | 97000 | 95000 | 89000 | 84000 | 80000 | 111000 | 64000 | 110000
| Variable O&M (€/MWh_e) | 4.3893 | 4.3872 | 4.3712 | 4.4502 | 3.1053 | 4.9345 | 2.7786 | 5.3745 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.22132 | 0.22132 | 0.22124 | 0.22166 | 0 | 0.22327 | 0 | 0.22324 | C, L
| Nominal investment (M€/MW fuel input) | 1.0259 | 1.0006 | 0.95164 | 0.88091 | 0.85023 | 1.1999 | 0.69586 | 1.2096 | J, K | 1
| - of which equipment | 0.66443 | 0.64799 | 0.61631 | 0.57757 | 0.54294 | 0.78415 | 0.44436 | 0.79043 | K
| - of which installation | 0.36152 | 0.35257 | 0.33533 | 0.30334 | 0.30729 | 0.41574 | 0.2515 | 0.41916 | K
| Fixed O&M (€/MW input/year) | 29500 | 28800 | 27300 | 25100 | 24300 | 33900 | 19100 | 32900
| Variable O&M (€/MWh input) | 1.33 | 1.34 | 1.34 | 1.34 | 0.95 | 1.5 | 0.83 | 1.61 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.01 | 0.0097525 | 0.0092757 | 0.0083909 | 0.0085 | 0.0115 | 0.0069568 | 0.011595 | K
| Heat efficiency, net (%), name plate | 81.3951 | 81.5454 | 81.4328 | 81.9799 | 44 | 85 | 43 | 83 | B, H | 1
| Heat efficiency, net (%), annual average | 82.9138 | 83.0672 | 82.9601 | 83.4806 | 47 | 87 | 46 | 85 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.9432 | 1.8691 | 1.8689 | 1.8699 | 1 | 28 | 1 | 28 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3 | Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 40°C and flow 80°C.
At DH return temperature 40 °C and flow 80 °C, for year 2015, the name plate net electricity efficiency increases by about 2.1%-point, to 30.4% and the net name plate heat efficiency is increased about 0.5%-point, to 81.4%, the Cb coefficient increases about 0.02, and the additional heat potential with heat pumps reduced by around 2.7%-point. Other cases experience similar changes.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F | It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note. The N2O level is relatively high due to the use of a CFB.
G | Warm start is starting with a glowing bed and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09a Wood Chips, Large 50 degree
| Technology | Large Wood Chips CHP, 600 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 169.5293 | 169.8425 | 170.4686 | 167.4763 | 153.6782 | 230.2133 | 162.187 | 238.7485 | A
| Electricity efficiency, net (%), name plate | 28.2549 | 28.3071 | 28.4114 | 27.9127 | 25 | 39 | 27 | 40 | A, H | 1
| Electricity efficiency, net (%), annual average | 26.8421 | 26.8917 | 26.9909 | 26.5171 | 23 | 37 | 24 | 38 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.9781 | 2.9563 | 2.9578 | 2.9502 | 2.2017 | 3.2889 | 1.8156 | 3.4488 |  | 1
| Cb coefficient (50°C/100°C) | 0.34939 | 0.34888 | 0.35063 | 0.34231 | 0.31567 | 0.47289 | 0.3315 | 0.48798
| Cv coefficient (50°C/100°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.08848 | 0.088317 | 0.087993 | 0.089565 | 0.07507 | 0.10156 | 0.067174 | 0.11196 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E+G | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 94.925 | 98.985 | 97.97 | 98.985 | F | 1,2,3
| NOX (g per GJ fuel) | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | 1,2,3
| CH4 (g per GJ fuel) | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | 1,2,3
| N2O (g per GJ fuel) | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | 1,2,3
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2,3
Financial data
| Nominal investment (M€/MWe) | 3.631 | 3.5346 | 3.3495 | 3.156 | 3.0036 | 4.2388 | 2.493 | 4.3335 | J, K | 1
| - of which equipment | 2.3516 | 2.2891 | 2.1692 | 2.0692 | 1.918 | 2.7701 | 1.592 | 2.8318 | K
| - of which installation | 1.2795 | 1.2455 | 1.1803 | 1.0868 | 1.0856 | 1.4687 | 0.90102 | 1.5017 | K
| Fixed O&M (€/MWe/year) | 105000 | 102000 | 96000 | 90000 | 86000 | 120000 | 69000 | 118000
| Variable O&M (€/MWh_e) | 4.5977 | 4.6015 | 4.5843 | 4.6676 | 3.3389 | 5.1899 | 2.9877 | 5.6615 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.18721 | 0.18721 | 0.18713 | 0.18755 | 0 | 0.19047 | 0 | 0.19044 | C, L
| Nominal investment (M€/MW fuel input) | 1.0259 | 1.0006 | 0.95164 | 0.88091 | 0.85023 | 1.1999 | 0.69586 | 1.2096 | J, K | 1
| - of which equipment | 0.66443 | 0.64799 | 0.61631 | 0.57757 | 0.54294 | 0.78415 | 0.44436 | 0.79043 | K
| - of which installation | 0.36152 | 0.35257 | 0.33533 | 0.30334 | 0.30729 | 0.41574 | 0.2515 | 0.41916 | K
| Fixed O&M (€/MW input/year) | 29500 | 28800 | 27300 | 25100 | 24300 | 33900 | 19100 | 32900
| Variable O&M (€/MWh input) | 1.3 | 1.3 | 1.3 | 1.3 | 0.95 | 1.47 | 0.83 | 1.58 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.01 | 0.0097525 | 0.0092757 | 0.0083909 | 0.0085 | 0.0115 | 0.0069568 | 0.011595 | K
| Heat efficiency, net (%), name plate | 80.8694 | 81.1376 | 81.0304 | 81.5429 | 46 | 84 | 45 | 83 | B, H | 1
| Heat efficiency, net (%), annual average | 82.2822 | 82.553 | 82.451 | 82.9385 | 48 | 86 | 48 | 85 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 4.6395 | 4.4624 | 4.462 | 4.4641 | 4 | 28 | 4 | 28 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3 | Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 50°C and flow 100°C.
At DH return temperature 40 °C and flow 80 °C, for year 2015, the name plate net electricity efficiency increases by about 2.1%-point, to 30.4% and the net name plate heat efficiency is increased about 0.5%-point, to 81.4%, the Cb coefficient increases about 0.02, and the additional heat potential with heat pumps reduced by around 2.7%-point. Other cases experience similar changes.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F | It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note. The N2O level is relatively high due to the use of a CFB.
G | Warm start is starting with a glowing bed and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09a Wood Chips, Medium
| Technology | Medium Wood Chips CHP, 80 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 23.7703 | 23.7703 | 23.8607 | 23.428 | 22.1679 | 31.7831 | 22.737 | 32.7311 | A
| Electricity efficiency, net (%), name plate | 29.7129 | 29.7129 | 29.8259 | 29.285 | 27 | 40 | 28 | 41 | A, H, F | 1
| Electricity efficiency, net (%), annual average | 28.2272 | 28.2272 | 28.3346 | 27.8208 | 24 | 38 | 25 | 39 | A, H, F | 1
| Auxiliary electricity consumption (% of thermal input) | 2.9611 | 2.9611 | 2.9627 | 2.9548 | 2.1853 | 3.2707 | 1.7985 | 3.4305 |  | 1
| Cb coefficient (40°C/80°C) | 0.36575 | 0.36575 | 0.36768 | 0.35852 | 0.3411 | 0.48905 | 0.34795 | 0.50089
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 0.21035 | 0.21035 | 0.20955 | 0.21342 | 0.17879 | 0.2419 | 0.16006 | 0.26677
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E+G | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 94.925 | 98.985 | 97.97 | 98.985 | F | 1,2,3
| NOX (g per GJ fuel) | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 | F | 1,2,3
| CH4 (g per GJ fuel) | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | 1,2,3
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1,2,3
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2,3
Financial data
| Nominal investment (M€/MWe) | 3.6331 | 3.5432 | 3.3572 | 3.1955 | 2.9666 | 4.1781 | 2.4634 | 4.3764 | J, K | 1
| - of which equipment | 2.4331 | 2.3729 | 2.2483 | 2.1738 | 1.9465 | 2.798 | 1.6164 | 2.9647 | K
| - of which installation | 1.2 | 1.1703 | 1.1089 | 1.0216 | 1.02 | 1.38 | 0.84703 | 1.4117 | K
| Fixed O&M (€/MWe/year) | 154000 | 149000 | 140000 | 129000 | 126000 | 173000 | 97000 | 167000
| Variable O&M (€/MWh_e) | 4.4872 | 4.4872 | 4.4699 | 4.5539 | 3.181 | 5.0551 | 2.8477 | 5.5085 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.22132 | 0.22132 | 0.22124 | 0.22166 | 0 | 0.22327 | 0 | 0.22324 | C, L
| Nominal investment (M€/MW fuel input) | 1.0795 | 1.0528 | 1.0013 | 0.9358 | 0.88145 | 1.2414 | 0.72142 | 1.2816 | J, K | 1
| - of which equipment | 0.72294 | 0.70504 | 0.67057 | 0.63661 | 0.57837 | 0.83138 | 0.47336 | 0.86822 | K
| - of which installation | 0.35656 | 0.34774 | 0.33074 | 0.29919 | 0.30308 | 0.41005 | 0.24805 | 0.41342 | K
| Fixed O&M (€/MW input/year) | 45800 | 44400 | 41800 | 37800 | 37300 | 51500 | 28300 | 48800
| Variable O&M (€/MWh input) | 1.33 | 1.33 | 1.33 | 1.33 | 0.95 | 1.5 | 0.83 | 1.61 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.015 | 0.014629 | 0.013914 | 0.012586 | 0.01275 | 0.01725 | 0.010435 | 0.017392 | K
| Heat efficiency, net (%), name plate | 81.2372 | 81.2372 | 81.1194 | 81.6831 | 46 | 84 | 43 | 83 | B, H | 1
| Heat efficiency, net (%), annual average | 82.7228 | 82.7228 | 82.6107 | 83.1473 | 49 | 86 | 46 | 85 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.9432 | 1.9432 | 1.943 | 1.944 | 1 | 26 | 1 | 28 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3 | Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The boiler in the plant is a grate fired boiler producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel. It is to be expected that it is necessary with a specific DeNOx plant (SNCR might not be sufficient).
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Through a turbine by-pass all the produced steam energy is used for District Heat production.
C | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | It is to be expected that necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 40 g/GJ in which case SCR is used with slight adverse effect on electricity efficiency. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note.
G | Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09a Wood Chips, Small
| Technology | Small Wood Chips CHP, 20 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 2.933 | 2.933 | 2.9446 | 2.887 | 2.8461 | 2.9749 | 2.7859 | 2.9786 | A
| Electricity efficiency, net (%), name plate | 14.6649 | 14.6649 | 14.7231 | 14.4348 | 14 | 15 | 13 | 15 | A, H | 1
| Electricity efficiency, net (%), annual average | 13.9316 | 13.9316 | 13.9869 | 13.7131 | 12 | 15 | 12 | 15 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.734 | 2.734 | 2.735 | 2.7299 | 2.0804 | 2.9894 | 1.6612 | 2.9899 |  | 1
| Cb coefficient (40°C/80°C) | 0.15183 | 0.15183 | 0.15253 | 0.14908 | 0.14734 | 0.154 | 0.14386 | 0.15381
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.6819 | 0.6819 | 0.67921 | 0.69277 | 0.57962 | 0.78419 | 0.51958 | 0.86596
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | D | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | D | 1
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 94.925 | 98.985 | 97.97 | 98.985 | F | 1,2
| NOX (g per GJ fuel) | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | F | 1,2
| CH4 (g per GJ fuel) | 20 | 10 | 8 | 4 | 4 | 16 | 2 | 16 | F | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1,2
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2
Financial data
| Nominal investment (M€/MWe) | 6.4781 | 6.3177 | 5.9851 | 5.7965 | 5.5064 | 7.4498 | 4.5785 | 7.905 | E, J, K | 1
| - of which equipment | 4.0232 | 3.9236 | 3.7171 | 3.7039 | 3.4197 | 4.6267 | 2.8435 | 5.0134 | K
| - of which installation | 2.4548 | 2.3941 | 2.268 | 2.0927 | 2.0866 | 2.8231 | 1.735 | 2.8917 | K
| Fixed O&M (€/MWe/year) | 285000 | 281000 | 273000 | 270000 | 241000 | 326000 | 205000 | 347000
| Variable O&M (€/MWh_e) | 9.2612 | 9.2612 | 9.2246 | 9.4088 | 6.445 | 10.4137 | 5.7774 | 11.35 | L
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.2462 | 0.2462 | 0.2462 | 0.2462 | 0 | 0.24842 | 0 | 0.24842 | C, L
| Nominal investment (M€/MW fuel input) | 0.95 | 0.92649 | 0.88119 | 0.83672 | 0.8075 | 1.0925 | 0.66089 | 1.1411 | J, K | 1
| - of which equipment | 0.59 | 0.5754 | 0.54727 | 0.53465 | 0.5015 | 0.6785 | 0.41045 | 0.72367 | K
| - of which installation | 0.36 | 0.35109 | 0.33392 | 0.30207 | 0.306 | 0.414 | 0.25044 | 0.41741 | K
| Fixed O&M (€/MW input/year) | 41800 | 41200 | 40200 | 39000 | 35300 | 47800 | 29600 | 50100
| Variable O&M (€/MWh input) | 1.36 | 1.36 | 1.36 | 1.36 | 0.95 | 1.53 | 0.83 | 1.64 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.02 | 0.019505 | 0.018551 | 0.016782 | 0.017 | 0.023 | 0.013914 | 0.023189 | K
| Heat efficiency, net (%), name plate | 96.5846 | 96.5846 | 96.5239 | 96.8245 | 71 | 98 | 69 | 98 | B, H | 1
| Heat efficiency, net (%), annual average | 97.3179 | 97.3179 | 97.2601 | 97.5463 | 73 | 98 | 70 | 98 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.9432 | 1.9432 | 1.943 | 1.944 | 1 | 26 | 1 | 28 | C | 1
References:
1 | Rambøll Danmark, internal model and evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E | Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G | Warm start is starting with a glowing fuel layer on the grate.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | Cv=1 describes turbine by-pass operation. During operation the turbine can be by-passed fully or partly for direct district heating production, at operator choice.
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09b Wood Pellets, Large 40 degr
| Technology | Large Wood Pellets CHP, 800 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 267.517 | 268.0993 | 268.8387 | 268.8387 | 262.3523 | 348.1933 | 262.3523 | 348.581 | A
| Electricity efficiency, net (%), name plate | 33.4396 | 33.5124 | 33.6048 | 33.6048 | 32 | 44 | 32 | 44 | A, H | 1
| Electricity efficiency, net (%), annual average | 31.7676 | 31.8368 | 31.9246 | 31.9246 | 29 | 42 | 29 | 42 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 3.2838 | 3.2669 | 3.2701 | 3.2701 | 2.4078 | 3.6904 | 1.9262 | 3.6921 |  | 1
| Cb coefficient (40°C/80°C) | 0.51328 | 0.51349 | 0.51567 | 0.51567 | 0.50249 | 0.6669 | 0.50323 | 0.66863
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.056071 | 0.055949 | 0.055796 | 0.055796 | 0.047557 | 0.064342 | 0.041847 | 0.069744
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 1
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring, %) | 98.25 | 98.25 | 98.25 | 98.25 | 95.625 | 99.125 | 98.25 | 99.125 |  | 1,2
| NOX (g per GJ fuel) | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | C+F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 |  | 1,2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 1,2
Financial data
| Nominal investment (M€/MWe) | 2.309 | 2.2483 | 2.1353 | 1.937 | 1.9062 | 2.6411 | 1.5661 | 2.655 | J,K | 1
| - of which equipment | 1.2891 | 1.2559 | 1.194 | 1.0854 | 1.0412 | 1.4708 | 0.86007 | 1.4784 | K
| - of which installation | 1.0198 | 0.99244 | 0.94132 | 0.85153 | 0.86498 | 1.1703 | 0.70599 | 1.1767 | K
| Fixed O&M (€/MWe/year) | 64000 | 62000 | 59000 | 54000 | 53000 | 72000 | 42000 | 71000
| Variable O&M (€/MWh_e) | 1.7169 | 1.7189 | 1.714 | 1.714 | 1.3763 | 1.9612 | 1.211 | 2.1172 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.056599 | 0.056599 | 0.056599 | 0.056599 | 0 | 0.058575 | 0 | 0.058575 | C,L
| Nominal investment (M€/MW fuel input) | 0.77211 | 0.75347 | 0.71756 | 0.65091 | 0.63882 | 0.88509 | 0.52627 | 0.89221 | J,K | 1
| - of which equipment | 0.43108 | 0.42088 | 0.40123 | 0.36476 | 0.34894 | 0.4929 | 0.28903 | 0.4968 | K
| - of which installation | 0.34103 | 0.33259 | 0.31633 | 0.28616 | 0.28988 | 0.39219 | 0.23725 | 0.39541 | K
| Fixed O&M (€/MW input/year) | 21400 | 20900 | 20000 | 18300 | 17600 | 24300 | 14100 | 23900
| Variable O&M (€/MWh input) * | 0.57 | 0.58 | 0.58 | 0.58 | 0.46 | 0.66 | 0.41 | 0.71 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.0025 | 0.0024381 | 0.0023189 | 0.0020977 | 0.002125 | 0.002875 | 0.0017392 | 0.0028987 | K
| Heat efficiency, net (%), name plate | 65.1483 | 65.2636 | 65.1668 | 65.1668 | 43 | 67 | 43 | 67 | B, H | 1
| Heat efficiency, net (%), annual average | 66.8202 | 66.9392 | 66.8471 | 66.8471 | 46 | 69 | 46 | 69 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.73 | 1.664 | 1.6639 | 1.6639 | 1 | 13 | 1 | 13 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an increased electrical efficiency and subsequently re-heating of steam is introduced.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D | This is given by grid code (Energinet.dk)
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G | Warm start is starting with the steam system being pressurized.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09b Wood Pellets, Large 50 degr
| Technology | Large Wood Pellets CHP, 800 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 252.9486 | 253.4357 | 254.1496 | 254.1496 | 248.1088 | 333.423 | 248.1088 | 333.795 | A
| Electricity efficiency, net (%), name plate | 31.6186 | 31.6795 | 31.7687 | 31.7687 | 31 | 42 | 31 | 42 | A, H | 1
| Electricity efficiency, net (%), annual average | 30.0376 | 30.0955 | 30.1803 | 30.1803 | 27 | 40 | 27 | 40 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 3.2976 | 3.2803 | 3.2834 | 3.2834 | 2.4257 | 3.7051 | 1.9405 | 3.7069 |  | 1
| Cb coefficient (50°C/100°C) | 0.48976 | 0.48902 | 0.49111 | 0.49111 | 0.47874 | 0.64336 | 0.47944 | 0.64501
| Cv coefficient (50°C/100°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.059301 | 0.059187 | 0.05902 | 0.05902 | 0.050309 | 0.068065 | 0.044265 | 0.073775
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 1
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring, %) | 98.25 | 98.25 | 98.25 | 98.25 | 95.625 | 99.125 | 98.25 | 99.125 |  | 1,2
| NOX (g per GJ fuel) | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | C+F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 |  | 1,2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 1,2
Financial data
| Nominal investment (M€/MWe) | 2.4419 | 2.3784 | 2.2587 | 2.0489 | 2.0165 | 2.7939 | 1.6566 | 2.8085 | J,K | 1
| - of which equipment | 1.3634 | 1.3285 | 1.263 | 1.1482 | 1.1015 | 1.5559 | 0.90978 | 1.5638 | K
| - of which installation | 1.0786 | 1.0499 | 0.99573 | 0.90075 | 0.91503 | 1.238 | 0.7468 | 1.2447 | K
| Fixed O&M (€/MWe/year) | 68000 | 66000 | 63000 | 58000 | 56000 | 77000 | 45000 | 75000
| Variable O&M (€/MWh_e) | 1.7198 | 1.7262 | 1.7212 | 1.7212 | 1.4559 | 1.9826 | 1.281 | 2.1477 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.026248 | 0.026248 | 0.026248 | 0.026248 | 0 | 0.029392 | 0 | 0.029392 | C,L
| Nominal investment (M€/MW fuel input) | 0.77211 | 0.75347 | 0.71756 | 0.65091 | 0.63882 | 0.88509 | 0.52627 | 0.89221 | J,K | 1
| - of which equipment | 0.43108 | 0.42088 | 0.40123 | 0.36476 | 0.34894 | 0.4929 | 0.28903 | 0.4968 | K
| - of which installation | 0.34103 | 0.33259 | 0.31633 | 0.28616 | 0.28988 | 0.39219 | 0.23725 | 0.39541 | K
| Fixed O&M (€/MW input/year) | 21400 | 20900 | 20000 | 18300 | 17600 | 24300 | 14100 | 23900
| Variable O&M (€/MWh input) * | 0.54 | 0.55 | 0.55 | 0.55 | 0.46 | 0.63 | 0.41 | 0.68 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.0025 | 0.0024381 | 0.0023189 | 0.0020977 | 0.002125 | 0.002875 | 0.0017392 | 0.0028987 | K
| Heat efficiency, net (%), name plate | 64.5594 | 64.7812 | 64.6877 | 64.6877 | 43 | 67 | 43 | 67 | B, H | 1
| Heat efficiency, net (%), annual average | 66.1403 | 66.3652 | 66.2762 | 66.2762 | 47 | 69 | 47 | 69 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 4.1302 | 3.9725 | 3.9721 | 3.9721 | 3 | 13 | 3 | 13 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an increased electrical efficiency and subsequently re-heating of steam is introduced.
The system is optimised at DH return temperature 50°C and flow 100°C.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D | This is given by grid code (Energinet.dk)
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G | Warm start is starting with the steam system being pressurized.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09b Wood Pellets, Medium
| Technology | Medium Wood Pellets CHP, 80 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 24.6764 | 24.6764 | 24.749 | 24.4042 | 23.8401 | 33.3574 | 23.7759 | 34.0297 | A
| Electricity efficiency, net (%), name plate | 30.8455 | 30.8455 | 30.9362 | 30.5052 | 29 | 42 | 29 | 43 | A, H, F | 1
| Electricity efficiency, net (%), annual average | 29.3032 | 29.3032 | 29.3894 | 28.9799 | 26 | 40 | 26 | 41 | A, H, F | 1
| Auxiliary electricity consumption (% of thermal input) | 2.5131 | 2.5131 | 2.5143 | 2.5081 | 1.9147 | 2.9424 | 1.5273 | 3.051 |  | 1
| Cb coefficient (40°C/80°C) | 0.45568 | 0.45568 | 0.45766 | 0.4483 | 0.44023 | 0.61598 | 0.43676 | 0.62512
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 0.18236 | 0.18236 | 0.18183 | 0.18439 | 0.15501 | 0.20971 | 0.1383 | 0.23049
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | D | 1
| Minimum load (% of full load) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | E | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 98.25 | 98.25 | 98.25 | 98.25 | 95.625 | 99.125 | 98.25 | 99.125 | F | 1,2
| NOX (g per GJ fuel) | 80 | 50 | 40 | 20 | 40 | 50 | 10 | 40 | F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1,2
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2
Financial data
| Nominal investment (M€/MWe) | 3.0831 | 3.0068 | 2.8514 | 2.7142 | 2.5035 | 3.5456 | 2.0719 | 3.713 | J,K | 1
| - of which equipment | 1.9695 | 1.9207 | 1.8215 | 1.7694 | 1.557 | 2.2649 | 1.2885 | 2.4074 | K
| - of which installation | 1.1136 | 1.0861 | 1.0299 | 0.94485 | 0.94657 | 1.2807 | 0.78336 | 1.3056 | K
| Fixed O&M (€/MWe/year) | 128000 | 124000 | 117000 | 108000 | 104000 | 144000 | 81000 | 140000
| Variable O&M (€/MWh_e) | 1.8606 | 1.8606 | 1.8549 | 1.8822 | 1.4953 | 2.1301 | 1.3341 | 2.3316 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.056599 | 0.056599 | 0.056599 | 0.056599 | 0 | 0.058575 | 0 | 0.058575 | C,L
| Nominal investment (M€/MW fuel input) | 0.951 | 0.92746 | 0.88212 | 0.82797 | 0.77223 | 1.0937 | 0.63202 | 1.1326 | J,K | 1
| - of which equipment | 0.6075 | 0.59246 | 0.5635 | 0.53975 | 0.48025 | 0.69862 | 0.39306 | 0.73437 | K
| - of which installation | 0.3435 | 0.335 | 0.31862 | 0.28823 | 0.29197 | 0.39502 | 0.23896 | 0.39827 | K
| Fixed O&M (€/MW input/year) | 39500 | 38300 | 36200 | 33100 | 32100 | 44400 | 24600 | 42700
| Variable O&M (€/MWh input) * | 0.57 | 0.57 | 0.57 | 0.57 | 0.46 | 0.66 | 0.41 | 0.71 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.003 | 0.0029257 | 0.0027827 | 0.0025173 | 0.00255 | 0.00345 | 0.002087 | 0.0034784 | K
| Heat efficiency, net (%), name plate | 67.6913 | 67.6913 | 67.5969 | 68.0458 | 44 | 71 | 42 | 71 | A, H, F | 1
| Heat efficiency, net (%), annual average | 69.2336 | 69.2336 | 69.1437 | 69.5711 | 47 | 73 | 45 | 73 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.729 | 1.729 | 1.7288 | 1.7298 | 1 | 11 | 1 | 13 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent back pressure steam turbine. It is possible to pulverize wood pellets and use it for suspension firing but it has not been possible to find an appropriate reference.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Through a turbine by-pass all the produced steam energy is used for District Heat production.
C | Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | SNCR is assumed at NOx emissions at no less than 40 g/GJ. At lower NOx-levels it is chosen to include a tail-end SCR catalyst with slight adverse effect on electricity efficiency.
G | Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09b Wood Pellets, Small
| Technology | Small Wood Pellets CHP, 20 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3.082 | 3.082 | 3.0912 | 3.0454 | 3.0029 | 3.1177 | 2.9543 | 3.1214 | A
| Electricity efficiency, net (%), name plate | 15.4101 | 15.4101 | 15.456 | 15.2271 | 15 | 16 | 14 | 16 | A, H | 1
| Electricity efficiency, net (%), annual average | 14.6396 | 14.6396 | 14.6832 | 14.4658 | 13 | 15 | 13 | 15 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.2902 | 2.2902 | 2.2911 | 2.287 | 1.744 | 2.5032 | 1.3926 | 2.5037 |  | 1
| Cb coefficient (40°C/80°C) | 0.1847 | 0.1847 | 0.18536 | 0.18209 | 0.17996 | 0.18684 | 0.17664 | 0.18663
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.48669 | 0.48669 | 0.48525 | 0.49254 | 0.41369 | 0.5597 | 0.36941 | 0.61568
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | D | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | D | 1
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 98.25 | 98.25 | 98.25 | 98.25 | 95.625 | 99.125 | 98.25 | 99.125 | F | 1
| NOX (g per GJ fuel) | 90 | 50 | 40 | 30 | 40 | 70 | 20 | 40 | F | 1
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1
Financial data
| Nominal investment (M€/MWe) | 6.2167 | 6.0628 | 5.7493 | 5.539 | 5.2842 | 7.1492 | 4.3768 | 7.5546 | E,J,K | 1
| - of which equipment | 4.0558 | 3.9554 | 3.7508 | 3.704 | 3.4474 | 4.6642 | 2.8554 | 5.019 | K
| - of which installation | 2.1609 | 2.1074 | 1.9984 | 1.835 | 1.8368 | 2.4851 | 1.5214 | 2.5356 | K
| Fixed O&M (€/MWe/year) | 275000 | 271000 | 261000 | 253000 | 232000 | 314000 | 192000 | 325000
| Variable O&M (€/MWh_e) | 3.8885 | 3.8885 | 3.8769 | 3.9352 | 2.993 | 4.4295 | 2.6726 | 4.839 | L
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.056599 | 0.056599 | 0.056599 | 0.056599 | 0 | 0.058575 | 0 | 0.058575 | C,L
| Nominal investment (M€/MW fuel input) | 0.958 | 0.93429 | 0.88861 | 0.84343 | 0.8143 | 1.1017 | 0.66646 | 1.1503 | E,J,K | 1
| - of which equipment | 0.625 | 0.60953 | 0.57973 | 0.56402 | 0.53125 | 0.71875 | 0.4348 | 0.76425 | K
| - of which installation | 0.333 | 0.32476 | 0.30888 | 0.27942 | 0.28305 | 0.38295 | 0.23166 | 0.3861 | K
| Fixed O&M (€/MW input/year) | 42500 | 41700 | 40300 | 38500 | 35700 | 48400 | 29200 | 49500
| Variable O&M (€/MWh input) | 0.6 | 0.6 | 0.6 | 0.6 | 0.46 | 0.68 | 0.41 | 0.74 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.004 | 0.003901 | 0.0037103 | 0.0033564 | 0.0034 | 0.0046 | 0.0027827 | 0.0046378 | K
| Heat efficiency, net (%), name plate | 83.4333 | 83.4333 | 83.3855 | 83.624 | 72 | 85 | 71 | 85 | B, H | 1
| Heat efficiency, net (%), annual average | 84.2038 | 84.2038 | 84.1583 | 84.3853 | 74 | 86 | 72 | 86 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.729 | 1.729 | 1.7288 | 1.7298 | 1 | 11 | 1 | 13 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
E | Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the thermail input.
F | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G | Warm start is starting with a glowing fuel layer on the grate.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09c Straw, Large, 40 degree
| Technology | Large Straw CHP, 132 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 41.595 | 41.595 | 41.7232 | 41.7232 | 39.481 | 54.6206 | 40.6204 | 55.8372 | A
| Electricity efficiency, net (%), name plate | 31.5113 | 31.5113 | 31.6085 | 31.6085 | 29 | 42 | 30 | 43 | A, H | 1
| Electricity efficiency, net (%), annual average | 29.9358 | 29.9358 | 30.028 | 30.028 | 26 | 40 | 27 | 41 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.8381 | 2.8381 | 2.8399 | 2.8399 | 2.0912 | 3.1371 | 1.7287 | 3.2976 |  | 1
| Cb coefficient (40°C/80°C) | 0.45437 | 0.45437 | 0.45643 | 0.45643 | 0.43128 | 0.59666 | 0.44437 | 0.61083
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.24041 | 0.24041 | 0.23967 | 0.23967 | 0.20435 | 0.27648 | 0.17976 | 0.29959
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 95.45 | 96.36 | 99.09 | 99.818 | 90.9 | 99.818 | 95.45 | 99.909 | F | 1,2
| NOX (g per GJ fuel) | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1,2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2
Financial data
| Nominal investment (M€/MWe) | 3.4649 | 3.3813 | 3.2103 | 2.9122 | 2.8569 | 3.9717 | 2.3466 | 3.9914 | J,K | 1
| - of which equipment | 2.139 | 2.0882 | 1.9842 | 1.8031 | 1.7299 | 2.447 | 1.4271 | 2.4588 | J,K
| - of which installation | 1.3259 | 1.2931 | 1.2261 | 1.1091 | 1.127 | 1.5248 | 0.91955 | 1.5326 | J,K
| Fixed O&M (€/MWe/year) | 126000 | 122000 | 115000 | 103000 | 103000 | 142000 | 79000 | 133000 | J
| Variable O&M (€/MWh_e) | 2.1064 | 2.1064 | 2.0998 | 2.0998 | 1.6178 | 2.3975 | 1.4231 | 2.5798 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.088886 | 0.088886 | 0.088886 | 0.088886 | 0 | 0.090904 | 0 | 0.090904 | C, L
| Nominal investment (M€/MW fuel input) | 1.0918 | 1.0655 | 1.0147 | 0.92052 | 0.90026 | 1.2515 | 0.74174 | 1.2616 | J,K | 1
| - of which equipment | 0.67403 | 0.65802 | 0.62718 | 0.56994 | 0.54513 | 0.77107 | 0.45108 | 0.77719 | K
| - of which installation | 0.4178 | 0.40746 | 0.38754 | 0.35057 | 0.35513 | 0.48047 | 0.29066 | 0.48443 | K
| Fixed O&M (€/MW input/year) | 39700 | 38500 | 36300 | 32400 | 32500 | 44600 | 24900 | 41900 | J
| Variable O&M (€/MWh input) * | 0.66 | 0.66 | 0.66 | 0.66 | 0.51 | 0.76 | 0.45 | 0.82 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.065 | 0.063391 | 0.060292 | 0.054541 | 0.05525 | 0.07475 | 0.045219 | 0.075365 | K
| Heat efficiency, net (%), name plate | 69.3511 | 69.3511 | 69.251 | 69.251 | 45 | 72 | 44 | 71 | B, H | 1
| Heat efficiency, net (%), annual average | 70.9267 | 70.9267 | 70.8314 | 70.8314 | 48 | 74 | 47 | 73 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.7679 | 1.7679 | 1.7677 | 1.7677 | 1 | 15 | 1 | 15 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G | Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09c Straw, Large, 50 degree
| Technology | Large Straw CHP, 132 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 38.9906 | 38.9906 | 39.1138 | 39.1138 | 36.8812 | 52.0111 | 38.0699 | 53.2806 | A
| Electricity efficiency, net (%), name plate | 29.5384 | 29.5384 | 29.6317 | 29.6317 | 27 | 40 | 28 | 41 | A, H | 1
| Electricity efficiency, net (%), annual average | 28.0614 | 28.0614 | 28.1501 | 28.1501 | 25 | 38 | 25 | 39 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.8554 | 2.8554 | 2.8572 | 2.8572 | 2.1147 | 3.1556 | 1.7474 | 3.316 |  | 1
| Cb coefficient (50°C/100°C) | 0.42889 | 0.42889 | 0.43085 | 0.43085 | 0.40569 | 0.57212 | 0.41935 | 0.5869
| Cv coefficient (50°C/100°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.25647 | 0.25647 | 0.25566 | 0.25566 | 0.218 | 0.29494 | 0.19175 | 0.31958
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 95.45 | 96.36 | 99.09 | 99.818 | 90.9 | 99.818 | 95.45 | 99.909 | F | 1,2
| NOX (g per GJ fuel) | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1,2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2
Financial data
| Nominal investment (M€/MWe) | 3.6963 | 3.6071 | 3.4244 | 3.1065 | 3.0478 | 4.237 | 2.5032 | 4.2577 | J,K | 1
| - of which equipment | 2.2819 | 2.2277 | 2.1166 | 1.9234 | 1.8455 | 2.6104 | 1.5223 | 2.6228 | J,K
| - of which installation | 1.4144 | 1.3794 | 1.3079 | 1.1831 | 1.2023 | 1.6266 | 0.9809 | 1.6348 | J,K
| Fixed O&M (€/MWe/year) | 134000 | 130000 | 123000 | 109000 | 110000 | 151000 | 84000 | 142000 | J
| Variable O&M (€/MWh_e) | 2.1422 | 2.1422 | 2.1352 | 2.1352 | 1.7259 | 2.4568 | 1.518 | 2.6514 | L
Technology specific data
| Steam reheat | None | None | None | None | None | Yes | None | Yes
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.057896 | 0.057896 | 0.057896 | 0.057896 | 0 | 0.061106 | 0 | 0.061106 | C, L
| Nominal investment (M€/MW fuel input) | 1.0918 | 1.0655 | 1.0147 | 0.92052 | 0.90026 | 1.2515 | 0.74174 | 1.2616 | J,K | 1
| - of which equipment | 0.67403 | 0.65802 | 0.62718 | 0.56994 | 0.54513 | 0.77107 | 0.45108 | 0.77719 | K
| - of which installation | 0.4178 | 0.40746 | 0.38754 | 0.35057 | 0.35513 | 0.48047 | 0.29066 | 0.48443 | K
| Fixed O&M (€/MW input/year) | 39700 | 38500 | 36300 | 32400 | 32500 | 44600 | 24900 | 41900 | J
| Variable O&M (€/MWh input) * | 0.63 | 0.63 | 0.63 | 0.63 | 0.51 | 0.73 | 0.45 | 0.79 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.065 | 0.063391 | 0.060292 | 0.054541 | 0.05525 | 0.07475 | 0.045219 | 0.075365 | K
| Heat efficiency, net (%), name plate | 68.8712 | 68.8712 | 68.775 | 68.775 | 47 | 71 | 46 | 70 | B, H | 1
| Heat efficiency, net (%), annual average | 70.3482 | 70.3482 | 70.2566 | 70.2566 | 49 | 73 | 49 | 72 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 4.2201 | 4.2201 | 4.2197 | 4.2197 | 4 | 15 | 4 | 15 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used.
The system is optimised at DH return temperature 50°C and flow 100°C.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G | Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09c Straw, Medium
| Technology | Medium Straw CHP, 80 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25.2858 | 25.2858 | 25.3645 | 24.9912 | 23.6731 | 25.718 | 24.3259 | 25.8365 | A
| Electricity efficiency, net (%), name plate | 31.6072 | 31.6072 | 31.7056 | 31.239 | 29 | 33 | 30 | 33 | A, H | 1
| Electricity efficiency, net (%), annual average | 30.0269 | 30.0269 | 30.1203 | 29.6771 | 26 | 31 | 27 | 31 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.847 | 2.847 | 2.8488 | 2.8396 | 2.091 | 3.1682 | 1.7285 | 3.2112 |  | 1
| Cb coefficient (40°C/80°C) | 0.46058 | 0.46058 | 0.46271 | 0.45267 | 0.4312 | 0.46845 | 0.44062 | 0.46798
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 0.27684 | 0.27684 | 0.27598 | 0.2801 | 0.23531 | 0.31836 | 0.21007 | 0.35012
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 95.45 | 96.36 | 99.09 | 99.818 | 90.9 | 99.818 | 95.45 | 99.909 | F | 1,2
| NOX (g per GJ fuel) | 90 | 70 | 50 | 30 | 20 | 90 | 10 | 50 | F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1,2
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1,2
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1,2
Financial data
| Nominal investment (M€/MWe) | 3.6625 | 3.5719 | 3.3867 | 3.2054 | 2.9989 | 4.3068 | 2.5794 | 4.3926 | J,K | 1
| - of which equipment | 2.2167 | 2.1618 | 2.0497 | 1.9779 | 1.7699 | 2.6441 | 1.5616 | 2.6965 | J,K | 1
| - of which installation | 1.4459 | 1.4101 | 1.337 | 1.2275 | 1.229 | 1.6628 | 1.0177 | 1.6962 | J,K | 1
| Fixed O&M (€/MWe/year) | 147000 | 143000 | 134000 | 124000 | 120000 | 168000 | 95000 | 160000 | J | 1
| Variable O&M (€/MWh_e) | 2.099 | 2.099 | 2.0923 | 2.1247 | 1.6129 | 2.3893 | 1.4399 | 2.6104 | L | 1
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.088886 | 0.088886 | 0.088886 | 0.088886 | 0 | 0.090904 | 0 | 0.090904 | C, L
| Nominal investment (M€/MW fuel input) | 1.1576 | 1.129 | 1.0738 | 1.0013 | 0.94786 | 1.3613 | 0.80577 | 1.3722 | J,K | 1
| Variable O&M, including electricity (€/MWh input) | 0.70063 | 0.68328 | 0.64988 | 0.61789 | 0.55941 | 0.83572 | 0.48784 | 0.84235 | K
| - of which installation | 0.457 | 0.44569 | 0.4239 | 0.38346 | 0.38845 | 0.52555 | 0.31792 | 0.52987 | K
| Fixed O&M (€/MW input/year) | 46600 | 45200 | 42600 | 38700 | 38000 | 53000 | 29600 | 49900 | J
| Variable O&M (€/MWh input) * | 0.66 | 0.66 | 0.66 | 0.66 | 0.51 | 0.76 | 0.45 | 0.82 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.07 | 0.068267 | 0.06493 | 0.058736 | 0.0595 | 0.0805 | 0.048697 | 0.081162 | K
| Heat efficiency, net (%), name plate | 68.6251 | 68.6251 | 68.5222 | 69.0107 | 53 | 72 | 53 | 71 | B, H | 1
| Heat efficiency, net (%), annual average | 70.2054 | 70.2054 | 70.1074 | 70.5726 | 56 | 74 | 56 | 73 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.7669 | 1.7669 | 1.7667 | 1.7677 | 1 | 15 | 1 | 15 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C | Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G | Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09c Straw, Small
| Technology | Small Straw CHP, 20 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3.0497 | 3.0497 | 3.0594 | 3.0113 | 2.9692 | 3.0866 | 2.9184 | 3.0437 | A
| Electricity efficiency, net (%), name plate | 15.2485 | 15.2485 | 15.2968 | 15.0567 | 14 | 16 | 14 | 16 | A, H | 1
| Electricity efficiency, net (%), annual average | 14.4861 | 14.4861 | 14.5319 | 14.3039 | 13 | 15 | 13 | 15 | A, H | 1
| Auxiliary electricity consumption (% of thermal input) | 2.3732 | 2.3732 | 2.3741 | 2.3698 | 1.8068 | 2.5941 | 1.4428 | 2.5902 |  | 1
| Cb coefficient (40°C/80°C) | 0.17819 | 0.17819 | 0.17885 | 0.17553 | 0.17348 | 0.18034 | 0.17012 | 0.17742
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
| Forced outage (%) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.9837 | 0.9837 | 0.9806 | 0.99623 | 0.83615 | 1.1313 | 0.74718 | 1.2453
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | D | 1
| Minimum load (% of full load) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | D | 1
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 95.45 | 96.36 | 99.09 | 99.818 | 90.9 | 99.818 | 95.45 | 99.909 | F | 1
| NOX (g per GJ fuel) | 90 | 70 | 50 | 40 | 50 | 90 | 40 | 50 | F | 1
| CH4 (g per GJ fuel) | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | F | 1
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1
Financial data
| Nominal investment (M€/MWe) | 6.8531 | 6.6835 | 6.3367 | 6.0865 | 5.8251 | 7.8811 | 5.0912 | 8.3101 | E,J,K | 1
| - of which equipment | 3.8692 | 3.7735 | 3.5777 | 3.5509 | 3.2888 | 4.4496 | 2.9889 | 4.8063 | K
| - of which installation | 2.9839 | 2.91 | 2.759 | 2.5356 | 2.5363 | 3.4315 | 2.1023 | 3.5038 | K
| Fixed O&M (€/MWe/year) | 318000 | 313000 | 302000 | 293000 | 268000 | 362000 | 227000 | 375000 | J
| Variable O&M (€/MWh_e) | 4.5161 | 4.5161 | 4.5019 | 4.5737 | 3.3432 | 5.1194 | 2.9875 | 5.5829 | L
Technology specific data
| Steam reheat | None | None | None | None | None | None | None | None
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | C
| Output of recovered condensate (tonne/MWh_input) | 0.088886 | 0.088886 | 0.088886 | 0.088886 | 0 | 0.090904 | 0 | 0.090904 | C, L
| Nominal investment (M€/MW fuel input) | 1.045 | 1.0191 | 0.96931 | 0.91643 | 0.88825 | 1.2017 | 0.76657 | 1.2512 | E,J,K | 1
| Variable O&M, including electricity (€/MWh input) | 0.59 | 0.5754 | 0.54727 | 0.53465 | 0.5015 | 0.6785 | 0.45003 | 0.72367 | K
| - of which installation | 0.455 | 0.44374 | 0.42204 | 0.38179 | 0.38675 | 0.52325 | 0.31653 | 0.52755 | K
| Fixed O&M (€/MW input/year) | 48600 | 47700 | 46100 | 44100 | 40800 | 55300 | 34200 | 56500 | J
| Variable O&M (€/MWh input) * | 0.69 | 0.69 | 0.69 | 0.69 | 0.51 | 0.78 | 0.45 | 0.84 | L
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.08 | 0.07802 | 0.074206 | 0.067127 | 0.068 | 0.092 | 0.055654 | 0.092757 | K
| Heat efficiency, net (%), name plate | 85.5765 | 85.5765 | 85.5262 | 85.7764 | 72 | 87 | 71 | 87 | B, H | 1
| Heat efficiency, net (%), annual average | 86.3389 | 86.3389 | 86.2911 | 86.5292 | 73 | 88 | 72 | 88 | B, H | 1
| Additional heat potential with heat pumps (% of thermal input) | 1.7669 | 1.7669 | 1.7667 | 1.7677 | 1 | 14 | 1 | 15 | C | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. NOTICE: There are to our knowledge no references on ORC plants running on straw.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D | Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E | Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
G | Warm start is starting with a glowing fuel layer on the grate.
H | The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09a Wood Chips HOP, small
| Technology | Wood Chips, DH-Small, 6 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 6.8407 | 6.8407 | 6.8407 | 6.8407 | 5.3402 | 6.8643 | 5.3402 | 6.8703 | A | 1
| Total efficiency, net (%), name plate | 114.0119 | 114.0119 | 114.0119 | 114.0119 | 89 | 115 | 89 | 115 | B,C | 1
| Total efficiency, net (%), annual average | 114.0119 | 114.0119 | 114.0119 | 114.0119 | 89 | 115 | 89 | 115 | B,C | 1
| Auxiliary electricity consumption (% of heat gen) | 2.2162 | 2.2162 | 2.2162 | 2.2162 | 2.1135 | 2.4723 | 1.691 | 2.4702 | C,K
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement (1000 m2/MWth heat output) | 0.21928 | 0.21928 | 0.21928 | 0.21928 | 0.18638 | 0.25217 | 0.16446 | 0.27409
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | E | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | E | 1
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 89.85 | 98.985 | 97.97 | 98.985 | G | 1
| NOX (g per GJ fuel) | 90 | 60 | 50 | 40 | 40 | 80 | 30 | 40 | I | 2
| CH4 (g per GJ fuel) | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O (g per GJ fuel) | 4 | 3 | 3 | 1 | 1 | 4 | 1 | 4 | I | 2
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (M€/MWth - heat output) | 0.70753 | 0.69002 | 0.65628 | 0.59368 | 0.6014 | 0.81366 | 0.49221 | 0.82035 | F, L
| - of which equipment | 0.40931 | 0.39918 | 0.37967 | 0.34345 | 0.34792 | 0.47071 | 0.28475 | 0.47458 | F, L
| - of which installation | 0.29821 | 0.29083 | 0.27661 | 0.25023 | 0.25348 | 0.34295 | 0.20746 | 0.34577 | F, L
| Fixed O&M (€/MWth/year), heat output | 33000 | 32500 | 31500 | 29600 | 27800 | 37700 | 22800 | 38000
| Variable O&M (€/MWh) heat output | 2.5874 | 2.7204 | 3.4296 | 3.7842 | 2.3388 | 3.7093 | 3.2914 | 5.221 | M
| - of which is electricity costs (€/MWh-heat) | 1.3962 | 1.5292 | 2.2384 | 2.593 | 1.5127 | 1.9935 | 2.563 | 3.3802 | M
| - of which is other O&M costs (€/MWh-heat) | 1.1912 | 1.1912 | 1.1912 | 1.1912 | 0.82614 | 1.7159 | 0.72831 | 1.8408 | M
Technology specific data
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D, J
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D, J
| Output of recovered condensate (tonne/MWh_input) | 0.2462 | 0.2462 | 0.2462 | 0.2462 | 0 | 0.24842 | 0 | 0.24842 | D
| Nominal investment (M€/MW fuel input) | 0.80667 | 0.7867 | 0.74824 | 0.67686 | 0.68567 | 0.92767 | 0.56118 | 0.9353 | J, L | 1
| - of which equipment | 0.46667 | 0.45512 | 0.43287 | 0.39157 | 0.39667 | 0.53667 | 0.32465 | 0.54108 | L
| - of which installation | 0.34 | 0.33158 | 0.31537 | 0.28529 | 0.289 | 0.391 | 0.23653 | 0.39422 | L
| Fixed O&M (€/MW input/year) | 37700 | 37100 | 35900 | 33700 | 31700 | 42900 | 26000 | 43300
| Variable O&M, including electricity (€/MWh input) | 2.95 | 3.1 | 3.91 | 4.31 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.02 | 0.019505 | 0.018551 | 0.016782 | 0.017 | 0.023 | 0.013914 | 0.023189 | L
| Additional heat potential with heat pumps (% of thermal input) | 1.9432 | 1.9432 | 1.9432 | 1.9432 | 1 | 26 | 1 | 26 | D | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E | Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F | Reference to heat output because of the lack of electricity production
G | Assuming content of sulphur in fuel of 20 g/GJ
H | Warm start is starting with a glowing fuel layer on the grate.
I | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
J | The nominal investment is in the range 0.6 to 1.1 M€/MWth
K | Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 09a Wood Chips HOP, medium
| Technology | Wood Chips, DH-Medium, 45 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 51.6377 | 51.6377 | 51.6377 | 51.637 | 40.3835 | 51.8149 | 39.6586 | 51.8599 | A | 1
| Total efficiency, net (%), name plate | 114.7504 | 114.7504 | 114.7504 | 114.7488 | 89 | 116 | 88 | 116 | B,C | 1
| Total efficiency , net (%), annual average | 114.7504 | 114.7504 | 114.7504 | 114.7488 | 89 | 116 | 88 | 116 | B,C | 1
| Auxiliary electricity consumption (% of heat gen) | 2.2039 | 2.2039 | 2.2039 | 2.2026 | 2.098 | 2.4587 | 1.7093 | 2.4549 | C,K
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement (1000 m2/MWth heat output) | 0.058097 | 0.058097 | 0.058097 | 0.058098 | 0.049383 | 0.066812 | 0.043573 | 0.072622
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | E | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 1
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 94.925 | 98.985 | 97.97 | 98.985 | G | 1
| NOX (g per GJ fuel) | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | I | 2
| CH4 (g per GJ fuel) | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O (g per GJ fuel) | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | I | 2
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (M€/MWth - heat output) | 0.50603 | 0.4935 | 0.46937 | 0.45394 | 0.43012 | 0.58193 | 0.35204 | 0.61606 | F, L
| - of which equipment | 0.36988 | 0.36073 | 0.34309 | 0.3397 | 0.3144 | 0.42537 | 0.25732 | 0.45821 | F, L
| - of which installation | 0.13614 | 0.13277 | 0.12628 | 0.11424 | 0.11572 | 0.15656 | 0.094711 | 0.15785 | F, L
| Fixed O&M (€/MWth/year), heat output | 42800 | 42000 | 40500 | 38200 | 35800 | 48500 | 28800 | 48500
| Variable O&M (€/MWh) heat output | 2.572 | 2.7043 | 3.4095 | 3.7606 | 2.3252 | 3.6806 | 3.2726 | 5.2735 | M
| - of which is electricity costs (€/MWh-heat) | 1.3885 | 1.5207 | 2.226 | 2.577 | 1.5043 | 1.9788 | 2.5489 | 3.4145 | M
| - of which is other O&M costs (€/MWh-heat) | 1.1836 | 1.1836 | 1.1836 | 1.1836 | 0.82084 | 1.7017 | 0.72364 | 1.859 | M
Technology specific data
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D
| Output of recovered condensate (tonne/MWh_input) | 0.2462 | 0.2462 | 0.2462 | 0.2462 | 0 | 0.24842 | 0 | 0.24842 | D
| Nominal investment (M€/MW fuel input) | 0.58067 | 0.56629 | 0.53861 | 0.52089 | 0.49357 | 0.66777 | 0.40396 | 0.70692 | L | 1
| - of which equipment | 0.42444 | 0.41394 | 0.3937 | 0.38981 | 0.36078 | 0.48811 | 0.29528 | 0.52579 | L
| - of which installation | 0.15622 | 0.15236 | 0.14491 | 0.13108 | 0.13279 | 0.17966 | 0.10868 | 0.18113 | L
| Fixed O&M (€/MW input/year) | 49100 | 48200 | 46400 | 43900 | 41100 | 55600 | 33000 | 55700
| Variable O&M, including electricity (€/MWh input) | 2.95 | 3.1 | 3.91 | 4.32 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.017 | 0.016579 | 0.015769 | 0.014265 | 0.01445 | 0.01955 | 0.011827 | 0.019711 | L
| Additional heat potential with heat pumps (% of thermal input) | 1.9432 | 1.9432 | 1.9432 | 1.9442 | 1 | 26 | 1 | 28 | D | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplierand operator information, or pre-project studies.
2 | Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate as the basis assumption. Fluid-bed combustion technology may be an alternative.It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 30-49,9 MW fired capacity (heat input).
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E | Load control of the heat production is important and units of this size can make rapid load variations.
F | Reference to heat output because of the lack of electricity production
G | assuming content of sulphur in fuel of 20 g/GJ
H | Warm start is starting with a glowing fuel layer on the grate.
I | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
J
K | Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 09a Wood Chips HOP, large
| Technology | Wood Chips, DH-Large, 90 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 103.4256 | 103.4256 | 103.4256 | 103.4242 | 80.9174 | 103.7801 | 79.4676 | 103.8701 | A | 1
| Total efficiency, net (%), name plate | 114.9174 | 114.9174 | 114.9174 | 114.9158 | 89 | 116 | 88 | 116 | B,C | 1
| Total efficiency , net (%), annual average | 114.9174 | 114.9174 | 114.9174 | 114.9158 | 89 | 116 | 88 | 116 | B,C | 1
| Auxiliary electricity consumption (% of heat gen) | 2.2012 | 2.2012 | 2.2012 | 2.1998 | 2.0946 | 2.4556 | 1.7064 | 2.4519 | C,K
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement (1000 m2/MWth heat output) | 0.048344 | 0.048344 | 0.048344 | 0.048345 | 0.041092 | 0.055595 | 0.036258 | 0.060431
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | E | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 1
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.97 | 97.97 | 97.97 | 97.97 | 94.925 | 98.985 | 97.97 | 98.985 | G | 1
| NOX (g per GJ fuel) | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 |  | 2,3
| CH4 (g per GJ fuel) | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 |  | 3
| N2O (g per GJ fuel) | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | 3
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 3
Financial data
| Nominal investment (M€/MWth - heat output) | 0.45057 | 0.43941 | 0.41793 | 0.40357 | 0.38298 | 0.51815 | 0.31345 | 0.54792 | F, L
| - of which equipment | 0.33937 | 0.33097 | 0.31479 | 0.31027 | 0.28847 | 0.39028 | 0.2361 | 0.41899 | F, L
| - of which installation | 0.11119 | 0.10844 | 0.10314 | 0.0933 | 0.094512 | 0.12787 | 0.077354 | 0.12892 | F, L
| Fixed O&M (€/MWth/year), heat output | 35200 | 34600 | 33300 | 31400 | 29500 | 39900 | 23600 | 39900
| Variable O&M (€/MWh) heat output | 2.5686 | 2.7007 | 3.405 | 3.7556 | 2.3221 | 3.6741 | 3.2684 | 5.2642 | M
| - of which is electricity costs (€/MWh-heat) | 1.3867 | 1.5188 | 2.2232 | 2.5738 | 1.5025 | 1.9755 | 2.5458 | 3.4087 | M
| - of which is other O&M costs (€/MWh-heat) | 1.1818 | 1.1818 | 1.1818 | 1.1819 | 0.81965 | 1.6986 | 0.7226 | 1.8555 | M
Technology specific data
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D
| Output of recovered condensate (tonne/MWh_input) | 0.2462 | 0.2462 | 0.2462 | 0.2462 | 0 | 0.24842 | 0 | 0.24842 | D
| Nominal investment (M€/MW fuel input) | 0.51778 | 0.50496 | 0.48027 | 0.46376 | 0.44011 | 0.59544 | 0.36021 | 0.62964 | L | 1
| - of which equipment | 0.39 | 0.38035 | 0.36175 | 0.35655 | 0.3315 | 0.4485 | 0.27131 | 0.48149 | L
| - of which installation | 0.12778 | 0.12462 | 0.11852 | 0.10722 | 0.10861 | 0.14694 | 0.088892 | 0.14815 | L
| Fixed O&M (€/MW input/year) | 40500 | 39700 | 38200 | 36100 | 33900 | 45900 | 27200 | 45800
| Variable O&M, including electricity (€/MWh input) | 2.95 | 3.1 | 3.91 | 4.32 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.015 | 0.014629 | 0.013914 | 0.012586 | 0.01275 | 0.01725 | 0.010435 | 0.017392 | L
| Additional heat potential with heat pumps (% of thermal input) | 1.9432 | 1.9432 | 1.9432 | 1.9442 | 1 | 26 | 1 | 28 | D | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3 | Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate. Fluid-bed combustion technology may be an alternative. It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 80-99,9 MW fired capacity (heat input).
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E | Load control of the heat production is important and units of this size can make rapid load variations.
F | Reference to heat output because of the lack of electricity production
G | Assuming content of sulphur in fuel of 20 g/GJ
H | Warm start is starting with a glowing fuel layer on the grate.
I
J
K | Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 09b Wood Pellets HOP
| Technology | Wood Pellets, DH only, 6 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 6.0703 | 6.0703 | 6.0703 | 6.0703 | 5.4461 | 6.0926 | 5.3681 | 6.0986 | A | 1
| Total efficiency, net (%), name plate | 101.1711 | 101.1711 | 101.1711 | 101.1711 | 90 | 102 | 89 | 102 | B,C | 1
| Total efficiency , net (%), annual average | 101.1711 | 101.1711 | 101.1711 | 101.1711 | 90 | 102 | 89 | 102 | B,C | 1
| Auxiliary electricity consumption (% of heat gen) | 2.0554 | 2.0554 | 2.0554 | 2.0554 | 1.7045 | 2.2952 | 1.3836 | 2.2915 | C,K
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement (1000 m2/MWth heat output) | 0.16474 | 0.16474 | 0.16474 | 0.16474 | 0.14003 | 0.18945 | 0.12355 | 0.20592
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | E | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | E | 1
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 98.25 | 98.25 | 98.25 | 98.25 | 91.25 | 99.125 | 98.25 | 99.125 | G | 1
| NOX (g per GJ fuel) | 90 | 50 | 40 | 40 | 40 | 70 | 20 | 40 | G | 1
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G | 1
| N2O (g per GJ fuel) | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | G | 1
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | G | 1
Financial data
| Nominal investment (M€/MWth - heat output) | 0.73275 | 0.71462 | 0.67968 | 0.61484 | 0.62284 | 0.84266 | 0.50976 | 0.89938 | F, L
| - of which equipment | 0.44479 | 0.43378 | 0.41257 | 0.37322 | 0.37807 | 0.51151 | 0.30943 | 0.5655 | F, L
| - of which installation | 0.28796 | 0.28083 | 0.2671 | 0.24162 | 0.24477 | 0.33116 | 0.20033 | 0.33388 | F, L
| Fixed O&M (€/MWth/year), heat output | 33600 | 32700 | 31000 | 27900 | 28000 | 37900 | 21700 | 37100 | F
| Variable O&M (€/MWh) heat output | 1.8384 | 1.9617 | 2.6195 | 2.9483 | 1.8147 | 2.3001 | 2.7389 | 3.5237 | F, M
| - of which is electricity costs (€/MWh-heat) | 1.2949 | 1.4182 | 2.0759 | 2.4048 | 1.4017 | 1.6106 | 2.3749 | 2.769 | F, M
| - of which is other O&M costs (€/MWh-heat) | 0.54352 | 0.54352 | 0.54352 | 0.54352 | 0.41292 | 0.68951 | 0.36398 | 0.75467 | F, M
Technology specific data
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D,J
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D,J
| Output of recovered condensate (tonne/MWh_input) | 0.056599 | 0.056599 | 0.056599 | 0.056599 | 0 | 0.058575 | 0 | 0.058575 | D
| Nominal investment (M€/MW fuel input) | 0.74133 | 0.72298 | 0.68764 | 0.62204 | 0.63013 | 0.85253 | 0.51573 | 0.90991 | J, L | 1
| - of which equipment | 0.45 | 0.43886 | 0.41741 | 0.37759 | 0.3825 | 0.5175 | 0.31305 | 0.57212 | L
| - of which installation | 0.29133 | 0.28412 | 0.27023 | 0.24445 | 0.24763 | 0.33503 | 0.20267 | 0.33779 | L
| Fixed O&M (€/MW input/year) | 34000 | 33100 | 31300 | 28300 | 28300 | 38300 | 21900 | 37500
| Variable O&M, including electricity (€/MWh input) | 1.86 | 1.98 | 2.65 | 2.98 | 1.84 | 2.09 | 2.78 | 3.15 | M
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.004 | 0.003901 | 0.0037103 | 0.0033564 | 0.0034 | 0.0046 | 0.0027827 | 0.0046378 | L
| Additional heat potential with heat pumps (% of thermal input) | 1.729 | 1.729 | 1.729 | 1.729 | 1 | 11 | 1 | 13 | D | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate.
The system is optimised at DH return temperature 40°C and flow 80°C.
B | Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D | Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E | Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F | Reference to heat output because of the lack of electricity production
G | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
I | Warm start is starting with a glowing fuel layer on the grate.
J | The nominal investment is in the range 0.6 to 1.1 M€/Mwth
K | Result of model calculation, there are reports of DH plants operating at lower power consumption
L | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 09c Straw HOP
| Technology | Small Straw, DH only, 6 MW feed
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 6.194 | 6.194 | 6.194 | 6.194 | 5.3378 | 6.2166 | 5.3378 | 6.2226 | A | 1
| Total efficiency, net (%), name plate | 103.2334 | 103.2334 | 103.2334 | 103.2334 | 88 | 104 | 88 | 104 | B,C | 1
| Total efficiency , net (%), annual average | 103.2334 | 103.2334 | 103.2334 | 3 | 88 | 104 | 88 | 104 | B,C | 1
| Auxiliary electricity consumption (% of heat gen) | 2.0956 | 2.0956 | 2.0956 | 2.0956 | 1.8096 | 2.338 | 1.4478 | 2.3357 | C,J
| Forced outage (%) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement (1000 m2/MWe) | 0.24217 | 0.24217 | 0.24217 | 0.24217 | 0.20584 | 0.2785 | 0.18163 | 0.30271
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | E | 1
| Minimum load (% of full load) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | E | 1
| Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 95.45 | 96.36 | 99.09 | 99.818 | 90.9 | 99.818 | 95.45 | 99.909 | G | 1
| NOX (g per GJ fuel) | 90 | 70 | 70 | 70 | 40 | 90 | 20 | 70 | G | 1
| CH4 (g per GJ fuel) | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | G | 1
| N2O (g per GJ fuel) | 4 | 3 | 2 | 1 | 1 | 4 | 1 | 4 | G | 1
| Particles (g per GJ fuel) | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | G | 1
Financial data
| Nominal investment (M€/MWth - heat output) | 0.89764 | 0.87542 | 0.83263 | 0.7532 | 0.763 | 1.0811 | 0.62447 | 1.0896 | F,K
| - of which equipment | 0.43591 | 0.42512 | 0.40433 | 0.36576 | 0.37052 | 0.55008 | 0.30325 | 0.5542 | F,K
| - of which installation | 0.46174 | 0.45031 | 0.42829 | 0.38744 | 0.39248 | 0.531 | 0.32122 | 0.53537 | F,K
| Fixed O&M (€/MWth/year), heat output | 52300 | 50800 | 47900 | 42900 | 43400 | 59600 | 32800 | 55700 | F
| Variable O&M (€/MWh) heat output | 1.9873 | 2.113 | 2.7836 | 3.1189 | 1.9215 | 2.5855 | 2.8556 | 3.8411 | F, M
| - of which is electricity costs (€/MWh-heat) | 1.3202 | 1.446 | 2.1166 | 2.4519 | 1.4294 | 1.708 | 2.4219 | 2.8962 | F, M
| - of which is other O&M costs (€/MWh-heat) | 0.66708 | 0.66708 | 0.66708 | 0.66708 | 0.49204 | 0.87748 | 0.43373 | 0.94489 | F, M
Technology specific data
| Flue gas condensation | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D
| Combustion air humidification | Yes | Yes | Yes | Yes | No | Yes | No | Yes | D
| Output of recovered condensate (tonne/MWh_input) | 0.088886 | 0.088886 | 0.088886 | 0.088886 | 0 | 0.090904 | 0 | 0.090904 | D, M
| Nominal investment (M€/MW fuel input) | 0.92667 | 0.90373 | 0.85955 | 0.77756 | 0.78767 | 1.116 | 0.64466 | 1.1248 | I,K | 1
| - of which equipment | 0.45 | 0.43886 | 0.41741 | 0.37759 | 0.3825 | 0.56786 | 0.31305 | 0.57212 | K
| - of which installation | 0.47667 | 0.46487 | 0.44214 | 0.39997 | 0.40517 | 0.54817 | 0.33161 | 0.55268 | K
| Fixed O&M (€/MW input/year) | 54000 | 52400 | 49400 | 44200 | 44800 | 61600 | 33900 | 57500
| Variable O&M, including electricity (€/MWh input) | 2.05 | 2.18 | 2.87 | 3.22 | 1.99 | 2.3 | 2.96 | 3.42 | M
| Fuel storage specific cost in excess of 2 days (M€/MW_input/storage day) | 0.08 | 0.07802 | 0.074206 | 0.067127 | 0.068 | 0.092 | 0.055654 | 0.092757 | K
| Additional heat potential with heat pumps (% of thermal input) | 1.7669 | 1.7669 | 1.7669 | 1.7669 | 1 | 15 | 1 | 15 | D | 1
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2
Notes:
A | The plant is directly producing hot water for District Heating by burning fuel on a grate.
B | Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C | The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D | Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
The system is optimised at DH return temperature 40°C and flow 80°C.
E | Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F | Reference to heat output because of the lack of electricity production
G | Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
Warm start is starting with a glowing fuel layer on the grate.
I | The nominal investment is in the range 0.6 to 1.1 M€/MWth
J | Result of model calculation, there are reports of DH plants operating at lower power consumption
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L
M | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 €/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 09a Wood Chips extract. plant
| Technology | Large Wood Chips CHP, 600 MW feed, Extraction
|  | 2015 | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
(No FGC)
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 258.2 | 257.7 | 258.2 | 259.7 | 248.6 | 238.8 | 258.6 | 242.6 | 261.3 | A
| Electricity efficiency, net (%), name plate | 43 | 43 | 43 | 43.2 | 41.4 | 39.8 | 43.1 | 40.4 | 43.6 | A, H | 1
| Electricity efficiency, net (%), annual average | 40.9 | 40.8 | 40.9 | 41 | 39.4 | 37.8 | 41 | 38.5 | 41.4 | A, H | 1
| Cb coefficient (50°C/100°C) | 0.59 | 0.44 | 0.45 | 0.42 | 0.4 | 0.42 | 0.41 | 0.43 | 0.44
| Cv coefficient (50°C/100°C) | 0.18 | 0.14 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1
| Construction time (years) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 1
| Space requirement (1000 m2/MWe) | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E+G | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring, %) | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | F | 1, 2,3
| NOX (g per GJ fuel) | 30 | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | 1, 2,3
| CH4 (g per GJ fuel) | 3 | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | 1, 2,3
| N2O (g per GJ fuel) | 10 | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | 1, 2,3
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1, 2,3
Financial data
| Nominal investment (M€/MWe) | 2.5 | 2.6 | 2.5 | 2.4 | 2.3 | 2.4 | 3.1 | 2.2 | 3.3 | J, K | 1
| - of which equipment | 1.6 | 1.6 | 1.6 | 1.5 | 1.4 | 1.5 | 1.9 | 1.4 | 2.1 | K
| - of which installation | 0.9 | 1 | 0.9 | 0.9 | 0.8 | 0.8 | 1.1 | 0.8 | 1.2 | K
| Fixed O&M (€/MWe/year) | 69 000 | 70 000 | 69 000 | 64 000 | 62 000 | 66 000 | 80 000 | 57 000 | 79 000
| Variable O&M (€/MWeh) | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.6 | 2.7 | 2.5 | L
Technology specific data
| Steam reheat | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Flue gas condensation | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Combustion air humidification | No | No | No | No | No | No | Yes | No | Yes
| Additional heat potential with heat pumps (%of thermal input) | - | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | C | 1
| Nominal investment (M€/MWth) (fuel input) | 1.09 | 1.1 | 1.08 | 1.02 | 0.94 | 0.94 | 1.32 | 0.88 | 1.44 | J, K | 1
| - of which equipment | 0.69 | 0.69 | 0.67 | 0.63 | 0.59 | 0.59 | 0.84 | 0.55 | 0.92 | K
| - of which installation | 0.4 | 0.42 | 0.41 | 0.4 | 0.36 | 0.35 | 0.48 | 0.33 | 0.52 | K
| Fixed O&M (€/MW input/year) | 30 200 | 30 200 | 29 500 | 27 900 | 25 500 | 26 400 | 34 400 | 23 200 | 34 200
| Variable O&M (€/MWh input) | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | L
| Fuel storage specific cost in excess of 2 days (M€/MW/storage day) | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | K
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3 | Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 – Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. – NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
Notes:
A | The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent
extraction steam turbine with steam re-heat.
B | -
C | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humidification and assuming 50 °C DH return temperature. DH water may be heated in two (or more) stages, first stage being direct condensation (at hardly any drop in electricity output), second stage extraction steam with drop in electricity output, cf. the Cv-value.
D | Secondary regulation normally relates to power production.
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is
particularly low for fluid bed types of plants.
F | It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
G | Warm start is starting with a glowing bed and a warm deaerator.
H | The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | -
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities.
Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply
opportunities and energy supply obligations, amongst other things.
The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 09b Wood Pellets extract. plant
| Technology | Large Wood Pellets CHP, 800 MW feed, Extraction
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
(with FGC)
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 356.4 | 357.6 | 358.7 | 358.4 | 347.3 | 359.4 | 351.7 | 364.4 | A
| Electricity efficiency, net (%), name plate | 44.5 | 44.7 | 44.8 | 44.8 | 43.4 | 44.9 | 44 | 45.5 | A, H | 1
| Electricity efficiency, net (%), annual average | 42.3 | 42.5 | 42.6 | 42.6 | 41.2 | 42.7 | 41.8 | 43.3 | A, H | 1
| Cb coefficient (50°C/100°C) | 0.59 | 0.59 | 0.59 | 0.52 | 0.57 | 0.52 | 0.59 | 0.53
| Cv coefficient (50°C/100°C) | 0.17 | 0.17 | 0.17 | 0.15 | 0.17 | 0.15 | 0.17 | 0.15 | I
| Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1
| Construction time (years) | 5 | 5 | 5 | 5 | 5 | 1 | 1 | 1 |  | 1
| Space requirement (1000 m2/MWe) | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Regulation ability
| Primary regulation (% per 30 seconds) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Secondary regulation (% per minute) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | D | 1
| Minimum load (% of full load) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 1
| Warm start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring, %) | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 |  | 1,2
| NOX (g per GJ fuel) | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | C+F | 1,2
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2
| N2O (g per GJ fuel) | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | 1,2
| Particles (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 1,2
Financial data
| Nominal investment (M€/MWe) | 2.22 | 2.15 | 2.04 | 1.9 | 1.93 | 2.59 | 1.8 | 2.78 | J,K | 1
| - of which equipment | 1.34 | 1.3 | 1.23 | 1.16 | 1.16 | 1.58 | 1.08 | 1.7 | K
| - of which installation | 0.88 | 0.86 | 0.81 | 0.74 | 0.77 | 1 | 0.71 | 1.08 | K
| Fixed O&M (€/MWe/year) | 57 000 | 55 000 | 52 000 | 49 000 | 51 000 | 63 000 | 46 000 | 63 000
| Variable O&M (€/MWeh) | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.1 | 1.2 | 1.1 | L
Technology specific data
| Steam reheat | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Flue gas condensation | No | no | no | Yes | no | Yes | no | Yes | C
| Combustion air humidification | No | no | no | Yes | no | Yes | no | Yes
| Additional heat potential with heat pumps (% of thermal input) | - | - | - | 3.6 | - | 3.6 | - | 3.6 | C | 1
| Nominal investment (M€/MWth) (fuel input) | 0.99 | 0.96 | 0.92 | 0.85 | 0.84 | 1.16 | 0.79 | 1.26 | J,K | 1
| - of which equipment | 0.59 | 0.58 | 0.55 | 0.52 | 0.51 | 0.71 | 0.48 | 0.77 | K
| - of which installation | 0.39 | 0.38 | 0.36 | 0.33 | 0.33 | 0.45 | 0.31 | 0.49 | K
| Fixed O&M (€/MW input/year) | 25 200 | 24 600 | 23 500 | 21 900 | 22 200 | 28 300 | 20 000 | 28 600
| Variable O&M (€/MWh input) | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | L
| Fuel storage specific cost in excess of 2 days (M€/MW/storage day) | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | K
References:
1 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2 | EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
Notes:
A | The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent extraction steam turbine
with steam reheat.
B
C | Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield additional 6% (of thermal input) when operated with combustion air humidification and assuming 50 °C DH return temperature. DH water may be heated in two (or more) stages, first stage being direct condensation (at hardly any drop in electricity output), second stage extraction steam with drop in electricity output, cf. the listed Cv-value. For the 2050 estimate flue gas condensation has been included to super-optimize and show the order of advantage is a reduction of the Cv of 0.02 as resulting average for maximum heat output including condensation.
D | This is given by grid code (Energinet.dk)
E | A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F | This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G | Warm start is starting with the steam system being pressurized.
H | The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I | The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current
power/heat prices is shown.
J | Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total
investment, e.g. additional fuel storage, conditions for foundation and harbour facilities.
Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity,
i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may
not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and
thermal input, respectively, are not to be added up!
K | Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
L | Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.

## 10 Stirling
| Technology | Stirling engine, fired by gasified biomass
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity electric, (kW) | 37 | 40 |  |  |  | 1
| Generating capacity, heat, (kJ/s) | 120 | 120 |  |  |  | 1
| Electrical efficiency (%) | 20 | 22 |  |  | A | 1
| Time for wam-up (hours) | 1 | 1 |  |  |  | 1
| Forces outage (%) | 4 | 3 |  |  |  | 1
| Planned outage (weeks per year) | 3 | 2 |  |  |  | 1
| Technical lifetime (years) | 15 | 15 |  |  |  | 1
| Construction time (years) | 0.4 | 0.3 |  |  | B | 1
Environment
| SO2 (degree of desulphuring, %) | 0 | 0 |  |  |  | 1
| NOx (ppm) | 130 | 100 |  |  |  | 1
| CH4 (ppm) | 0 | 0 |  |  |  | 1
| N20 (ppm) | 0 | 0 |  |  |  | 1
Financial data
| Specific investment costs (M€/MW) | 5 | 3.8 |  |  | C+E | 1
| Fixed O&M (€/MW/year) | 32000 | 32000 |  |  | D+E | 1
| Variable O&M (€/MWh) | 26 | 21 |  |  | D+E | 1
References:
1 | Stirling DK, December 2009
Notes:
A | The efficiency of the gasifier is 97%, while the total efficiency for the whole system is 90% (2020).
B | The plants may be delivered as pre-assembled container solutions reducing construction times on site to a couple of weeks.
C | Complete plant, including gasifier, combustion chambers, engines, control system, piping, and instrumentation.
D | O&M for the Stirling engine itself is (2010) around 16 €/MWh, while the remianing O&M costs are for biomass feeding, gasification, heat exchangers etc.
E | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
This sheet has been moved from a previous datasheet and
does therefore not follow the same guideline as the remainder
of the data sheets in the file.

## 11 SOFC-CHP
| Technology | 11 SOFC - CHP Natural Gas / Biogas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.25 | 2.5 | 10 | 20 |  |  |  |  | A | 3; *; *; *
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | 56 | 58 | 60 | 60
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 56 | 58 | 60 | 60 | 52 | 60 | 56 | 62 | B | 3; *; *; *
| Cb coefficient (50oC/100oC) | - | 1.6667 | 1.6129 | 1.6129 |  |  |  |  | C, L | -; *; *; *
| Cv coefficient (50oC/100oC) | - | - | - | -
Forced outage (%)
Planned outage (weeks per year)
| Technical lifetime (years) | 15 | 20 | 20 | 20 |  |  |  |  | D | 6; 6; *; *
| Construction time (years) | 1 | 1 | 1 | 1
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
| Minimum load (% of full load) | 70 | 70 | 70 | 70
| Warm start-up time (hours) | 0.025 | 0.025 | 0.025 | 0.025 |  |  |  |  | E
| Cold start-up time (hours) | 25 | 25 | 25 | 25 |  |  |  |  | E | *; *; *; *
Environment
| SO2 (degree of desulphuring, %) | 100 | 100 | 100 | 100 | [5 empty] | 3
| NOX (g per GJ fuel) | 1.3 | 1.4 | 1.5 | 1.6 | [5 empty] | 3
| CH4 (g per GJ fuel) | 1.25 | 1.25 | 1.25 | 1.25 |  |  |  |  | F | 7
| N2O (g per GJ fuel) | NA | NA | NA | NA |  |  |  |  | F | *
Financial data (in 2015€)
| Nominal investment (M€/MW) | 8.3 | 3.3 | 2 | 0.8 | 2.7 | 5.8 | 0.4 | 1.3 | G, H, I, J | 8, 13
| - of which equipment | 6.64 | 2.31 | 1.2 | 0.464 |  |  |  |  | G
| - of which installation | 1.66 | 0.99 | 0.8 | 0.336 |  |  |  |  | G
| Fixed O&M (€/MW/year) | 415000 | 165000 | 100000 | 40000 | 135000 | 290000 | 20000 | 65000 | K | 8
| Variable O&M (€/MWh) | -
| Startup cost (€/MW/startup) | -
Technology specific data
Notes:
A | Installed systems consist of modules of app. 200 kWel power, these modules can be clustered into larger units. Today, often up to app. 2 MWel power and upwards. [5,8]
B | The electrical efficiency (based on the lower heating value, LHV) of Bloom Energy’s systems decreases from an initial value of 60 % to 52 % by the end-of life for the stacks. This gives an average electrical efficiency of 56 % for the life-time of a stack. Uncertainties represent the aforementioned interval.
C | No CHP-systems in this power range are available, therefore, Bloom Energy ES-5710 unit has been chosen as the reference system. This system is a power producing system and does not take the produced heat into account. . The produced heat can be used as thermal storage, hot water production, heating or for feed in to the distributed heating system. High total efficiencies can be expected as the systems are compact and with a small surface area, leading to low heat losses and thereby high total system efficiency. Thus it is not unrealistic to assume a total efficiency above 90 % (thermal efficiency > 35 %) for this type of system.
D | Values correspond to the durability for the whole plant; the stack may be exchanged several times during the life time of the plant.
E | Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
F | Value for SOFC microCHP systems used here, since SOFC-CHP’s has the same operating principle.
G | A bloom unit costs approximately 6600 euro per kWel. To this must the installation costs be added, which of course depends on the location and the size of the unit. Additional costs are also to cover for necessary modifications of the system, e.g. implementation of hot water storage and subsystems for exporting the heat from the unit to surrounding buildings or distributed heating grid.
H | Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
I | The best estimates for nominal investments in 2020, 2030 and 2050 are estimated from [9]. In 2020 an annual production of 50 units is assumed, in 2030 a yearly production of 250 units is assumed, and in 2050 a production of 4000 units per year is assumed.
J | Estimation of uncertainties for investment costs are estimated from [9] with an annual production of 10/150 units in 2020 and 1000/10000 units in 2050
K | Fixed O&M costs are estimated as 5% of the investment cost.
L | The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
References:
[1] | BloomEnergy, www.bloomenergy.com, 2014-11-11
[2] | https://www.mhps.com/en/technology/index.html, 2014-11-14
[3] | BloomEnergy, Product datasheet: ES-5710 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5710.pdf
[4] | BloomEnergy, Product datasheet: ES-5700 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5700.pdf
[5] | Iskov H., Rasmussen N.B., “Update of technology data for energy plants: Fuel cells, electrolysis and technologies for bio-SNG”, Danish gas Technology centre, 2013.
[6] | Fuel Cell and Hydrogen Joint Undertaking: “Multi – Annual Work Plan 2014-2020”, adopted 2014-06-30
[7] | http://www.asue.de, 2014-11-17
[8] | BloomEnergy Server, http://en.wikipedia.org/wiki/Bloom_Energy_Server, 2015-02-02
[13] | Chick, LA; Gotthold, DW; Weimar, MR; Whyatt, GA, Cost Study for Manufacturing of Solid Oxide Fuel Cell Power Systems, 2013, Pacific Northwest National Laboratory prepared for the U.S. Department of Energy.
* | An asterisk in the reference indicate high uncertainty or "guesstimate", where more certain data where not available

## 12 LT-PEMFC CHP
| Technology | 12 LT-PEMFC CHP hydrogen gas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.05 | 0.1 | 1 | 2 | [5 empty] | 5
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | 45 | 50 | 50 | 50 | [5 empty] | 5
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 45 | 50 | 50 | 50 | 45 | 52 | 46 | 53 | A | 3, 5
| Cb coefficient (50oC/100oC) | - | 1.25 | 1.25 | 1.25 |  |  |  |  | D
| Cv coefficient (50oC/100oC) | - | - | - | -
| Forced outage (%) | 0.1 | 0.1 | 0.1 | 0.1
| Planned outage (weeks per year) |  | 0.1 | 0.1 | 0.1
| Technical lifetime (years) | 10 | 10 | 10 | 10 | [5 empty] | 5
| Construction time (years) | 1 | 1 | 1 | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 50 | 25 | 2.5 | 1.25
Secondary regulation (% per minute)
| Minimum load (% of full load) | 10 | 10 | 10 | 10
| Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01
Cold start-up time (hours)
Environment
| SO2 (degree of desulphuring, %) | 100 | 100 | 100 | 100
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1.9 | 1.3 | 1.1 | 0.8 | 1.1 | 1.6 | 0.5 | 0.9 | B | 3, 4
| - of which equipment | 1.6 | 1 | 0.8 | 0.6 | [5 empty] | 4
| - of which installation | 0.3 | 0.3 | 0.3 | 0.2 | [5 empty] | 4
| Fixed O&M (€/MW/year) | 95000 | 65000 | 55000 | 40000 |  |  |  |  | C
Variable O&M (€/MWh)
Technology specific data
| Minimum load efficiency (%) | 30 | 35 | 35 | 35 | [5 empty] | 5
Notes:
A | Uncertainties for efficiency based on [2]
B | Estimation of uncertainties for nominal investment costs based on [2]
C | Fixed O&M costs are estimated to 5% of the investment cost based on [2]
D | The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
References:
[3] | International Energy Agency, 2015, Technology Roadmap - Hydrogen and Fuel Cells.
[4] | Ea Energy Analyses et al. 2016, Technology Data for Hydrogen Technologies.
[5] | Practical data and expert opinion from Dantherm Power
* | An asterisk in the reference indicate high uncertainty or "guesstimate", where more certain data where not available.

## 20 Onshore turbines
| Technology | 20 Large wind turbines on land
| Year of final investment decision | 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 3.1 | 4.2 | 5 | 5.5 | 6 | 2 | 6 | 1.5 | 8 | A1 | 3
| Average annual full-load hours | 3100 | 3400 | 3600 | 3700 | 3800 | 2000 | 4000 | 2000 | 4500 | A, L | 3
| Forced outage (%) | 3% | 2.5% | 2% | 1.8% | 1.5% | 1% | 5% | 1% | 5% | B | 4
| Planned outage (%) | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.1% | 0.5% | 0.1% | 0.5% | C | 4
| Technical lifetime (years) | 25 | 27 | 30 | 30 | 30 | 25 | 35 | 25 | 40 | D | 14
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 | E | 4
| Space requirement (1000m2/MW) | --- | --- | --- | --- | --- | --- | --- | --- | --- | F
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | G
| Secondary regulation (% per minute) | [9 empty] | G
Financial data (in 2015€)
| Nominal investment (M€/MW) | 1.326 | 1.1188 | 1.0356 | 0.97757 | 0.96307 | 0.77045 | 1.1557 | 0.79557 | 1.1934 |  | 16, 2, 4
| - of which equipment | 0.89 | 0.7146 | 0.64314 | 0.59169 | 0.57883 | 0.57168 | 0.85752 | 0.46306 | 0.69459 |  | 25
| - of which installation/development | 0.115 | 0.0909 | 0.08181 | 0.075265 | 0.073629 | 0.07272 | 0.10908 | 0.058903 | 0.088355 |  | 25
| - of which is related to grid connection | 0.063145 | 0.053275 | 0.050611 | 0.050611 | 0.050611 | 0.04262 | 0.06393 | 0.040489 | 0.060734 |  | 25
| - of which is related to rent of land | 0.085 | 0.085 | 0.085 | 0.085 | 0.085 | 0.068 | 0.102 | 0.068 | 0.102 |  | 25
| - of which is related to decommissioning of existing turbines | 0.0399 | 0.036 | 0.036 | 0.036 | 0.036 | 0.0288 | 0.0432 | 0.0288 | 0.0432 |  | 25
| - of which is related to other costs (i.e. compensation of neighbours, etc.) | 0.133 | 0.139 | 0.139 | 0.139 | 0.139 | 0.1112 | 0.1668 | 0.1112 | 0.1668 | I | 25.26
| Fixed O&M (€/MW/year) | 25600 | 14000 | 12600 | 11592 | 11340 | 11200 | 16800 | 9072 | 13608 | I | 25.26
| Variable O&M (€/MWh) | 2.8 | 1.5 | 1.35 | 1.242 | 1.215 | 1.2 | 1.8 | 0.972 | 1.458
Technology specific data
| Rotor diameter | 106 | 130 | 145 | 155 | 165 | 90 | 130 | 100 | 150 | K | 4, 26
| Hub height | 85 | 85 | 100 | 105 | 110 | 85 | 120 | 85 | 150 |  | 4, 26
| Specific power (W/m2) | 351.2854 | 316.4264 | 302.7918 | 291.4804 | 280.6038 | 314.3801 | 452.0377 | 190.9859 | 452.7074
| Average capacity factor | 35.39% | 38.81% | 41.1% | 42.24% | 43.38% | 22.83% | 45.66% | 22.83% | 51.37% |  | 4, 26
| Average availability (%) | 96.7% | 97.2% | 97.7% | 97.7% | 98.2% | 98.9% | 94.5% | 98.9% | 94.5%
References:
2 | DTU International Energy Report - Wind Energy, DTU, 2014
3 | Master data register of wind turbines at end of December 2014, Danish Energy Agency, 2015
4 | Nielsen, P. et. al., Vindmøllers økonomi EUDP projekt 33033-0196, 2010
14 | Information from Energinet.dk based on analyses of installed projects (2013-14), published under "Købsretsordningen", 2015
15 | Når all-inclusive service alligevel ikke dækker alt, Naturlig Energi, nov. 2014
16 | Schwabe, P., Lensink, S. & Hand, M., IEA Wind Task 26: Multi-national case study of the financial cost of wind energy, 2011
18 | Hvor længe holder en mølle, Naturlig Energi, januar 2012
25 | Analysis of "køberets" projects 2017-18
26 | Interviews with project developers and suppliers dec.18-jan.19
Notes:
A1 | The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present max. 150m tip height.
A | The full load hours (annual produktion (MWh) per installed power (MW)) depending on the actual location of the wind farm, wake losses and technological characteristics of the individual turbine. The value is an average for the expected locations of the wind farms. FLH also depends on wake losses, noise reduction and technological characteristics of the individual turbine. The level for 2020 is based on expectations from the November 18 auction winners locations and the 2019 prefered technology choice. For 2030 and 2050 a slight increase is assumed based on decrease in specific power and increase in hub height.
B | Modern turbines has typically higher forced outage than older smaller turbines had when they were newer due to more complex technology.
C | Planned outage is typically 1-2 service visits a year, with a maximum duration of one work day, but there can also be planned outage due to shadow flicker stop or sector management (protect turbines at given wind speeds and directions, where they are dense spaced).
D | The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
E | The construction time is the periode from FID to commissioning. But from first "dig" to turbines are in operation less than ½ a year is needed for smaller wind farms (clusters), where the similar periode for larger wind farms will be longer. The planning time from idea to construction starts will typically be 2-3 years, but can be essentially more if permitting problems occour.
F | An area of around 50 m x 50 m is needed for a modern wind turbine. Another way of defining the "area use" could be the noise zone, which ranges up to 600-800 m from the wind turbine in worst case.
G | Wind turbines can be downward regulated within very short time and can therefore (if the wind is blowing) be used in both the primary and secondary downward regulation.
H | 2015 Investment costs are based on a number of prospects for projects published in relation to Køberetsordningen. 2020 investment costs are based on updated data from Køberetsordningen. Note that the investment costs listed here includes construction loan interests
I | 75 % of the total yearly O&M costs are assumed to be fixed cost and 25 % are assumed to be variable cost.
K | Currently only turbines up to 150 m total height is installed commercially in Denmark because of strict demands to higher turbines. No change in the national regulation is assumed until after 2020. Some test sites allow for larger turbines. Aboard e.g. in Germany turbines with at total higher of 200 m is installed today.
L | It is expected that the production (FLH) increase 13% from 2015 to 2020 and 3% from 2020-2030 and 1% per decade from 2030-2050

## 20 Domestic turbines
| Technology | 20 Small wind turbines, grid connected (< 25 kW)
| Year of final investment decision | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | < 0,025 |  |  |  | 0.005 | 0.025 | 0.005 | 0.025
| Average annual full-load hours | 1600 | 1600 | 1600 | 1600 | 1000 | 2300 | 1000 | 2300 | A,J
| Forced outage (%) | 3% | 3% | 3% | 3% | 2% | 10% | 2% | 10%
| Planned outage (%) | 0.3% | 0.3% | 0.3% | 0.3% | 0.1% | 0.5% | 0.1% | 0.5% | B
| Technical lifetime (years) | 20 | 20 | 20 | 20 | --- | --- | --- | ---
| Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
| Space requirement (1000m2/MW) | 0.8 | 0.8 | 0.8 | 0.8 | --- | --- | --- | --- | C
Regulation ability
| Primary regulation (% per 30 seconds) | --- | --- | --- | --- | --- | --- | --- | --- | D
| Secondary regulation (% per minute) | --- | --- | --- | --- | --- | --- | --- | --- | D
Financial data (in 2015€)
| Nominal investment (M€/MW) | 4 | 3.8 | 3.61 | 3.4295 | 3 | 6 | 3 | 6 | E/F
| - of which equipment | 90% | 90% | 90% | 90% | 85% | 95% | 85% | 95% | E/F
| - of which installation | 10% | 10% | 10% | 10% | 15% | 5% | 15% | 5% | E/F
| Fixed O&M (€/MW/year) | 100000 | 95000 | 90000 | 85000 | --- | --- | --- | --- | G
| Variable O&M (€/MWh) | --- | --- | --- | --- | --- | --- | --- | ---
Technology specific data
| Rotor diameter | 8 | 8 | 8 | 8 | 4 | 14 | 4 | 14 | H
| Hub height | 18 | 18 | 18 | 18 | 14 | 18 | 14 | 18 | H
| Fixed O&M (€/unit) | 540 | 540 | 540 | 540 | 350 | 700 | 350 | 700 | E/F
Notes:
A | The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
B | The maintenance normally consists of 1 -2 annual service visits.
C | An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
D | Not considered relevant for small domestic turbines.
E | Based on information from manufacturers and resellers. The
F | The prices depends significantly on turbine size (5 kW - 6 M€/MW; 10 kW - 4 M€/MW ; 25 kW - 3 M€/MW)
G | The service cost is assumed fixed to 100€/kW/y.
H | Domestic turbines have a maximum total height of 25 m according to Danish regulations.
J | No development in the capacity factor is expected, because no changing in the size limitation (legislation) is expected. And because location is crucial and one must expect the turbines is put up at the best positions already. But change in legislation i

## 21 Offshore turbines
Technology |  | 21 Large wind turbines offshore
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 8.4 | 15 | 20 | 25 | 30 | 12.75 | 17.25 | 22.5 | 37.5 | A | 1, 2
| Forced outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Technical lifetime [years] | 27 | 30 | 30 | 30 | 30 | 25 | 35 | 25 | 35 | C
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 3 | 1.5 | 2.5 | D
| Space requirement [1000 m2/MW_e] | 165.355 | 177.3605 | 171.9641 | 169.841 | 171.2564 | 150.7565 | 203.9646 | 128.4423 | 214.0705 | E | 3
Regulation ability
Primary regulation [p.u. per 30 seconds]
Secondary regulation [p.u. per minute]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total) [M€/MW_e, 2020] | 2.1159 | 1.8837 | 1.7954 | 1.6764 | 1.6427 | 1.8837 | 1.8837 | 1.6427 | 1.6427 | F | 3
| Nominal investment (equipment) [M€/MW_e, 2020] | 1.196 | 1.169 | 1.1465 | 1.0986 | 1.0967 | 1.169 | 1.169 | 1.0967 | 1.0967 |  | 3
| Nominal investment (installation) [M€/MW_e, 2020] | 0.53911 | 0.40406 | 0.36506 | 0.33266 | 0.31708 | 0.40406 | 0.40406 | 0.31708 | 0.31708 |  | 3
| Nominal investment (other) [M€/MW_e, 2020] | 0.38081 | 0.31068 | 0.28378 | 0.2451 | 0.22896 | 0.31068 | 0.31068 | 0.22896 | 0.22896 | G | 3
| Fixed O&M (*total) [€/MW_e/y, 2020] | 50000 | 42000 | 39000 | 34000 | 33000 | 35700 | 48300 | 24750 | 49500 | H | 3
| Variable O&M (*total) [€/MWh_e, 2020] | 5 | 4.1721 | 3.8947 | 3.4208 | 3.2519 | 3.5463 | 4.7979 | 2.4389 | 4.8779 | H | 3
Technology-specific data
| Nominal investment (equipment: turbines) [M€/MW_e, 2020] | 0.71632 | 0.69499 | 0.67129 | 0.61348 | 0.60676 | 0.59074 | 0.79923 | 0.45507 | 0.91014 |  | 3
| Nominal investment (equipment: foundation) [M€/MW_e, 2020] | 0.20689 | 0.21461 | 0.21768 | 0.22033 | 0.2127 | 0.18242 | 0.24681 | 0.15953 | 0.31905 |  | 3, 4
| Nominal investment (equipment: array cables) [M€/MW_e, 2020] | 0.02614 | 0.019706 | 0.016604 | 0.014302 | 0.012951 | 0.01675 | 0.022662 | 0.0097129 | 0.019426 |  | 3
| Nominal investment (equipment: grid connection) [M€/MW_e, 2020] | 0.24667 | 0.23966 | 0.24096 | 0.25053 | 0.2643 | 0.20371 | 0.2756 | 0.19822 | 0.39645 |  | 3, 5
| Nominal investment (installation: turbines) [M€/MW_e, 2020] | 0.13367 | 0.093184 | 0.08023 | 0.067186 | 0.061191 | 0.079206 | 0.10716 | 0.045893 | 0.091786 |  | 3
| Nominal investment (installation: foundation) [M€/MW_e, 2020] | 0.22983 | 0.1586 | 0.14035 | 0.12539 | 0.11379 | 0.13481 | 0.1824 | 0.085339 | 0.17068 |  | 3
| Nominal investment (installation: array cables) [M€/MW_e, 2020] | 0.05228 | 0.037686 | 0.031218 | 0.026042 | 0.023287 | 0.032033 | 0.043339 | 0.017465 | 0.034931 |  | 3
| Nominal investment (installation: grid connection) [M€/MW_e, 2020] | 0.12333 | 0.11458 | 0.11326 | 0.11404 | 0.11881 | 0.097395 | 0.13177 | 0.089109 | 0.17822 |  | 3
| Nominal investment (Project development etc.) [M€/MW_e, 2020] | 0.38081 | 0.31068 | 0.28378 | 0.2451 | 0.22896 | 0.26408 | 0.35728 | 0.17172 | 0.34344 |  | 3, 6
| Average annual full-load hours [MWh_e/MW_e] | 4400 | 4775 | 4800 | 4850 | 4900 | 4300 | 5250 | 4050 | 5500 | J | 3
| Hub height [m] | 103.5 | 138 | 155 | 170 | 185 | 124.2 | 151.8 | 157.25 | 212.75 |  | 1
| Rotor diameter [m] | 167 | 236 | 270 | 300 | 330 | 212.4 | 259.6 | 280.5 | 379.5 |  | 1
| Specific area coverage [MW_e/km2] | 6.0476 | 5.6382 | 5.8152 | 5.8879 | 5.8392 | 6.6332 | 4.9028 | 7.7856 | 4.6714 | E | 3
| Specific power [W_e/m2] | 383.4921 | 342.9078 | 349.3113 | 353.6777 | 350.7547 | 359.8415 | 325.9041 | 364.1052 | 331.5262 | I | 1
Notes:
General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
A starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
G. Other is planning & development, environmental impact assessment, insurances and finance costs.
H. Roughly 80 % of the total yearly O&M costs are assumed to be fixed cost and 20 % are assumed to be variable cost depending on capacity factor.
I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
References:
1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
3. EMD cost and AEP Excel calculation tool
4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
6. Interview with Per Stenholt, Vattenfall, November 21

## 21 Near shore turbines
Technology |  | 21 Near shore wind turbines
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 8.4 | 10 | 15 | 15 | 15 | 8.5 | 11.5 | 11.25 | 18.75 | A | 1, 2
| Forced outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Technical lifetime [years] | 27 | 30 | 30 | 30 | 30 | 25 | 35 | 25 | 35 | C
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 3 | 1.5 | 2.5 | D
| Space requirement [1000 m2/MW_e] | 32.0212 | 35.1844 | 35.811 | 35.811 | 35.811 | 29.9067 | 40.4621 | 26.8582 | 44.7637 | E | 3
Regulation ability
Primary regulation [p.u. per 30 seconds]
Secondary regulation [p.u. per minute]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total) [M€/MW_e, 2020] | 1.6999 | 1.488 | 1.3844 | 1.2384 | 1.1859 | 1.488 | 1.488 | 1.1859 | 1.1859 | F | 3
| Nominal investment (equipment) [M€/MW_e, 2020] | 0.91584 | 0.8468 | 0.83616 | 0.75131 | 0.72066 | 0.8468 | 0.8468 | 0.72066 | 0.72066 |  | 3
| Nominal investment (installation) [M€/MW_e, 2020] | 0.38968 | 0.3138 | 0.25365 | 0.22841 | 0.21927 | 0.3138 | 0.3138 | 0.21927 | 0.21927 |  | 3
| Nominal investment (other) [M€/MW_e, 2020] | 0.39435 | 0.32741 | 0.29454 | 0.25871 | 0.24593 | 0.32741 | 0.32741 | 0.24593 | 0.24593 | G | 3
| Fixed O&M (*total) [€/MW_e/y, 2020] | 50000 | 42000 | 39000 | 34000 | 33000 | 35700 | 48300 | 24750 | 49500 | H | 3
| Variable O&M (*total) [€/MWh_e, 2020] | 5 | 4.1721 | 3.8947 | 3.4208 | 3.2519 | 3.5463 | 16.6885 | 2.4389 | 13.0076 | H | 3
Technology-specific data
| Nominal investment (equipment: turbines) [M€/MW_e, 2020] | 0.71632 | 0.65694 | 0.65458 | 0.58469 | 0.55948 | 0.5584 | 2.6278 | 0.41961 | 2.2379 |  | 3
| Nominal investment (equipment: foundation) [M€/MW_e, 2020] | 0.13493 | 0.12851 | 0.12325 | 0.11009 | 0.10535 | 0.10924 | 0.51406 | 0.079011 | 0.42139 |  | 3, 4
| Nominal investment (equipment: array cables) [M€/MW_e, 2020] | 0.012591 | 0.011578 | 0.0093792 | 0.0090889 | 0.0089781 | 0.009841 | 0.04631 | 0.0067336 | 0.035912 |  | 3
| Nominal investment (equipment: grid connection) [M€/MW_e, 2020] | 0.052 | 0.049769 | 0.048946 | 0.047431 | 0.046853 | 0.042303 | 0.19907 | 0.03514 | 0.18741 |  | 3, 5
| Nominal investment (installation: turbines) [M€/MW_e, 2020] | 0.13367 | 0.10708 | 0.087766 | 0.078395 | 0.075016 | 0.091022 | 0.42834 | 0.056262 | 0.30006 |  | 3
| Nominal investment (installation: foundation) [M€/MW_e, 2020] | 0.20483 | 0.16078 | 0.12525 | 0.11187 | 0.10705 | 0.13666 | 0.64312 | 0.080288 | 0.4282 |  | 3
| Nominal investment (installation: array cables) [M€/MW_e, 2020] | 0.025183 | 0.022142 | 0.017635 | 0.016549 | 0.016144 | 0.01882 | 0.088566 | 0.012108 | 0.064576 |  | 3
| Nominal investment (installation: grid connection) [M€/MW_e, 2020] | 0.026 | 0.023795 | 0.023007 | 0.021591 | 0.021062 | 0.020226 | 0.09518 | 0.015797 | 0.084249 |  | 3
| Nominal investment (Project development etc.) [M€/MW_e, 2020] | 0.39435 | 0.32741 | 0.29454 | 0.25871 | 0.24593 | 0.2783 | 1.3096 | 0.18445 | 0.98374 |  | 3, 6
| Average annual full-load hours [MWh_e/MW_e] | 4100 | 4325 | 4450 | 4450 | 4450 | 3675 | 4975 | 3250 | 6500 | J | 3
| Hub height [m] | 103.5 | 115.5 | 138 | 138 | 138 | 98.175 | 132.825 | 103.5 | 207 |  | 1
| Rotor diameter [m] | 167 | 191 | 236 | 236 | 236 | 162.35 | 219.65 | 177 | 354 |  | 1
| Specific area coverage [MW_e/km2] | 31.2293 | 28.4217 | 27.9244 | 27.9244 | 27.9244 | 33.4373 | 24.7145 | 37.2325 | 22.3395 | E | 3
| Specific power [W_e/m2] | 383.4921 | 349.0144 | 342.9078 | 342.9078 | 342.9078 | 410.6052 | 303.4908 | 457.2104 | 190.5043 | I | 1
Notes:
General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
A starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
E: For Nearshore the space requirements becomes "artificial", while typically 1-row projects will be expected. The space is here calculated based on square layout to give a number.
F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
G. Other is planning & development, environmental impact assessment, insurances and finance costs.
H. Roughly 80 % of the total yearly O&M costs are assumed to be fixed cost and 20 % are assumed to be variable cost depending on capacity factor.
I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
References:
1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
3. EMD cost and AEP Excel calculation tool
4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
6. Interview with Per Stenholt, Vattenfall, November 21

## 22 Rooftop PV residential
Technology |  | PV - renewable power - solar - residential rooftop
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; note: B3,C
| Forced outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Space requirement [1000 m2/MW_e] | ctrl: 6.3636; ctrl: 5.122; ctrl: 4.5652; ctrl: 4.2857; ctrl: 4.0385; ref: 6
Regulation ability
Primary regulation [p.u. per 30 seconds]
Secondary regulation [p.u. per minute]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] | 1.5927 | 1.1828 | 0.80004 | 0.66583 | 0.60554 | 1.129 | 1.2366 | 0.51584 | 0.80615 | M,N | 2, 4
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.6723 | 1.2419 | 0.84005 | 0.69912 | 0.63581 | 1.1855 | 1.2984 | 0.54163 | 0.84645 | M,O | 2, 4
| Nominal investment (installation) [2020-MEUR/MW_e] |  | 0.2826 | 0.22767 | 0.20437 | 0.19296 | 0.26976 | 0.29545 | 0.17166 | 0.21403
| Nominal investment (equipment) [2020-MEUR/MW_e] | ctrl: 0.81387; ctrl: 0.7456; ctrl: 0.44228; ctrl: 0.34206; ctrl: 0.29869; note: W
| Nominal investment (other) [2020-MEUR/MW_e] | ctrl: 0.85846; ctrl: 0.21113; ctrl: 0.17009; ctrl: 0.15268; ctrl: 0.14416; note: W
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 16700 | 13400 | 10700 | 9600 | 8900 | 12100 | 14800 | 8100 | 9900 | P
Fixed O&M (land rent) [2020-EUR/MW_e/y]
| Fixed O&M (other) [2020-EUR/MW_e/y] | ctrl: 13400; ctrl: 10700; ctrl: 9600; ctrl: 8900
Technology-specific data
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 981.4568; ctrl: 1060.8444; ctrl: 1171.863; ctrl: 1184.1984; ctrl: 1196.5338; note: A1
| Global horizontal irradiance [MWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; note: B3,C
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 934.7208; ctrl: 1010.328; ctrl: 1116.06; ctrl: 1127.808; ctrl: 1139.556; note: A1,I
| Average annual degradation of full-load hours [p.u.] | ctrl: 0.005; ctrl: 0.004; ctrl: 0.003; ctrl: 0.003; ctrl: 0.003
| Sizing factor (DC/AC) [W_e/W_e] | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 |  |  |  |  | D | 6
| Transposition factor | ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; note: E
| Performance ratio (measure of combined losses) [p.u.] | ctrl: 0.79; ctrl: 0.86; ctrl: 0.95; ctrl: 0.96; ctrl: 0.97; note: F
| Performance ratio (contribution from bifaciality) [p.u.] | ref: 3
| PV module conversion efficiency [p.u.] | 0.165 | 0.205 | 0.23 | 0.245 | 0.26 |  |  |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Space requirement (per DC) [1000m2/MW_e] | ctrl: 6.0606; ctrl: 4.878; ctrl: 4.3478; ctrl: 4.0816; ctrl: 3.8462; ref: 6
| Nominal investment (equipment: pv modules [2020-MEUR/MW_e] | 0.81387 | 0.49112 | 0.27221 | 0.20271 | 0.17327 | 0.4688 | 0.51345 | 0.13645 | 0.32639 | M,O
| Nominal investment (equipment: inverter [2020-MEUR/MW_e] |  | 0.22318 | 0.14485 | 0.11672 | 0.10405 | 0.21303 | 0.23332 | 0.086266 | 0.12244
| Nominal investment (equipment: grid connection) [2020-MEUR/MW_e] |  | 0.031299 | 0.025216 | 0.022635 | 0.021371 | 0.029877 | 0.032722 | 0.019012 | 0.023704
Nominal investment (other: soft costs) [2020-MEUR/MW_e]
| Nominal investment (other: other, i.e. residual balance of plant) [2020-MEUR/MW_e] | 0.85846 | 0.21113 | 0.17009 | 0.15268 | 0.14416 | 0.20153 | 0.22073 | 0.12824 | 0.1599
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | 0.77511 | 0.46774 | 0.25925 | 0.19306 | 0.16502 | 0.44647 | 0.489 | 0.12995 | 0.31085 | M,O
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] |  | 0.21255 | 0.13796 | 0.11116 | 0.099095 | 0.20289 | 0.22221 | 0.082158 | 0.11661
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] |  | 0.029809 | 0.024015 | 0.021557 | 0.020353 | 0.028454 | 0.031164 | 0.018107 | 0.022575
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] |  | 0.26915 | 0.21683 | 0.19464 | 0.18377 | 0.25691 | 0.28138 | 0.16349 | 0.20383
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | 0.81759 | 0.20108 | 0.16199 | 0.14541 | 0.13729 | 0.19194 | 0.21022 | 0.12214 | 0.15228
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | 15900 | 12800 | 10200 | 9100 | 8500 | 11500 | 14100 | 7700 | 9400 | P
Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y]
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 12800; ctrl: 10200; ctrl: 9100; ctrl: 8500
Nominal investment (*total, per DC) [2020-MEUR/MW_e]
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | ctrl: 39.54%
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | ctrl: 17.97%
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | ctrl: 2.52%
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] | ctrl: 22.76%
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | ctrl: 17%
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 – 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen):
| Real prices (€-2015) | ctrl: 2015; ctrl: 2016; ctrl: 2017; ctrl: 2018; ctrl: 2019; lower: 2020
| Index | ctrl: 1; ctrl: 1.002; ctrl: 1.014; ctrl: 1.03; ctrl: 1.043; lower: 1.062
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. ” Photovoltaics report”. Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Rooftop PV commercial
Technology |  | PV - renewable power - solar - commercial/industrial rooftop
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; note: B2,C
| Forced outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Space requirement [1000 m2/MW_e] | ctrl: 6.6667; ctrl: 5.3659; ctrl: 4.7826; ctrl: 4.4898; ctrl: 4.2308; ref: 6
Regulation ability
Primary regulation [p.u. per 30 seconds]
Secondary regulation [p.u. per minute]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] | 1.2976 | 0.79301 | 0.51437 | 0.41865 | 0.37627 | 0.77957 | 0.84005 | 0.32541 | 0.53424 | M,N | 2, 4
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.4274 | 0.87231 | 0.56581 | 0.46052 | 0.4139 | 0.85753 | 0.92406 | 0.35795 | 0.58766 | M,O | 2, 4
| Nominal investment (installation) [2020-MEUR/MW_e] | 0 | 0.13085 | 0.10541 | 0.094626 | 0.089342 | 0.12863 | 0.13861 | 0.081853 | 0.10041
| Nominal investment (equipment) [2020-MEUR/MW_e] | 0.8136 | 0.65423 | 0.39012 | 0.30281 | 0.265 | 0.64315 | 0.69304 | 0.22153 | 0.42031 | W
| Nominal investment (other) [2020-MEUR/MW_e] | 0.61377 | 0.087231 | 0.070276 | 0.063084 | 0.059561 | 0.085753 | 0.092406 | 0.054568 | 0.066939 | W
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 14300 | 10600 | 8900 | 8000 | 7500 | 9500 | 11700 | 6700 | 8300 | P
Fixed O&M (land rent) [2020-EUR/MW_e/y]
| Fixed O&M (other) [2020-EUR/MW_e/y] | ctrl: 14300; ctrl: 10600; ctrl: 8900; ctrl: 8000; ctrl: 7500
Technology-specific data
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1045.6516; ctrl: 1111.3608; ctrl: 1227.666; ctrl: 1240.5888; ctrl: 1253.5116; note: A1
| Global horizontal irradiance [MWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; note: B2,C
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 950.5924; ctrl: 1010.328; ctrl: 1116.06; ctrl: 1127.808; ctrl: 1139.556; note: A1,I
| Average annual degradation of full-load hours [p.u.] | ctrl: 0.005; ctrl: 0.004; ctrl: 0.003; ctrl: 0.003; ctrl: 0.003
| Sizing factor (DC/AC) [W_e/W_e] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 |  |  |  |  | D | 6
| Transposition factor | ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; note: E
| Performance ratio (measure of combined losses) [p.u.] | ctrl: 0.81; ctrl: 0.86; ctrl: 0.95; ctrl: 0.96; ctrl: 0.97; note: F
| Performance ratio (contribution from bifaciality) [p.u.] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0.01; ctrl: 0.02; ref: 3
| PV module conversion efficiency [p.u.] | 0.165 | 0.205 | 0.23 | 0.245 | 0.26 |  |  |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Space requirement (per DC) [1000m2/MW_e] | 6.0606 | 4.878 | 4.3478 | 4.0816 | 3.8462 |  |  |  |  | W | 6
| Nominal investment (equipment: pv modules [2020-MEUR/MW_e] | 0.8136 | 0.43616 | 0.24174 | 0.18002 | 0.15388 | 0.42876 | 0.46203 | 0.1248 | 0.28986 | M,O
| Nominal investment (equipment: inverter [2020-MEUR/MW_e] |  | 0.17446 | 0.11323 | 0.091243 | 0.081337 | 0.17151 | 0.18481 | 0.069449 | 0.096983
| Nominal investment (equipment: grid connection) [2020-MEUR/MW_e] |  | 0.043616 | 0.035138 | 0.031542 | 0.029781 | 0.042876 | 0.046203 | 0.027284 | 0.03347
Nominal investment (other: soft costs) [2020-MEUR/MW_e]
| Nominal investment (other: other, i.e. residual balance of plant) [2020-MEUR/MW_e] | 0.61377 | 0.087231 | 0.070276 | 0.063084 | 0.059561 | 0.085753 | 0.092406 | 0.054568 | 0.066939
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | 0.73963 | 0.39651 | 0.21977 | 0.16366 | 0.13989 | 0.38978 | 0.42003 | 0.11345 | 0.26351 | M,O
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] |  | 0.1586 | 0.10294 | 0.082948 | 0.073943 | 0.15591 | 0.16801 | 0.063135 | 0.088166
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] |  | 0.039651 | 0.031944 | 0.028675 | 0.027073 | 0.038978 | 0.042003 | 0.024804 | 0.030427
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] |  | 0.11895 | 0.095831 | 0.086024 | 0.08122 | 0.11694 | 0.12601 | 0.074411 | 0.091281
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | 0.55797 | 0.079301 | 0.063888 | 0.057349 | 0.054147 | 0.077957 | 0.084005 | 0.049608 | 0.060854
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | 13000 | 9600 | 8100 | 7300 | 6800 | 8600 | 10600 | 6100 | 7500 | P
Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y]
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 13000; ctrl: 9600; ctrl: 8100; ctrl: 7300; ctrl: 6800
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 – 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen):
| Real prices (€-2015) | ctrl: 2015; ctrl: 2016; ctrl: 2017; ctrl: 2018; ctrl: 2019; lower: 2020
| Index | ctrl: 1; ctrl: 1.002; ctrl: 1.014; ctrl: 1.03; ctrl: 1.043; lower: 1.062
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. ” Photovoltaics report”. Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Utility-scale PV
Technology |  | PV - renewable power - solar - utility-scale, ground mounted
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 4; ctrl: 40; ctrl: 40; ctrl: 40; ctrl: 40
| Forced outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
| Space requirement [1000 m2/MW_e] | 20.25 | 13.75 | 12.2554 | 11.5051 | 10.8413 |  |  |  |  | B,B1 | 6
Regulation ability
Primary regulation [p.u. per 30 seconds] | bar: note
Secondary regulation [p.u. per minute] | bar: note
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] | 1.1467 | 0.45 | 0.30698 | 0.25666 | 0.23406 | 0.435 | 0.48 | 0.20266 | 0.32019 | M,N,O,Q | 2, 4
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.5481 | 0.5625 | 0.38373 | 0.32082 | 0.29258 | 0.54375 | 0.6 | 0.25332 | 0.40023 | M,N,O,Q | 2, 4
| Nominal investment (installation) [2020-MEUR/MW_e] | 0.14334 | 0.12776 | 0.10293 | 0.092394 | 0.087235 | 0.1235 | 0.13628 | 0.07859 | 0.098721 | V
| Nominal investment (equipment) [2020-MEUR/MW_e] | 1.0894 | 0.34914 | 0.21184 | 0.16653 | 0.1469 | 0.3375 | 0.37242 | 0.12208 | 0.23537 | W
| Nominal investment (other) [2020-MEUR/MW_e] | 0.31535 | 0.085598 | 0.068961 | 0.061903 | 0.058446 | 0.082745 | 0.091304 | 0.052654 | 0.066142 | W
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 13600 | 11300 | 9500 | 8100 | 7400 | 10100 | 12400 | 6600 | 8100
| Fixed O&M (land rent) [2020-EUR/MW_e/y] | ctrl: 4400; ctrl: 3900; ctrl: 3100; ctrl: 2500; note: S
| Fixed O&M (other) [2020-EUR/MW_e/y] | ctrl: 6900; ctrl: 5600; ctrl: 5000; ctrl: 4900
Technology-specific data
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1324.7979; ctrl: 1343.277; ctrl: 1483.8525; ctrl: 1499.472; ctrl: 1515.0915; note: A1
| Global horizontal irradiance [MWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 5.4; ctrl: 50; ctrl: 50; ctrl: 50; ctrl: 50; note: C
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 981.3318; ctrl: 1074.6216; ctrl: 1187.082; ctrl: 1199.5776; ctrl: 1212.0732; note: A1, K
| Average annual degradation of full-load hours [p.u.] | 0.005 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.005 |  |  | A2
| Sizing factor (DC/AC) [W_e/W_e] | 1.35 | 1.25 | 1.25 | 1.25 | 1.25 |  |  |  |  | D | 6
| Transposition factor | ctrl: 1.15; ctrl: 1.17; ctrl: 1.17; ctrl: 1.17; ctrl: 1.17; note: E
| Performance ratio (measure of combined losses) [p.u.] | ctrl: 0.81; ctrl: 0.86; ctrl: 0.95; ctrl: 0.96; ctrl: 0.97; note: F
| Performance ratio (contribution from bifaciality) [p.u.] | 0 | 0.01 | 0.05 | 0.05 | 0.05 |  |  |  |  | H | 3
| PV module conversion efficiency [p.u.] | 0.165 | 0.205 | 0.23 | 0.245 | 0.26 | 0.2 | 0.21 |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Space requirement (per DC) [1000m2/MW_e] | 15 | 11 | 9.8043 | 9.2041 | 8.6731 |  |  |  |  | B,B1 | 6
| Nominal investment (equipment: pv modules [2020-MEUR/MW_e] | 0.88873 | 0.25679 | 0.14233 | 0.10599 | 0.0906 | 0.24823 | 0.27391 | 0.072253 | 0.17066
| Nominal investment (equipment: inverter [2020-MEUR/MW_e] | 0.11467 | 0.031207 | 0.020254 | 0.016321 | 0.014549 | 0.030166 | 0.033287 | 0.012215 | 0.017468
| Nominal investment (equipment: grid connection) [2020-MEUR/MW_e] | 0.086006 | 0.061141 | 0.049258 | 0.044216 | 0.041747 | 0.059103 | 0.065217 | 0.03761 | 0.047244
| Nominal investment (other: soft costs) [2020-MEUR/MW_e] | 0.086006 | 0.036685 | 0.029555 | 0.02653 | 0.025048 | 0.035462 | 0.03913 | 0.022566 | 0.028346 | V
| Nominal investment (other: other, i.e. residual balance of plant) [2020-MEUR/MW_e] | 0.22935 | 0.048913 | 0.039406 | 0.035373 | 0.033398 | 0.047283 | 0.052174 | 0.030088 | 0.037795
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | 0.65832 | 0.20543 | 0.11386 | 0.084792 | 0.07248 | 0.19859 | 0.21913 | 0.057802 | 0.13653
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | 0.084944 | 0.024965 | 0.016204 | 0.013057 | 0.011639 | 0.024133 | 0.02663 | 0.0097724 | 0.013974
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | 0.063708 | 0.048913 | 0.039406 | 0.035373 | 0.033398 | 0.047283 | 0.052174 | 0.030088 | 0.037795 | R
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] | 0.10618 | 0.10221 | 0.082343 | 0.073916 | 0.069788 | 0.098802 | 0.10902 | 0.062872 | 0.078977 | V
| Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | 0.063708 | 0.029348 | 0.023644 | 0.021224 | 0.020039 | 0.02837 | 0.031304 | 0.018053 | 0.022677 | V
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | 0.16989 | 0.03913 | 0.031525 | 0.028298 | 0.026718 | 0.037826 | 0.041739 | 0.02407 | 0.030236
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | 10100 | 9000 | 7600 | 6500 | 5900 | 8100 | 9900 | 5300 | 6500
| Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | ctrl: 3500; ctrl: 3100; ctrl: 2500; ctrl: 2000; note: S; ref: 6
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 5500; ctrl: 4500; ctrl: 4000; ctrl: 3900; note: P2
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 – 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen):
| Real prices (€-2015) | ctrl: 2015; ctrl: 2016; ctrl: 2017; ctrl: 2018; ctrl: 2019; lower: 2020
| Index | ctrl: 1; ctrl: 1.002; ctrl: 1.014; ctrl: 1.03; ctrl: 1.043; lower: 1.062
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. ” Photovoltaics report”. Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Utility-scale PV tracker
Technology |  | PV - renewable power - solar - utility-scale ground mounted, single axis tracking
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 40; ctrl: 40; ctrl: 40; ctrl: 40
| Forced outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
| Space requirement [1000 m2/MW_e] | ctrl: 17.875; ctrl: 15.9321; ctrl: 14.9566; ctrl: 14.0938; note: B,B1; ref: 6
Regulation ability
Primary regulation [p.u. per 30 seconds] | bar: note
Secondary regulation [p.u. per minute] | bar: note
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] |  | 0.52028 | 0.36358 | 0.30745 | 0.28201 | 0.47781 | 0.56275 | 0.23357 | 0.37782 | M,N,O,Q | 2, 4
| Nominal investment (*total) [2020-MEUR/MW_e] |  | 0.65035 | 0.45447 | 0.38431 | 0.35251 | 0.59726 | 0.70344 | 0.29196 | 0.47227 | M,N,O,Q | 2, 4
| Nominal investment (installation) [2020-MEUR/MW_e] |  | 0.12783 | 0.10298 | 0.092444 | 0.087282 | 0.11739 | 0.13827 | 0.074704 | 0.10016 | V
| Nominal investment (equipment) [2020-MEUR/MW_e] |  | 0.43688 | 0.28249 | 0.22993 | 0.20675 | 0.40121 | 0.47254 | 0.1672 | 0.305 | W
| Nominal investment (other) [2020-MEUR/MW_e] |  | 0.085644 | 0.068998 | 0.061936 | 0.058478 | 0.078653 | 0.092636 | 0.05005 | 0.067106 | W
| Fixed O&M (*total) [2020-EUR/MW_e/y] |  | 12100 | 10400 | 9400 | 9000 | 10900 | 13400 | 8100 | 9900 | P2
| Fixed O&M (land rent) [2020-EUR/MW_e/y] | ctrl: 5300; ctrl: 4800; ctrl: 4400; ctrl: 4100; note: S
| Fixed O&M (other) [2020-EUR/MW_e/y] | ctrl: 6900; ctrl: 5600; ctrl: 5000; ctrl: 4900
Technology-specific data
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1544.7685; ctrl: 1712.1375; ctrl: 1724.3928; ctrl: 1742.3552; note: A1
| Global horizontal irradiance [MWh/m2/y] | ctrl: 1068; ctrl: 1068; ctrl: 1068; ctrl: 1068; note: A; ref: 1
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 50; ctrl: 50; ctrl: 50; ctrl: 50; note: C
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 1235.8148; ctrl: 1369.71; ctrl: 1379.5142; ctrl: 1393.8842; note: A1, K
| Average annual degradation of full-load hours [p.u.] |  | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.005 |  |  | A2
| Sizing factor (DC/AC) [W_e/W_e] | ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; note: D; ref: 5, 6
| Transposition factor | ctrl: 1.3455; ctrl: 1.35; ctrl: 1.3455; ctrl: 1.3455; note: E
| Performance ratio (measure of combined losses) [p.u.] | ctrl: 0.86; ctrl: 0.95; ctrl: 0.96; ctrl: 0.97; note: F
| Performance ratio (contribution from bifaciality) [p.u.] | ctrl: 0.01; ctrl: 0.05; ctrl: 0.05; ctrl: 0.05; note: H; ref: 3
| PV module conversion efficiency [p.u.] |  | 0.205 | 0.23 | 0.245 | 0.26 | 0.2 | 0.21 |  |  | U | 3
| Inverter lifetime [years] | ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Space requirement (per DC) [1000m2/MW_e] | ctrl: 14.3; ctrl: 12.7457; ctrl: 11.9653; ctrl: 11.275; note: B,B1; ref: 6
| Nominal investment (equipment: pv modules [2020-MEUR/MW_e] |  | 0.25693 | 0.14241 | 0.10605 | 0.090649 | 0.23596 | 0.27791 | 0.06868 | 0.17075
| Nominal investment (equipment: inverter [2020-MEUR/MW_e] |  | 0.031223 | 0.020265 | 0.01633 | 0.014557 | 0.028675 | 0.033772 | 0.011611 | 0.017723
| Nominal investment (equipment: grid connection) [2020-MEUR/MW_e] |  | 0.061174 | 0.049284 | 0.04424 | 0.04177 | 0.056181 | 0.066168 | 0.03575 | 0.047933
| Nominal investment (equipment: tracker related costs) [2020-MEUR/MW_e] |  | 0.087547 | 0.070531 | 0.063313 | 0.059777 | 0.080401 | 0.094694 | 0.051163 | 0.068597 | T
| Nominal investment (other: soft costs) [2020-MEUR/MW_e] |  | 0.04894 | 0.039427 | 0.035392 | 0.033416 | 0.044944 | 0.052935 | 0.0286 | 0.038346 | V
| Nominal investment (other: other, i.e. residual balance of plant) [2020-MEUR/MW_e] |  | 0.036705 | 0.029571 | 0.026544 | 0.025062 | 0.033708 | 0.039701 | 0.02145 | 0.02876
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] |  | 0.20555 | 0.11393 | 0.084838 | 0.072519 | 0.18877 | 0.22233 | 0.054944 | 0.1366
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] |  | 0.024979 | 0.016212 | 0.013064 | 0.011645 | 0.02294 | 0.027018 | 0.0092891 | 0.014178
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] |  | 0.04894 | 0.039427 | 0.035392 | 0.033416 | 0.044944 | 0.052935 | 0.0286 | 0.038346 | R
| Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] |  | 0.070038 | 0.056425 | 0.05065 | 0.047822 | 0.064321 | 0.075755 | 0.04093 | 0.054878 | T
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] |  | 0.10226 | 0.082387 | 0.073956 | 0.069826 | 0.093916 | 0.11061 | 0.059763 | 0.080128 | V
| Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] |  | 0.039152 | 0.031542 | 0.028314 | 0.026733 | 0.035956 | 0.042348 | 0.02288 | 0.030677 | V
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] |  | 0.029364 | 0.023656 | 0.021235 | 0.02005 | 0.026967 | 0.031761 | 0.01716 | 0.023008
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] |  | 9700 | 8300 | 7500 | 7200 | 8700 | 10700 | 6500 | 7900
| Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | ctrl: 4200; ctrl: 3800; ctrl: 3500; ctrl: 3300; note: S; ref: 6
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 5500; ctrl: 4500; ctrl: 4000; ctrl: 3900; note: P2
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 – 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen):
| Real prices (€-2015) | ctrl: 2015; ctrl: 2016; ctrl: 2017; ctrl: 2018; ctrl: 2019; lower: 2020
| Index | ctrl: 1; ctrl: 1.002; ctrl: 1.014; ctrl: 1.03; ctrl: 1.043; lower: 1.062
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. ” Photovoltaics report”. Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 23 Wave Energy
Wave Power
|  | 2015 | 2020 | 2030 | 2050 | Note | Ref
Energy/technical data
| Generating capacity for one power plant (MW) | 1.0 - 30 | 2.0 - 50 | 10 - 100 | 50 - 500 |  | 1;1;4;4
| Length of installation of one power plant km | 0.2 - 2 | 0.2 - 5.0 | 1 - 20 | 5 - 100 |  | 1;1;4;4
| Annual generated electricity production (MWh/MW) | 1500 | 2500 | 3500 | 4500 |  | 4
| Availlability (%) | 90 | 95 | 97 | 98 |  | 4
| Technical lifetime (years) | 10 | 20 | 25 | 30 |  | 4
| Construction time | 3 - 4 | 3 - 4 | 3 - 4 | 3 - 4 | C | 4
Financial data
| Nominal investment (M€/MW) | 4.6-11 | 3.8-9.0 | 2.2-4.5 | 1.6 | A+B | 2;2;2;3
| O&M (€/MWh) | 20 | 15 | 10 | 7 |  | 4
References:
1 | Wave Net final report, Project no. ERK5 – CT –1999-20001 (2000 - 2003)
2 | “Energy Technology Perspectives 2008”, International Energy Agency, 2008.
3 | “Energy Technology Perspectives 2010”, International Energy Agency, 2010.
4 | Danish Wave Energy Association, 2012
Notes:
A | The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning curve effect have been achieved.
B | Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
C | Much dependent on plant size and location.
This sheet has been moved from a previous datasheet and
does therefore not follow the same guideline as the remainder
of the data sheets in the file.

## 40 Comp. hp, airsource 1 MW
| Technology | Air source heat pumps 1 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 1 | 1 | 1 | 1 | 1 | 0.3 | 1.5 | 0.2 | 1.5
| Total efficiency, net (%), name plate | 255 | 260 | 265 | 275 | 280 | 240 | 300 | 250 | 320 | A, A1, B, C | 1;14;15
| Total efficiency , net (%), annual average | 290 | 295 | 300 | 310 | 315 | 275 | 335 | 285 | 355 | A, A1, B, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | E | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | F, G | 9;14;15
| Space requirements (1000m2 per MWheat) | 1 | 1 | 1 | 1 | 1 | 0.7 | 2 | 0.7 | 2 | Q | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 5 | 50 | H | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | H | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | H, J | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | H, I | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 1.4271 | 1.4271 | 1.3319 | 1.3319 | 1.3319 | 0.95139 | 1.9028 | 0.95139 | 1.9028 | A,K,L,P,Q | 1;14;15
| - of which equipment | 1.0703 | 1.0703 | 0.99895 | 0.99895 | 0.99895 | 0.71354 | 1.4271 | 0.71354 | 1.4271 | A | 1;14;15
| - of which installation | 0.25687 | 0.25687 | 0.23975 | 0.23975 | 0.23975 | 0.17125 | 0.19028 | 0.17125 | 0.19028 | A | 1;14;15
| - of which grid connection | 0.028542 | 0.028542 | 0.026639 | 0.026639 | 0.026639 | 0.019028 | 0.19028 | 0.019028 | 0.19028 | K | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | 1;14;15
| Variable O&M (€/MWh) | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.17 | 3.17 | 2.17 | 3.17 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E,N | 1;14;15
| - of which is other O&M costs (€/MWh) | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.17 | 3.17 | 2.17 | 3.17 | M | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Technology specific data
Notes
A | Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Includes energy consumption for defrosting and auxiliary electricity consumption.
C | Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E | Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F | Does not include tendering and regulatory approvals.
G | The development within construction time will depend on future production figures and standardization of plants.
H | The regulation ablility will depend on the future markets for regulation services.
I | Cold start of time is starting a heat pump where stand by heating has not been applied
J | Operation at part load will usually increase COP but also variable O&M costs
K | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L | Land is usually owned by the company
M | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O | 1/4 MWh-heat per MW is lost during startup
P | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
Q | Including land for air coolers
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, airsource 3 MW
| Technology | Air source heat pumps 3 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Total efficiency, net (%), name plate | 310 | 315 | 320 | 330 | 340 | 290 | 330 | 300 | 350 | A, A1, B, C | 1;14;15
| Total efficiency , net (%), annual average | 340 | 350 | 360 | 365 | 370 | 320 | 370 | 330 | 380 | A, A1, B, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | E | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | F, G | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 1.2 | 0.5 | 1.2 | Q | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 100 | 5 | 100 | H | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | H | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | H, J | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | H, I | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 0.95139 | 0.95139 | 0.85625 | 0.85625 | 0.85625 | 0.76111 | 1.4271 | 0.66597 | 1.4271 | A,K,L,P,Q | 1;14;15
| - of which equipment | 0.76111 | 0.76111 | 0.685 | 0.685 | 0.685 | 0.60889 | 1.1417 | 0.53278 | 1.1417 | A | 1;14;15
| - of which installation | 0.17125 | 0.17125 | 0.15412 | 0.15412 | 0.15412 | 0.137 | 0.14271 | 0.11987 | 0.14271 | A | 1;14;15
| - of which grid connection | 0.019028 | 0.019028 | 0.017125 | 0.017125 | 0.017125 | 0.015222 | 0.14271 | 0.013319 | 0.14271 | K | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | 1;14;15
| Variable O&M (€/MWh) | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 3.69 | 2.19 | 2.19 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E,N | 1;14;15
| - of which is other O&M costs (€/MWh) | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 3.69 | 2.19 | 2.19 | M | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Technology specific data
Notes
A | Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Includes energy consumption for defrosting and auxiliary electricity consumption.
C | Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E | Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F | Does not include tendering and regulatory approvals.
G | The development within construction time will depend on future production figures and standardization of plants.
H | The regulation ablility will depend on the future markets for regulation services.
I | Cold start of time is starting a heat pump where stand by heating has not been applied
J | Operation at part load will usually increase COP but also variable O&M costs
K | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L | Land is usually owned by the company
M | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O | 1/4 MWh-heat per MW is lost during startup
P | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
Q | Including land for air coolers
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, airsource 10 MW
| Technology | Air source heat pumps 10 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Total efficiency, net (%), name plate | 350 | 350 | 355 | 360 | 360 | 330 | 370 | 330 | 380 | A, A1, B, C | 1;14;15
| Total efficiency , net (%), annual average | 380 | 380 | 385 | 390 | 390 | 360 | 400 | 360 | 410 | A, A1, B, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | E | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | F, G | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 1 | 0.4 | 1 | Q | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 100 | 5 | 100 | H | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | H | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | H, J | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | H, I | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 0.85625 | 0.85625 | 0.76111 | 0.76111 | 0.76111 | 0.66597 | 1.1417 | 0.66597 | 1.1417 | A,K,L,P,Q | 1;14;15
| - of which equipment | 0.685 | 0.685 | 0.60889 | 0.60889 | 0.60889 | 0.53278 | 0.91333 | 0.53278 | 0.91333 | A | 1;14;15
| - of which installation | 0.15412 | 0.15412 | 0.137 | 0.137 | 0.137 | 0.11987 | 0.11417 | 0.11987 | 0.11417 | A | 1;14;15
| - of which grid connection | 0.017125 | 0.017125 | 0.015222 | 0.015222 | 0.015222 | 0.013319 | 0.11417 | 0.013319 | 0.11417 | K | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | 1;14;15
| Variable O&M (€/MWh) | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1 | 2.69 | 1 | 2.69 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E,N | 1;14;15
| - of which is other O&M costs (€/MWh) | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.5 | 2.69 | 1.5 | 2.69 | M | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Technology specific data
Notes
A | Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Includes energy consumption for defrosting and auxiliary electricity consumption.
C | Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E | Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F | Does not include tendering and regulatory approvals.
G | The development within construction time will depend on future production figures and standardization of plants.
H | The regulation ablility will depend on the future markets for regulation services.
I | Cold start of time is starting a heat pump where stand by heating has not been applied
J | Operation at part load will usually increase COP but also variable O&M costs
K | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L | Land is usually owned by the company
M | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O | 1/4 MWh-heat per MW is lost during startup
P | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
Q | Including land for air coolers
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 1 MW
| Technology | Heat pumps utilizing industrial waste heat 1 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 1 | 1 | 1 | 1 | 1 | 0.3 | 1.5 | 0.2 | 1.5
| Total efficiency, net (%), name plate | 400 | 410 | 420 | 430 | 440 | 400 | 430 | 400 | 450 | A, A1, B, D | 1;14;15
| Total efficiency , net (%), annual average | 410 | 420 | 430 | 440 | 450 | 410 | 450 | 410 | 480 | A, A1, C, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | D | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | E, F | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 5 | 50 | G | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | G | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | G, I | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | G, H | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 1.2368 | 1.2368 | 1.1417 | 1.1417 | 1.1417 | 0.95139 | 1.9028 | 0.95139 | 1.9028 | A,J,K,O | 1;14;15
| - of which equipment | 0.9276 | 0.9276 | 0.85625 | 0.85625 | 0.85625 | 0.71354 | 1.4271 | 0.71354 | 1.4271 | A | 1;14;15
| - of which installation | 0.22262 | 0.22262 | 0.2055 | 0.2055 | 0.2055 | 0.17125 | 0.19028 | 0.17125 | 0.19028 | A | 1;14;15
| - of which grid connection | 0.024736 | 0.024736 | 0.022833 | 0.022833 | 0.022833 | 0.019028 | 0.19028 | 0.019028 | 0.19028 | J | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | 1;14;15
| Variable O&M (€/MWh) | 2.69 | 2.69 | 2.69 | 3.09 | 3.17 | 1.69 | 2.69 | 2.69 | 3.17 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D,M | 1;14;15
| - of which is other O&M costs (€/MWh) | 2.69 | 2.69 | 2.69 | 3.09 | 3.17 | 1.69 | 2.69 | 2.69 | 3.17 | L | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Technology specific data
Notes
A | Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D | Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E | Does not include tendering and regulatory approvals.
F | The development within construction time will depend on future production figures and standardization of plants.
G | The regulation ability will depend on the future marktes for regulation services.
H | Cold start of time is starting a heat pump where stand by heating has not been applied
I | Operation at part load will usually increase COP but also variable O&M costs
J | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K | Land is usually owned by the company
L | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N | 1/4 MWh-heat per MW is lost during startup
O | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 3 MW
| Technology | Heat pumps utilizing industrial waste heat 3 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Total efficiency, net (%), name plate | 450 | 460 | 470 | 480 | 490 | 440 | 480 | 450 | 510 | A, A1, B, D | 1;14;15
| Total efficiency , net (%), annual average | 460 | 470 | 480 | 490 | 500 | 450 | 490 | 460 | 520 | A, A1, C, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | D | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | E, F | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.1 | 0.03 | 0.1 |  | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 5 | 50 | G | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | G | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | G, I | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | G, H | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 0.85625 | 0.85625 | 0.76111 | 0.76111 | 0.76111 | 0.66597 | 1.1417 | 0.66597 | 1.1417 | A,J,K,O | 1;14;15
| - of which equipment | 0.685 | 0.685 | 0.60889 | 0.60889 | 0.60889 | 0.53278 | 0.91333 | 0.53278 | 0.91333 | A | 1;14;15
| - of which installation | 0.15412 | 0.15412 | 0.137 | 0.137 | 0.137 | 0.11987 | 0.11417 | 0.11987 | 0.11417 | A | 1;14;15
| - of which grid connection | 0.017125 | 0.017125 | 0.015222 | 0.015222 | 0.015222 | 0.013319 | 0.11417 | 0.013319 | 0.11417 | J | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | 1;14;15
| Variable O&M (€/MWh) | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 2.19 | 2.17 | 2.19 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D,M | 1;14;15
| - of which is other O&M costs (€/MWh) | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 2.19 | 2.17 | 2.19 | L | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Technology specific data
Notes
A | Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D | Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E | Does not include tendering and regulatory approvals.
F | The development within construction time will depend on future production figures and standardization of plants.
G | The regulation ability will depend on the future marktes for regulation services.
H | Cold start of time is starting a heat pump where stand by heating has not been applied
I | Operation at part load will usually increase COP but also variable O&M costs
J | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K | Land is usually owned by the company
L | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N | 1/4 MWh-heat per MW is lost during startup
O | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 10 MW
| Technology | Heat pumps utilizing industrial waste heat 10 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Total efficiency, net (%), name plate | 500 | 510 | 520 | 530 | 540 | 490 | 520 | 500 | 560 | A, A1, B, D | 1;14;15
| Total efficiency , net (%), annual average | 510 | 520 | 530 | 540 | 550 | 500 | 530 | 510 | 570 | A, A1, C, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | D | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | E, F | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 |  | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 5 | 50 | G | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | G | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | G, I | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | G, H | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 0.66597 | 0.66597 | 0.57083 | 0.57083 | 0.57083 | 0.47569 | 0.95139 | 0.47569 | 0.95139 | A,J,K,O | 1;14;15
| - of which equipment | 0.53278 | 0.53278 | 0.45666 | 0.45666 | 0.45666 | 0.38055 | 0.76111 | 0.38055 | 0.76111 | A | 1;14;15
| - of which installation | 0.11987 | 0.11987 | 0.10275 | 0.10275 | 0.10275 | 0.085625 | 0.095139 | 0.085625 | 0.095139 | A | 1;14;15
| - of which grid connection | 0.013319 | 0.013319 | 0.011417 | 0.011417 | 0.011417 | 0.0095139 | 0.095139 | 0.0095139 | 0.095139 | J | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | 1;14;15
| Variable O&M (€/MWh) | 1.69 | 1.69 | 2.01 | 2.09 | 1.69 | 1.19 | 2.19 | 1.69 | 2.67 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D,M | 1;14;15
| - of which is other O&M costs (€/MWh) | 1.69 | 1.69 | 2.01 | 2.09 | 1.69 | 1.19 | 2.19 | 1.69 | 2.67 | L | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Technology specific data
Notes
A | Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D | Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E | Does not include tendering and regulatory approvals.
F | The development within construction time will depend on future production figures and standardization of plants.
G | The regulation ability will depend on the future marktes for regulation services.
H | Cold start of time is starting a heat pump where stand by heating has not been applied
I | Operation at part load will usually increase COP but also variable O&M costs
J | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K | Land is usually owned by the company
L | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N | 1/4 MWh-heat per MW is lost during startup
O | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, seawater 20 MW
| Technology | Heat pumps utilizing sea water 20 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 20 | 20 | 20 | 20 | 20 | 10 | 50 | 10 | 100
| Total efficiency, net (%), name plate | 340 | 340 | 340 | 350 | 350 | 330 | 350 | 340 | 360 | A, B, D | 1;14;15
| Total efficiency , net (%), annual average | 370 | 370 | 370 | 380 | 380 | 360 | 380 | 370 | 390 | A, C, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | D | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 1 | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.5 | 1.5 | E, F | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 | O | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 5 | 50 | G | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | G | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | G, I | 1;9;14;15
| Warm start-up time (hours) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | G | 9;14;15
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 2 | G, H | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 0.47569 | 0.47569 | 0.38055 | 0.38055 | 0.38055 | 0.28542 | 1 | 0.28542 | 1 | A,J,K,O | 1;14;15
| - of which equipment | 0.40434 | 0.40434 | 0.32347 | 0.32347 | 0.32347 | 0.2426 | 0.85 | 0.2426 | 0.85 | A | 1;14;15
| - of which installation | 0.071354 | 0.071354 | 0.057083 | 0.057083 | 0.057083 | 0.042812 | 0.05 | 0.042812 | 0.05 | A | 1;14;15
| - of which grid connection | 0.0047569 | 0.0045257 | 0.0036205 | 0.0036205 | 0.0036205 | 0.0027154 | 0.095139 | 0.0027154 | 0.095139 | J | 1;14;15
| Fixed O&M (€/MJ/s/year) | 4000 | 4000 | 4000 | 4000 | 4000 | 2000 | 5000 | 2000 | 5000 | L | 1;14;15
| Variable O&M (€/MWh) | 1.19 | 1.19 | 1.51 | 1.59 | 1.67 | 1.19 | 1.69 | 1.47 | 1.19 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | 1;14;15
| - of which is other O&M costs (€/MWh) | 1.19 | 1.19 | 1.51 | 1.59 | 1.67 | 1.19 | 1.69 | 1.47 | 1.19 | L | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Technology specific data
Notes
A | Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
B | Total efficiency, net (%), name plate is at a sea water temperature of 4 °C and district heating temperatures of 40 °C return and 80 °C forward.
C | Annual average is at varying sea water temperatures and district heating temperatures of 40 °C return and 80 °C forward.
D | Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E | Does not include tendering and regulatory approvals.
F | The development within construction time will depend on future production figures and standardization of plants.
G | The regulation ability will depend on the future marktes for regulation services.
H | Cold start of time is starting a heat pump where stand by heating has not been applied
I | Operation at part load will usually increase COP but also variable O&M costs
J | It is assumed that heat pumps is connected to existing power stations
K | Land is usually owned by the company
L | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N | 1/4 MWh-heat per MW is lost during startup
O | Regards heat pumps that are installed at existing power plants utilizing existing infra structure such as power supply, seawater intake, DH pipes etc. For stand alone plants it is estimated that the total investment is around the upper uncertainty in the table.
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Absorption heat pump, DH
| Technology | 40 Absorption heat pumps - district heating
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MWheat) (excluding drive energy) | 12 | 12 | 12 | 12 | 12 | 20 | 12 | 30 | A | 13
| Total efficiency, net (%), name plate | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Total efficiency , net (%), annual average | 170 | 171 | 173 | 175 | 170 | 180 | 170 | 180 | B | 4
| Electricity consumption for pumps etc. (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 3 | E | 3
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | C
| Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 15 | 30 | 15 | 30 |  | 3
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7
| Space requirement (1000m2 per MW) | 0.01 | 0.01 | 0.005 | 0.005 | 0.005 | 0.01 | 0.005 | 0.01
Regulation ability
| Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Minimum load (% of full load) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 2 | 0.25 | 2
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data (in 2015€)
| Nominal investment (M€ per MWheat excluding drive energy) | 0.6 | 0.564 | 0.5076 | 0.45684 | 0.4 | 0.8 | 0.4 | 0.8 | A | 3
| - of which equipment (%) | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
| - of which installation (%) | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
| Fixed O&M (€/MWheat/year) | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 3000 |  | 3
| Variable O&M (€/MWhheat) | 0.9 | 0.982 | 1.2538 | 1.4284 | 1 | 2.5 | 1.4 | 0.3
| - of which is electricity costs (€/MWhheat) | 0.6 | 0.7 | 1 | 1.2 | 0.7 | 2.1 | 1.2 | 0 | E
| - of which is other O&M costs (€/MWhheat) | 0.3 | 0.282 | 0.2538 | 0.22842 | 0.3 | 0.4 | 0.2 | 0.3 |  | 3
Technology specific data
References:
3 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014, see http://www.planenergi.dk/varmepumper/
4 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, 2013
13 | Scandinavian Energy Group, 2015
Notes:
A | The heat pump itself only represents a small part of the total investment. Depending on size the heat pump typically represents 0.2 M€ per. MW heating (excluding drive energy).
B | The heat is assumed delivered at 80 °C in 2015 and 60 °C in 2050
C | May vary depending on availability of heat source
D | May vary depending on specific type, heat source etc.
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 41 Electric Boilers
| Technology | 41 Heat only generation tech (boilers, heat pumps, geothermal) Electric boilers, 400 or 690 V, 0.06-5 MW; 10 or 15 kV, >10 MW
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 5 |  |  |  | 1 | 25 | 1 | 25
| Total efficiency, net (%), name plate | 98 | 99 | 99 | 99 | 98 | 99 | 99 | 99 |  | 1
| Total efficiency , net (%), annual average | 98 | 99 | 99 | 99 | 98 | 99 | 99 | 99 |  | 1
| Electricity consumption for pumps etc. (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1
| Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 | E | 1
| Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | E | 1
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 1
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation ability
| Primary regulation (% per 30 seconds) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 1
| Secondary regulation (% per minute) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 1
| Minimum load (% of full load) | 5 | [8 empty] | 1
| Warm start-up time (hours) | 0.008 | [8 empty] | 2
| Cold start-up time (hours) | 0.08 | [8 empty] | 2
Environment
| SO2 (g per GJ fuel) | Cf. the utilized electricity
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data (in 2015€)
| Nominal investment (M€ per MW), 400/690 V; 1-5 MW | 0.15 | 0.15 | 0.14 | 0.13 | 0.1 | 0.25 | 0.1 | 0.25 | A | 1
| - of which equipment | 0.12 | 0.11703 | 0.11131 | 0.10069 | 0.08 | 0.2 | 0.08 | 0.2 | B | 1
| - of which installation | 0.03 | 0.029257 | 0.027827 | 0.025173 | 0.02 | 0.05 | 0.02 | 0.05 | D | 1
| Nominal investment (M€ per MW); 10/15 kV; >10 MW | 0.07 | 0.07 | 0.06 | 0.06 | 0.02 | 0.17 | 0.02 | 0.17 | A | 1
| - of which equipment | 0.06 | 0.058515 | 0.05 | 0.050345 | 0.02 | 0.14 | 0.02 | 0.14 | C | 1
| - of which installation | 0.01 | 0.0097525 | 0.0092757 | 0.0083909 | 0 | 0.03 | 0 | 0.03 | D | 1
| Fixed O&M (€/MW/year) | 1100 | 1070 | 1020 | 920 | 1000 | 1100 | 900 | 1000 | A | 1
| Variable O&M (€/MWh) | 0.8 | 0.9 | 1 | 1 | 0.5 | 0.9 | 0.5 | 1 |  | 1
| - of which is electricity costs (€/MWh) | 0.3 | 0.3 | 0.5 | 0.6 | 0.1 | 0.3 | 0.1 | 0.6 | F
| - of which is other O&M costs (€/MWh) | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.3 | 0.5 | A | 1
Technology specific data
| Startup costs (€/MW/startup) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1
References:
1 | Tjæreborg Industri, 2016
2 | Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf
Notes:
A | The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
B | The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
C | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
D | The installation costs include costs for electrical integration & grid connection fees.
E | The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
F | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 44 Natural Gas DH Only
| Technology | 44 District heating boiler, natural gas fired
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 0.5 -10
| Total efficiency, net (%), nominel load | 105 | 105 | 106 | 106 | 95 | 107 | 96 | 108 | A | 1, 2, 3
| Total efficiency , net (%), annual average | 103 | 103 | 104 | 104 | 93 | 105 | 94 | 106 | B | 1, 3
| Electricity consumption for pumps etc. (% of heat gen) | 0.15 | 0.14 | 0.12 | 0.1 | 0.13 | 0.2 | 0.08 | 0.15 | L | 1
| Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3
| Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 | F | 3
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | >25 | 25 | >25 | K | 3
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 | F | 9
| Space requirement (1000m2 per MJ/s) | 0.005 | 0.005 | 0.005 | 0.005 | 0.003 | 0.01 | 0.003 | 0,01 | E | 2
Plant Dynamic Capabilities
| Primary regulation (% per 30 seconds) | - | - | - | - | - | - | - | - | C
| Secondary regulation (% per minute) | - | - | - | - | - | - | - | - | C
| Minimum load (% of full load) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 9
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.15 | 0,08 | 0.15 | D | 9
| Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 | D | 9
Environment
| SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0 | 0.3 | H | 1
| NOX (g per GJ fuel) | 10 | 9 | 7 | 6 | 8 | 60 | 5 | 30 |  | 1, 2
| CH4 (g per GJ fuel) | 3 | 3 | 2 | 2 | 2 | 6 | 2 | 6 |  | 1, 2
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | NA | NA | NA | NA | I | 7
Financial data (in 2015€)
| Nominal investment (M€ per MJ/s) | 0.06 | 0.06 | 0.05 | 0.05 | 0.035 | 0.25 | 0.035 | 0.25 | J | 2, 3
| - of which equipment | 0.04 | 0.04 | 0.03 | 0.03 | 0.025 | 0.15 | 0.025 | 0.15 |  | 2, 3
| - of which installation | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.1 | 0,01 | 0.1 |  | 2, 3
| Fixed O&M (€/MJ/s/year) | 2000 | 1950 | 1900 | 1700 | 1000 | 2500 | 1000 | 2500 | F
| Variable O&M (€/MWh) | 1.1 | 1.1 | 1 | 1 | 0.6 | 2.1 | 0.6 | 2.2
| - of which is electricity costs (€/MWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | L
| - of which is other O&M costs (€/MWh) | 1 | 1 | 0.9 | 0.9 | 0.5 | 2 | 0.5 | 2 |  | 8, 9
Technology specific data
References:
1 | DGC efficiency and emission test reports from district heating boilers, 2014
2 | Burner and boiler manufacturer informations, 2015
3 | Danish District Heating Association, data from a 2012 survey for the report
7 | National Environmental Research Institute, Denmark 2009
8 | Elsam/Elkraft update "Teknologidata for el- og varmeproduktionsanlæg", 1997
9 | DGC calculations, estimates
Notes:
A | Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
B | Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
C | Not Relevant for heat-only technologies
D | Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
E | Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
F | DGC Estimate
G | Ultra Low NOx burners can reach a level of 5 g/GJ
H | Fuel dependent , not tecchnology dependent
I | No data available
J | The average numbers are for a 2- 3 MW boiler installation
K | Technical lifetime often exceeds 25 years
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 45.1.a Geothermal DH, 1200m, E
| Technology | Geothermal heat-only plant with electric heat pump, 1200m. DH temp. 80/40°C
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 11.4183 | 11.3715 | 11.3269 | 11.2435 | 11.2045 | 19.28 | 4.28 | 19.28 | 4.28 | I, A | 1, 2
| Total efficiency, net (%) annual average | 460.2732 | 467.1895 | 474.044 | 487.5706 | 494.2443 | 530.853 | 405.9023 | 575.531 | 431.5527 | AG
| Auxiliary electricity consumption (% of heat gen) | 4.121% | 4.138% | 4.154% | 4.185% | 4.199% | 1.647% | 7.423% | 1.647% | 7.423% | B | 2, 3, 4
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 5
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time (years) | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement (1000m2 per MW) | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | H
| Secondary regulation (% per minute) | [9 empty] | H
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H | 2; 5
Warm start-up time (hours)
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Nominal investment (M€ per MW) | 2.7138 | 2.6536 | 2.4982 | 2.438 | 2.3777 | 1.6306 | 4.0559 | 1.5185 | 3.7595 | C,K | 2, 4, 7
| - of which is equipment excluding heat pump | 1.5359 | 1.4907 | 1.4455 | 1.4004 | 1.3552 | 0.86124 | 2.3131 | 0.78295 | 2.1028 |  | 2, 4
| - of which is installation | 0.51196 | 0.4969 | 0.48184 | 0.46678 | 0.45173 | 0.29578 | 0.79439 | 0.26889 | 0.72218 |  | 2, 4
| - of which is heat pump including its installation | 0.66597 | 0.66597 | 0.57083 | 0.57083 | 0.57083 | 0.47358 | 0.94844 | 0.46662 | 0.93451 | J,K
| Fixed O&M (€/MW/year) | 22600 | 21900 | 21300 | 20600 | 19900 | 21900 | 21900 | 19900 | 19900 | E,J | 1, 3; 2
| Variable O&M (€/MWh) | 5.6965 | 5.7127 | 6.1276 | 6.2523 | 5.8641 | 5.0893 | 6.0931 | 5.7517 | 6.6435 | FJ | 2
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| - of which is other O&M costs (€/MWh) | 5.6965 | 5.7127 | 6.1276 | 6.2523 | 5.8641 | 5.0893 | 6.0931 | 5.7517 | 6.6435 | F
Technology specific data
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | L, N | 1
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Depth of geothermal well (m) | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
| Heat generation from geothermal heat (MJ/s) | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | I,A,L,N | 1
| Heat generation from heat pumps (MJ/s) | 2.0103 | 1.9635 | 1.9189 | 1.8355 | 1.7965 | 3.3143 | 0.73674 | 3.0323 | 0.67407 | A | 1
| Total efficiency, heat pump COP (%) annual average | 568 | 579.1373 | 590.2745 | 612.549 | 623.6863 | 579.1373 | 579.1373 | 623.6863 | 623.6863 | A, N
Notes:
A | No part of the geothermal heat is transferred directly to DH water, all is used as source for the heat pump Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B | The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C | Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 M€/site (based on 1;4 and Ref. [10]). A well cost of 1800 €/m is assumed.
D | This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E | Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F | Include maintenance of filters and wells (chemical treatment)
G | Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H | A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I | Uncertainty does not consider the risk of not finding a suitable reservoir.
J | Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K | The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L | Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M | Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N | Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
References:
1 | PlanEnergi, GEUS, 2019
2 | Data collected from European energy projects
3 | Thisted District Heating, Personal Communication
4 | Energy Technology Data Catalogue, June 2019
5 | European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6 | Technology Catalogue, Ch. 40 (2020)
7 | Input from APMH March 2020 (drilling costs variations with depth)

## 45.1.b Geothermal DH, 2000m, E
| Technology | Geothermal heat-only plant with electric heat pump, 2000m. DH temperature 80/40°C
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 13.1357 | 13.1131 | 13.0916 | 13.0514 | 13.0327 | 22.18 | 4.93 | 22.18 | 4.93 | I, A | 1, 2
| Total efficiency, net (%) annual average | 844.3695 | 855.3276 | 866.0795 | 886.9878 | 897.155 | 1124.2643 | 650.4038 | 1207.5398 | 677.4038 | AG
| Auxiliary electricity consumption (% of heat gen) | 6.501% | 6.513% | 6.523% | 6.543% | 6.553% | 3.711% | 9.27% | 3.711% | 9.27% | B | 2, 3; 4
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 5
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time (years) | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement (1000m2 per MW) | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | H
| Secondary regulation (% per minute) | [9 empty] | H
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H | 2; 5
Warm start-up time (hours)
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Nominal investment (M€ per MW) | 2.8828 | 2.8044 | 2.6916 | 2.6129 | 2.5347 | 1.7018 | 4.1443 | 1.5598 | 3.793 | C,K | 2, 4, 7
| - of which is equipment excluding heat pump | 1.9805 | 1.9223 | 1.864 | 1.8058 | 1.7475 | 1.1384 | 2.8284 | 1.0349 | 2.5713 |  | 2, 4
| - of which is installation | 0.66017 | 0.64075 | 0.62133 | 0.60192 | 0.5825 | 0.39097 | 0.97138 | 0.35543 | 0.88307 |  | 2, 4
| - of which is heat pump including its installation | 0.24212 | 0.24139 | 0.20631 | 0.20519 | 0.20466 | 0.17241 | 0.34449 | 0.16949 | 0.33866 | J,K
| Fixed O&M (€/MW/year) | 23900 | 23200 | 22500 | 21800 | 21100 | 23200 | 23200 | 21100 | 21100 | E,J | 1, 3; 2
| Variable O&M (€/MWh) | 4.5876 | 4.5182 | 4.5926 | 4.5594 | 4.3437 | 4.2909 | 4.6489 | 4.3081 | 4.6244 | FJ | 2
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| - of which is other O&M costs (€/MWh) | 4.5876 | 4.5182 | 4.5926 | 4.5594 | 4.3437 | 4.2909 | 4.6489 | 4.3081 | 4.6244 | F
Technology specific data
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | L, N | 1
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Depth of geothermal well (m) | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
| Heat generation from geothermal heat (MJ/s) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | I,A,L,N | 1
| Heat generation from heat pumps (MJ/s) | 0.94568 | 0.92311 | 0.90159 | 0.86143 | 0.84267 | 1.5612 | 0.34669 | 1.4252 | 0.31648 | A | 1
| Total efficiency, heat pump COP (%) annual average | 505 | 514.902 | 524.8039 | 544.6078 | 554.5098 | 514.902 | 514.902 | 554.5098 | 554.5098 | A, N
Notes:
A | Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B | The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C | Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 M€/site (based on 1;4 and Ref. [10]). A well cost of 2000 €/m is assumed.
D | This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E | Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F | Include maintenance of filters and wells (chemical treatment)
G | Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H | A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I | Uncertainty does not consider the risk of not finding a suitable reservoir.
J | Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K | The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L | Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M | Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N | Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
References:
1 | PlanEnergi, GEUS, 2019
2 | Data collected from European energy projects
3 | Thisted District Heating, Personal Communication
4 | Energy Technology Data Catalogue, June 2019
5 | European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6 | Technology Catalogue, Ch. 40 (2020)
7 | Input from APMH March 2020 (drilling costs variations with depth)

## 45.2.a Geothermal DH, 1200m, A
| Technology | Geothermal heat-only plant with absorption heat pump, 1200m. DH temperature 80/40°C
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 22.6587 | 22.4747 | 22.2957 | 22.1215 | 21.952 | 38.56 | 8.56 | 38.56 | 8.56 | I, A | 1, 2
| Total efficiency, net (%) annual average | 165.1364 | 166.0219 | 166.9066 | 167.7904 | 168.6734 | 172.3494 | 164.4355 | 179.4245 | 170.8537 | AG
| Auxiliary electricity consumption (% of heat gen) | 2.076% | 2.093% | 2.11% | 2.127% | 2.143% | 0.8237% | 3.701% | 0.8237% | 3.701% | B | 2, 3, 4
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 5
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time (years) | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement (1000m2 per MW) | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | H
| Secondary regulation (% per minute) | [9 empty] | H
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H | 2; 5
Warm start-up time (hours)
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Nominal investment (M€ per MW) | 1.2645 | 1.2273 | 1.1901 | 1.1529 | 1.1157 | 0.7379 | 1.8827 | 0.68579 | 1.7415 | C,K | 2, 4, 7
| - of which is equipment excluding heat pump | 0.77396 | 0.7512 | 0.72843 | 0.70567 | 0.68291 | 0.42665 | 1.1565 | 0.38786 | 1.0514 |  | 2, 4
| - of which is installation | 0.25799 | 0.2504 | 0.24281 | 0.23522 | 0.22764 | 0.14652 | 0.3972 | 0.1332 | 0.36109 |  | 2, 4
| - of which is heat pump including its installation | 0.23251 | 0.22395 | 0.2152 | 0.20626 | 0.19714 | 0.16473 | 0.32897 | 0.16473 | 0.32897 | J,K
| Fixed O&M (€/MW/year) | 11100 | 10800 | 10500 | 10100 | 9800 | 10800 | 10800 | 9800 | 9800 | E,J | 1, 3; 2
| Variable O&M (€/MWh) | 2.0764 | 2.1069 | 2.1375 | 2.1255 | 2.1129 | 2.0725 | 2.0694 | 2.0301 | 2.027 | FJ | 2
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| - of which is other O&M costs (€/MWh) | 2.0764 | 2.1069 | 2.1375 | 2.1255 | 2.1129 | 2.0725 | 2.0694 | 2.0301 | 2.027 | F
Technology specific data
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | L, N | 1
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L, N | 1
| Depth of geothermal well (m) | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
| Heat generation from geothermal heat (MJ/s) | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.52 | 15.88 | 3.52 | I,A,L,N | 1
| Heat generation from heat pumps (MJ/s) | 13.2507 | 13.0667 | 12.8877 | 12.7135 | 12.544 | 22.0556 | 4.8889 | 21.1733 | 4.6933 | A | 1
| Total efficiency, heat pump COP (%) annual average | 171 | 172 | 173 | 174 | 175 | 172 | 172 | 175 | 175 | A, N
Notes:
A | No part of the geothermal heat is transferred directly to DH water. 100% heat source for the heat pump. Heat pump according to Ch. 40.
B | The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C | Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 M€/site (based on 1;4 and Ref. [10]). A well cost of 1800 €/m is assumed.
D | This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E | Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F | Include maintenance of filters and wells (chemical treatment)
G | Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H | A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I | Uncertainty does not consider the risk of not finding a suitable reservoir.
J | Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K | The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L | Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M | Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N | Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
References:
1 | PlanEnergi, GEUS, 2019
2 | Data collected from European energy projects
3 | Thisted District Heating, Personal Communication
4 | Energy Technology Data Catalogue, June 2019
5 | European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6 | Technology Catalogue, Ch. 40 (2020)
7 | Input from APMH March 2020 (drilling costs variations with depth)

## 45.2.b Geothermal DH, 2000m, A
| Technology | Geothermal heat-only plant with absorption heat pump, 2000m. DH temperature 80/40°C
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 17.5844 | 17.5094 | 17.4366 | 17.3657 | 17.2967 | 29.84 | 6.62 | 29.84 | 6.62 | I, A | 1, 2
| Total efficiency, net (%) annual average | 292.8597 | 295.2965 | 297.7265 | 300.1495 | 302.5656 | 316.8581 | 274.7898 | 329.46 | 284.2176 | AG
| Auxiliary electricity consumption (% of heat gen) | 4.857% | 4.877% | 4.898% | 4.918% | 4.937% | 2.761% | 6.903% | 2.761% | 6.903% | B | 2, 3; 4
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 5
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time (years) | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement (1000m2 per MW) | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | H
| Secondary regulation (% per minute) | [9 empty] | H
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H | 2; 5
Warm start-up time (hours)
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Nominal investment (M€ per MW) | 2.0946 | 2.033 | 1.9714 | 1.9098 | 1.8482 | 1.258 | 2.8655 | 1.1436 | 2.605 | C,K | 2, 4, 7
| - of which is equipment excluding heat pump | 1.4795 | 1.4359 | 1.3924 | 1.3489 | 1.3054 | 0.81838 | 2.1064 | 0.74398 | 1.9149 |  | 2, 4
| - of which is installation | 0.49315 | 0.47865 | 0.46414 | 0.44964 | 0.43513 | 0.28106 | 0.7234 | 0.25551 | 0.65763 |  | 2, 4
| - of which is heat pump including its installation | 0.12197 | 0.11838 | 0.1148 | 0.11121 | 0.10762 | 0.15855 | 0.035733 | 0.14413 | 0.032485 | J,K
| Fixed O&M (€/MW/year) | 17300 | 16800 | 16300 | 15800 | 15300 | 16800 | 16800 | 15300 | 15300 | E,J | 1, 3; 2
| Variable O&M (€/MWh) | 2.993 | 2.9566 | 2.9196 | 2.8599 | 2.7994 | 2.9301 | 2.93 | 2.7407 | 2.7407 | FJ | 2
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| - of which is other O&M costs (€/MWh) | 2.993 | 2.9566 | 2.9196 | 2.8599 | 2.7994 | 2.9301 | 2.93 | 2.7407 | 2.7407 | F
Technology specific data
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | L, N | 1
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L, N | 1
| Depth of geothermal well (m) | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
| Heat generation from geothermal heat (MJ/s) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.6 | 4.57 | 20.6 | 4.57 | I,A,L,N | 1
| Heat generation from heat pumps (MJ/s) | 5.3944 | 5.3194 | 5.2466 | 5.1757 | 5.1067 | 9.0055 | 1.9978 | 8.6452 | 1.9179 | A | 1
| Total efficiency, heat pump COP (%) annual average | 171 | 172 | 173 | 174 | 175 | 172 | 172 | 175 | 175 | A, N
Notes:
A | Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump according to Ch. 40.
B | The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C | Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 M€/site (based on 1;4 and Ref. [10]). A well cost of 1900 €/m is assumed.
D | This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E | Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F | Include maintenance of filters and wells (chemical treatment)
G | Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H | A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I | Uncertainty does not consider the risk of not finding a suitable reservoir.
J | Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K | The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L | Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M | Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N | Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
References:
1 | PlanEnergi, GEUS, 2019
2 | Data collected from European energy projects
3 | Thisted District Heating, Personal Communication
4 | Energy Technology Data Catalogue, June 2019
5 | European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6 | Technology Catalogue, Ch. 40 (2020)
7 | Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.a Geoth. DH, 1200m, E (LT)
| Technology | Geothermal heat-only plant with electric heat pump, 1200m. DH temperature 70/35°C
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 10.9321 | 10.8971 | 10.8636 | 10.8011 | 10.7718 | 18.45 | 4.1 | 18.45 | 4.1 | I, A | 1, 2
| Total efficiency, net (%) annual average | 548.0948 | 556.0987 | 564.0148 | 579.5894 | 587.2507 | 651.6826 | 467.8022 | 704.2911 | 494.316 | AG
| Auxiliary electricity consumption (% of heat gen) | 4.304% | 4.318% | 4.331% | 4.356% | 4.368% | 1.721% | 7.749% | 1.721% | 7.749% | B | 2, 3, 4
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 5
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time (years) | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement (1000m2 per MW) | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | H
| Secondary regulation (% per minute) | [9 empty] | H
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H | 2; 5
Warm start-up time (hours)
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Nominal investment (M€ per MW) | 2.6988 | 2.6355 | 2.4924 | 2.4289 | 2.3658 | 1.5964 | 4.041 | 1.482 | 3.7352 | C,K | 2, 4, 7
| - of which is equipment excluding heat pump | 1.6042 | 1.557 | 1.5098 | 1.4626 | 1.4155 | 0.89168 | 2.4146 | 0.81062 | 2.1951 |  | 2, 4
| - of which is installation | 0.53473 | 0.519 | 0.50327 | 0.48754 | 0.47182 | 0.30623 | 0.82927 | 0.27839 | 0.75388 |  | 2, 4
| - of which is heat pump including its installation | 0.55985 | 0.55951 | 0.4793 | 0.47877 | 0.47852 | 0.39844 | 0.79713 | 0.39299 | 0.78623 | J,K
| Fixed O&M (€/MW/year) | 23200 | 22500 | 21800 | 21100 | 20500 | 22500 | 22500 | 20500 | 20500 | E,J | 1, 3; 2
| Variable O&M (€/MWh) | 5.4607 | 5.4529 | 5.7799 | 5.8613 | 5.5142 | 4.933 | 5.7724 | 5.4336 | 6.1791 | FJ | 2
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| - of which is other O&M costs (€/MWh) | 5.4607 | 5.4529 | 5.7799 | 5.8613 | 5.5142 | 4.933 | 5.7724 | 5.4336 | 6.1791 | F
Technology specific data
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | L, N | 1
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L, N | 1
| Depth of geothermal well (m) | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
| Heat generation from geothermal heat (MJ/s) | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | I,A,L,N | 1
| Heat generation from heat pumps (MJ/s) | 1.5241 | 1.4891 | 1.4556 | 1.3931 | 1.3638 | 2.5135 | 0.55874 | 2.3021 | 0.51173 | A | 1
| Total efficiency, heat pump COP (%) annual average | 603 | 614.8235 | 626.6471 | 650.2941 | 662.1176 | 614.8235 | 614.8235 | 662.1176 | 662.1176 | A, N
Notes:
A | Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 19% of geothermal heat can be exchanged directly, leaving 79 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B | The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C | Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 M€/site (based on 1;4 and Ref. [10]). A well cost of 1900 €/m is assumed.
D | This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E | Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F | Include maintenance of filters and wells (chemical treatment)
G | Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H | A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I | Uncertainty does not consider the risk of not finding a suitable reservoir.
J | Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K | The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L | Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M | Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N | Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
References:
1 | PlanEnergi, GEUS, 2019
2 | Data collected from European energy projects
3 | Thisted District Heating, Personal Communication
4 | Energy Technology Data Catalogue, June 2019
5 | European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6 | Technology Catalogue, Ch. 40 (2020)
7 | Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.b Geoth DH, 2000m, E (LT)
| Technology | Geothermal heat-only plant with electric heat pump, 2000m. DH temperature 70/35 °C
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MW) | 12.6523 | 12.6417 | 12.6315 | 12.6124 | 12.6035 | 21.35 | 4.73 | 21.35 | 4.73 | I, A | 1, 2
| Total efficiency, net (%) annual average | 1185.4183 | 1196.3833 | 1207.0566 | 1227.574 | 1237.4392 | 1829.6967 | 816.9071 | 1936.7394 | 837.6245 | AG
| Auxiliary electricity consumption (% of heat gen) | 6.75% | 6.755% | 6.761% | 6.771% | 6.776% | 3.856% | 9.662% | 3.856% | 9.662% | B | 2, 3; 4
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 5
| Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime (years) | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time (years) | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement (1000m2 per MW) | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
| Primary regulation (% per 30 seconds) | [9 empty] | H
| Secondary regulation (% per minute) | [9 empty] | H
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H | 2; 5
Warm start-up time (hours)
| Cold start-up time (hours) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Nominal investment (M€ per MW) | 2.8756 | 2.7945 | 2.6945 | 2.6131 | 2.5322 | 1.6322 | 4.152 | 1.4911 | 3.7891 | C,K | 2, 4, 7
| - of which is equipment excluding heat pump | 2.0562 | 1.9957 | 1.9352 | 1.8747 | 1.8143 | 1.1438 | 2.948 | 1.0398 | 2.68 |  | 2, 4
| - of which is installation | 0.68539 | 0.66523 | 0.64507 | 0.62491 | 0.60475 | 0.39283 | 1.0125 | 0.35711 | 0.92041 |  | 2, 4
| - of which is heat pump including its installation | 0.13408 | 0.13363 | 0.11417 | 0.11348 | 0.11316 | 0.095568 | 0.19158 | 0.094131 | 0.1887 | J,K
| Fixed O&M (€/MW/year) | 24500 | 23800 | 23100 | 22300 | 21600 | 23800 | 23800 | 21600 | 21600 | E,J | 1, 3; 2
| Variable O&M (€/MWh) | 4.3402 | 4.2484 | 4.2362 | 4.164 | 3.9913 | 4.124 | 4.335 | 3.976 | 4.1637 | FJ | 2
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| - of which is other O&M costs (€/MWh) | 4.3402 | 4.2484 | 4.2362 | 4.164 | 3.9913 | 4.124 | 4.335 | 3.976 | 4.1637 | F
Technology specific data
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | L, N | 1
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L, N | 1
| Depth of geothermal well (m) | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
| Heat generation from geothermal heat (MJ/s) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | I,A,L,N | 1
| Heat generation from heat pumps (MJ/s) | 0.45733 | 0.44666 | 0.43647 | 0.41743 | 0.40852 | 0.75526 | 0.16771 | 0.69077 | 0.15339 | A | 1
| Total efficiency, heat pump COP (%) annual average | 557 | 567.9216 | 578.8431 | 600.6863 | 611.6078 | 567.9216 | 567.9216 | 611.6078 | 611.6078 | A, N
Notes:
A | Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 83% of geothermal heat can be exchanged directly, leaving 17 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B | The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C | Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 M€/site (based on 1;4 and Ref. [10]). A well cost of 1900 €/m is assumed.
D | This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary.
E | Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F | Include maintenance of filters and wells (chemical treatment)
G | Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H | A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I | Uncertainty does not consider the risk of not finding a suitable reservoir.
J | Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K | The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L | Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M | Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N | Temperature of geothermal heat is 80/40 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
References:
1 | PlanEnergi, GEUS, 2019
2 | Data collected from European energy projects
3 | Thisted District Heating, Personal Communication
4 | Energy Technology Data Catalogue, June 2019
5 | European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6 | Technology Catalogue, Ch. 40 (2020)
7 | Input from APMH March 2020 (drilling costs variations with depth)

## 46 Solar District Heating
| Technology | Solar District Heating
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical plant size (collector area), m2 | 10000 | 13000 | 21000 | 55000 | 10000 | 20000 | 10000 | 100000 | L
| Collector input, kWh/m2/year | 1046 | 1046 | 1046 | 1046 | 1013 | 1079 | 1013 | 1079 | Q
| Collector output, kWh/m2/year | 450 | 472.955 | 497.08 | 522.436 | 450 | 495.91 | 497.08 | 547.792 | A | 4
| Total efficiency , net (%), annual average | 43% | 45% | 48% | 49.95% | 42% | 49% | 46% | 54% | P
| Auxilary electricity consumption (share of heat gen.) | 0.3% | 0.3% | 0.3% | 0.3% | 0.2% | 0.4% | 0.2% | 0.4%
| Forced outage (%) | 0.5% | 0.5% | 0.5% | 0.5% | 0% | 1% | 0% | 1% | K
| Technical lifetime (years) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | I | 17
| Construction time (years) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Space requirement (1000m2 per MWh/year) | 6.7 | 6.3 | 6 | 5.7 | 6 | 6.7 | 5.5 | 6 | J
Regulation ability
| Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | F
| Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Investment cost of total solar systems excluding diurnal heat storage, €/MWhoutput/year | 428.8889 | 395.3865 | 362.1148 | 325.3987 | 371.0351 | 422.2222 | 292.0817 | 362.1148 | C, H, N
| - of which is equipment | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | O
| - of which is installation | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | O
| Investment cost of diurnal heat storage, €/MWhoutput/year | 60 | 57 | 54 | 52 | 41 | 75 | 37 | 68 | D, M
| Total investment cost of total solar system including diurnal heat storage, €/MWhoutput/year | 488.8889 | 452.3865 | 416.1148 | 377.3987 | 412.0351 | 497.2222 | 329.0817 | 430.1148 | E
| Fixed O&M €/(MWhoutput/year)/year | 0.09 | 0.09 | 0.08 | 0.08 | 0.08 | 0.1 | 0.07 | 0.08 | B
| Variable O&M €/MWhoutput | 0.19 | 0.21 | 0.3 | 0.35 | 0.14 | 0.28 | 0.23 | 0.47
| - of which is electricity costs, €/MWhoutput | 0.19 | 0.21 | 0.3 | 0.35 | 0.14 | 0.28 | 0.23 | 0.47
| - of which is other O&M costs, €/MWhoutput | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Investment cost of total solar systems excluding diurnal heat storage, €/m2 (collector area) | 193 | 187 | 180 | 170 | 184 | 190 | 160 | 180 | G, H, N | 16
| Fixed O&M, €/m2/year (collector area) | 0.0405 | 0.042566 | 0.039766 | 0.041795 | 0.039673 | 0.045 | 0.038345 | 0.039766 | B
Notes
A | The yield is weather dependent and very site-specific, depending much on the temperatures of the district heating network. The quoted yield the average measured output from 40 Danish solar heating plants for 2015.
B | Estimate is 0,2 €/MWh heat output in 2015, excluding electricity consumption.
C | Applying the formula 250,000 € + 167 €/m2 solar panel collector for plants <50.000m2, cf. figures from Note G.
D | Including a diurnal storage is mandatory, 0.2 m3/m2 being a typical average storage size. This figure can vary, dependent on the local conditions and desired solar fraction.
E | Can be combined with seasonal storage, cf. corresponding chapter.
F | Solar thermal plants can be regulated by varying the flow of the heat transfer fluid. The regulation ability is limited by the available heat demand in the heat sink (incl. available storage capacity) and solar radiation.
G | 2015-Prices of different plant sizes (Ref. 1):
| Size | m2 | 5000 | 10000 | 20000 | 50000 | 100000
| Price pr. m2 | €/m2 | 216 | 193.3333 | 180 | 174.6667 | 170
| Total price | M€ | 1.08 | 1.9333 | 3.6 | 8.7333 | 17
H | Prices include leveling of ground, laying of district heating pipelines in the ground inkl. 50 m of transmission pipeline to the district heating plant, heat exchanger connected to solar panel field and installed with collection tank and expansion with flanges to secondary side, control and electricity works, design and project management, start-up regulation and documentation.
I | The lifetime is minimum 25-30 years, proven in actual plants still in operation. Critical component is the teflon foil, not the material itself, but the application method. The pipes have been improved, designed for the relatively large number of temperature variations, compared to normal district heating pipelines. The fluid is well managed.
J | Space requirement is approximately 3 m2 for each m2 gross collector area. No development of this parameter is expected, since the main reason is to avoid the shadow effect. Minor optimization of the sides of the panels may be obtained, increasing the ratio of aperture/gross area. Other types of solar collectors such as vacuum and CSP (concentrated solar power) may have lower space requirement.
K | The forced outage is very small, therefore in practice close to 0 %. The modular construction makes it possible to maintain sections of the panels. Outage of critical components such as the heat exchanger is very limited.
L | The average plant size increases, but with large variations since both small plants and increasingly larger plants are installed. A 5 % annual increase of the average size is assumed. The plant size is rather dependent on the heat demand in the district heating grid, it is connected to. The collector area is, cf. international standards, stated as gross area.
M | Estimate of cost of tank storage (diurnal storage) is 135 €/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
N | Considering a reduction in prices for 2015-2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
O | The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, ground works (7%), design, permits, unforeseen (6%). Total for equipment is 85% and for installation is 15% (design, permits, unforeseen, ground works, control and start up), but including accumulation tank and a transmission pipeline.
P | Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
Q | The solar radiation on the horizontal surface.
R | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
References
4 | Solar Heating plants in Denmark, Simon Furbo, Bengt Perers and Federico Bava, Department of Civil Engineering, Technical University of Denmark. The projected outputs for 2020, 2030 and 2050 are not from this reference.
16 | Arcon-Sunmark, personal communication. The projected costs are not from this reference, but estimated based on two components; the lower specific costs of larger plants in 2015 and increased competition among suppliers and more efficient production of solar panels.
17 | "Life expectancy of solar collectors in solar district heating systems", Department of Civil Engineering, Technical University of Denmark, 2009.

## 50 Diesel engine farm
| Technology | Diesel engine farm
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 18 | [7 empty] | A, B
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | 37 | 37 | 37 | 37 | 35 | 39 |  |  |  | 1, 2, 3
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 35 | 35 | 35 | 35 | 33 | 37 |  |  | C
| Cb coefficient (50oC/100oC) | - | - | - | -
| Cv coefficient (50oC/100oC) | - | - | - | -
| Forced outage (%) | 0.9 | 0.9 | 0.9 | 0.9 | [5 empty] | 4
| Planned outage (days per year) | 1.2 | 1.2 | 1.2 | 1.2 |  |  |  |  | D, E | 5
| Technical lifetime (years) | 25 | 25 | 25 | 25
| Construction time (years) | 1 | 1 | 1 | 1 | [5 empty] | 6
Regulation ability
| Primary regulation (% of full load per 30 seconds) | 100 | 100 | 100 | 100 |  |  |  |  | F | 6
| Secondary regulation (% of full load per minute) | 100 | 100 | 100 | 100 |  |  |  |  | F | 6
| Minimum load (% of full load) | 1 | 1 | 1 | 1 |  |  |  |  | G
| Warm start-up time (minutes) | 1 | 1 | 1 | 1 | 0.5 | 2 |  |  | H | 6, 7
| Cold start-up time (minutes) | 5 | 5 | 5 | 5 | 3 | 10 |  |  | H | 6
Environment
| SO2 (g per GJ fuel) | 23 | 23 | 23 | 23 |  |  |  |  | I | 8
| NOX (g per GJ fuel) | 942 | 942 | 942 | 942 | [5 empty] | 8
| CH4 (g per GJ fuel) | 24 | 24 | 24 | 24 | [5 empty] | 8
| N2O (g per GJ fuel) | 2.1 | 2.1 | 2.1 | 2.1 | [5 empty] | 8
| Particles (g per GJ fuel) | 5 | 5 | 5 | 5 | [5 empty] | 8
Financial data
| Specific investment (M€/MW) | 0.35 | 0.343 | 0.343 | 0.336 | 0.2744 | 0.4116 | 0.2352 | 0.4368 | M, N, O | 1, 6, 9, 10
| - of which equipment | 0.2275 | 0.22295 | 0.22295 | 0.2184 |  |  |  |  | L
| - of which installation | 0.1225 | 0.12005 | 0.12005 | 0.1176 |  |  |  |  | L
| Fixed O&M (€/MW/year) | 8800 | 8800 | 8448 | 8096 |  |  |  |  | D, P, Q | 6
| Variable O&M (€/MWh) | 6 | 6 | 6 | 6 | 2.6 | 8.5 | 2.6 | 8.5 |  | 11,12,13
| Startup cost (€/MW/startup) | - | - | - | - |  |  |  |  | R | 6, 11
Technology specific data
Notes:
A | The range of generating capacity for a plant based on this technology is tipically 10-300 MW. Most of UK projects are in the range 18.5-20 MW. Emission requirements for plants with 18.5 MW and above are regulated by the Danish EPA and it is as of yet undetermined whether and exemption due to low operating hours can be obtained.
B | Engine size is normally in the range 400 kW - 2 MW. Here considered 10 engines of 1.8 MW.
C | Assuming the same efficiency reduction from nameplate to annual average compared to Gas Engines in the main technology catalogue.
D | The routine checks and oil change varies depending on the size. Smaller engines (400 kW) needs it every 250 h, while larger engines (2 MW) needs it every 1000h. Here assumed larger engines. Fixed O&M costs can increase for smaller sizes.
E | 1.5h monthly maintenance for general checks, 4h semiannual, 2h annually, 2h biannually, 6h every 6 years.
F | 50% of the output capacity can be reach within 15 seconds and after 20 seconds the total power output can be provided.
G | Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level.
H | The startup time of the single engine is around 30 seconds. The syncronization of all the machines and the connection to the grid might increase the startup time to 3-10 minutes.
I | Values related to the use of gas oil.
L | Split based on the Engine technology in the main technology catalogue
M | Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N | The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.282-0.456 M€/MW.
O | The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
P | Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
Q | Assumed two times the reported value for service agreement excluding consumables, to take into account other fixed O&M components.
R | The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact.
References:
1 | Interview with Rolls Royce Power Systems
2 | C. Breyer. Fuel-Parity: New very large and sustainable market segments for PV systems. 2010
3 | National Grid. Short Term Operating Reserve - Carbon intensity report. 2016
4 | EEA. Distributed Generation Operational Reliability and Availability Database. 2004
5 | Maintenance schedule Caterpillar Emergency generator. Available at: https://ae.usembassy.gov/wp-content/uploads/sites/254/2017/06/stc12017q0002_post-provided-generator-checklist.pdf
6 | Interview with UK manufacturer: Edina Power UK
7 | Warstsila. White paper - Combustion engine power plants. 2011
8 | Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
9 | Timera Energy. Investment in UK peaking assets. Available at: www.timera-energy.com/investment-in-uk-peaking-assets
10 | UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
11 | EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
12 | BEIS. Electricity Generation cost. November 2016
13 | LAZARD. Levelized cost of energy analysis v11. November 2017

## 51 Natural gas engine plant
| Technology | Natural gas engine plant
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 200 | [7 empty] | A, B
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | 48 | 48 | 50 | 50 |  |  |  |  | C | 1
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 46 | 46 | 48 | 48 |  |  |  |  | D | 2
| Cb coefficient (50oC/100oC) | - | - | - | -
| Cv coefficient (50oC/100oC) | - | - | - | -
| Forced outage (%) | 0.9 | 0.9 | 0.9 | 0.9 | [5 empty] | 3
| Planned outage (days per year) | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | E
| Technical lifetime (years) | 25 | 25 | 25 | 25 |  |  |  |  | F
| Construction time (years) | 1 | 1 | 1 | 1 | [5 empty] | 4, 5
Regulation ability
| Primary regulation (% of full load per 30 seconds) | 60 | 60 | 60 | 60 |  |  |  |  | G | 6
| Secondary regulation (% of full load per minute) | 100 | 100 | 100 | 100 |  |  |  |  | G | 6
| Minimum load (% of full load) | 1.5 | 1.5 | 1.5 | 1.5 |  |  |  |  | H | 6, 7
| Warm start-up time (minutes) | 2 | 2 | 2 | 2 |  |  |  |  | I | 7
| Cold start-up time (minutes) | 10 | 10 | 10 | 10 |  |  |  |  | I | 7
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 |  |  |  |  | F | 2
| NOX (g per GJ fuel) | 75 | 75 | 75 | 75 |  |  |  |  | F | 2
| CH4 (g per GJ fuel) | 315 | 315 | 315 | 315 |  |  |  |  | F | 2
| N2O (g per GJ fuel) | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | F | 2
| Particles (g per GJ fuel) | 0.76 | 0.76 | 0.76 | 0.76 | [5 empty] | 8
Financial data
| Specific investment (M€/MW) | 0.51 | 0.4947 | 0.4743 | 0.4488 | 0.39576 | 0.59364 | 0.31416 | 0.58344 | L, M, N, R | 7, 5, 9
| - of which equipment | 0.3315 | 0.32155 | 0.3083 | 0.29172 |  |  |  |  | F | 2
| - of which installation | 0.1785 | 0.17314 | 0.16601 | 0.15708 |  |  |  |  | F | 2
| Fixed O&M (€/MW/year) | 6500 | 6500 | 6250 | 6000 |  |  |  |  | O, P | 7
| Variable O&M (€/MWh) | 6 | 6 | 6 | 6 | 2.6 | 8.5 | 2.6 | 8.5 |  | 10,11, 12
| Startup cost (€/MW/startup) | 0 | 0 | 0 | 0 |  |  |  |  | Q | 10
Technology specific data
Notes:
A | The technology is modular, normally composed by a certain amount of 2-10 MW engines. Here 20 engines of 10 MW are considered.
B | Typical capacity for ultra peakers and emergency plants is in the range 20-300 MW
C | Based on large gas motor (Wartsila 34SG)
D | Assuming the same efficiency reduction from nameplate to annual average compared to main technology catalogue.
E | Based on maintenance schedule of gas engines, considering the reduced number of operating hours and the fact that a typical scheduled maintenance services occurs after 2000, 4000 and 6000 hours, with 1 or 2 days of downtime each. No major maintenance window (16,000 h) is reached.
F | Based on the Gas Engine in the main technology catalogue
G | The values refers to the engine at nominal operating temperature.
H | Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level. Calculation done assuming 20x10MW engines.
I | The engines can startup from warm in 2 minutes. The plant cold startup time is affected by the need to warm up the transformers, which brings it up to 10 minutes. If engines and transformers are hot, the startup time is lower. In case of smaller plants connected to distribution grid, the time to warm up the transformer might not constitute a bottleneck.
L | Dual fuel operation can be considered. Impacting 3-4% of the total plant cost and 7% of engine cost
M | Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N | The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.443-0.616 M€/MW. The lower bound refers to smaller plants with smaller engines, while the higher bound refers to dual fuel plant, located further away from the grid.
O | The fixed O&M cost is lower than a typical value for plants operating >4000 h a year. A typical large maintenance window including reinvestment is carried after 10,000 running hours. Due to the low utilization, this type of plants might never need it in its lifetime, reducing the fixed O&M cost drastically. Additionally the central and lower estimates assume unmanned/remote operation of the plant, whereas the upper boundary assumes manned operation.
P | Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
Q | The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact. Modern technology can sustain up to 1000 cycles/years with no significant wear.
R | The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
References:
1 | Wartsila. Power Plant solutions 2016
2 | Main technology catalogue: Technology Data for Energy Plants - August 2016
3 | EEA. Distributed Generation Operational Reliability and Availability Database. 2004
4 | Kiisa Power plant project for Elering
5 | Warstsila. White paper - Combustion engine power plants. 2011
6 | D. Santoianni. Defining true flexibility – a comparison of gas-fired power generating technologies. 2015
7 | Phone interview with Wartsila
8 | Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
9 | UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
10 | EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
11 | BEIS. Electricity Generation cost. November 2016
12 | LAZARD. Levelized cost of energy analysis v11. November 2017

## 52 OCGT - Natural gas
| Technology | Open cycle gas turbine - natural gas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 100 | [7 empty] | A
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | 41 | 42 | 43 | 45 |  |  |  |  | B, C | 1, 2
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | 39 | 40 | 41 | 43 |  |  |  |  | C | 3
| Cb coefficient (50oC/100oC) | - | - | - | -
| Cv coefficient (50oC/100oC) | - | - | - | -
| Forced outage (%) | 1.37 | 1.37 | 1.37 | 1.37 | [5 empty] | 4
| Planned outage (days per year) | 0.75 | 0.75 | 0.75 | 0.75 |  |  |  |  | D | 1
| Technical lifetime (years) | 25 | 25 | 25 | 25 |  |  |  |  | E | 3
| Construction time (years) | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | F | 5
Regulation ability
| Primary regulation (% of full load per 30 seconds) | 30 | 30 | 30 | 30 |  |  |  |  | G | 5
| Secondary regulation (% of full load per minute) | 30 | 30 | 30 | 30 | 15 | 50 |  |  | H | 5, 6, 7
| Minimum load (% of full load) | 25 | 20 | 20 | 20 |  |  |  |  | I | 8
| Warm start-up time (minutes) | 5 | 5 | 5 | 5 | 4.5 | 6.5 |  |  |  | 8, 9, 10
| Cold start-up time (minutes) | 10 | 10 | 10 | 10 | 7 | 11 |  |  | L | 1, 6, 8
Environment
| SO2 (g per GJ fuel) | 0.43 | 0.43 | 0.43 | 0.43 | [5 empty] | 11
| NOX (g per GJ fuel) | 48 | 48 | 48 | 48 | [5 empty] | 11
| CH4 (g per GJ fuel) | 1.7 | 1.7 | 1.7 | 1.7 | [5 empty] | 11
| N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 11
| Particles (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 11
Financial data
| Specific investment (M€/MW) | 0.468 | 0.45396 | 0.43524 | 0.41184 | 0.36317 | 0.54475 | 0.28829 | 0.53539 | M, N, O | 7, 9, 10
| - of which equipment | 0.36504 | 0.35409 | 0.33949 | 0.32124 | [5 empty] | 12
| - of which installation | 0.10296 | 0.099871 | 0.095753 | 0.090605 | [5 empty] | 12
| Fixed O&M (€/MW/year) | 8068 | 8068 | 7745.28 | 7422.56 |  |  |  |  | P | 9
| Variable O&M (€/MWh) | 4.5 | 4.5 | 4.5 | 4.5 | 3.5 | 5 | 3.5 | 5 |  | 5, 9, 10
| Startup cost (€/MW/startup) | 43 | 43 | 43 | 43 | [5 empty] | 9
Technology specific data
Notes:
A | The range of generating capacity for a power plant based on this technology is tipically 50-200 MW. Large aeroderivative gas turbines have a rating of 20-100 MW.
B | The efficiency is drastically reduced at part-load. The difference between efficiency at full load and part load is on average 15%.
C | Based on the Simple Cycle Turbine in the main technology catalogue. No improvement assumed in the future
D | Considering one service per year for borescope inspection (18h). No major maintenance intervals reached, due to low utilization.
E | Lifetime most likely >25years, given low utilization
F | Some manufacturers offers pre-assembled mobile packages with installation in 30 days.
G | Based on a droop control of 0.65 MW/s of a Industrial Trent 60 (66MW) turbine at self-sustained speed.
H | Based on a gas turbine at self-sustained speed. Ramp rates of 15 MW/min to 50 MW/min.
I | The minimum emissions-compliant load is around 50%, but in case emission regulations do not apply, this can be lower. The efficiency is reduced at part-load (roughly 15%)
L | The lower bound of 7 minutes might be increased to 10 minutes if the plant is connected to high voltage and transformer needs to warm up before starting operations, similarly to Natural gas engine plants.
M | Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N | The specific investment cost can vary depending on a number of parameters, like size of turbine, electrical equipment and other characteristics. The specific investment in 2015 from several projects is in the range 0.400-0.570.
O | The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
P | Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
References:
1 | GE - Aeroderivative turbines product brochures.
2 | Siemens - Aeroderivative turbine brochures
3 | Main technology catalogue: Technology Data for Energy Plants - August 2016
4 | EEA. Distributed Generation Operational Reliability and Availability Database. 2004
5 | M. Welch, T.Krol. Flexible Power Generation for Grid Support utilizing Aero-derivative Gas Turbine Technology. 2016
6 | EU Turbines. Gas and Steam Turbines Solutions for a sustainable energy mix (brochure). 2017
7 | Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
8 | Agora Energiwende. Flexibility in thermal power plants. 2017
9 | Energy Brainpool. Flexibility Needs and Options for Europe's Future Electricity System. September 2017.
10 | Phone interview with Siemens Turbomachinery UK
11 | Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
12 | ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009

## 52 OCGT - Light fuel oil
| Technology | Open cycle gas turbine - light fuel oil
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW)
| Electricity efficiency (condensation mode for extraction plants), net (%), name plate | -1 | -1 | -1 | -1 | -0.5 | 1 |  |  | A | 18
| Electricity efficiency (condensation mode for extraction plants), net (%), annual average | -1 | -1 | -1 | -1 | -0.5 | 1 |  |  | A | 18
| Cb coefficient (50oC/100oC) | - | - | - | -
| Cv coefficient (50oC/100oC) | - | - | - | -
Forced outage (%)
Planned outage (days per year)
Technical lifetime (years)
Construction time (years)
Regulation ability
Primary regulation (% of full load per 30 seconds)
Secondary regulation (% of full load per minute)
Minimum load (% of full load)
| Warm start-up time (minutes) | +0.5 | +0.5 | +0.5 | +0.5 |  |  |  |  | A | 18
| Cold start-up time (minutes) | +0.5 | +0.5 | +0.5 | +0.5 |  |  |  |  | A | 18
Environment
| SO2 (g per GJ fuel) | 23 | 23 | 23 | 23 |  |  |  |  | B | 11
| NOX (g per GJ fuel) | 230 | 230 | 230 | 230 |  |  |  |  | B | 11
| CH4 (g per GJ fuel) | 3 | 3 | 3 | 3 |  |  |  |  | B | 11
| N2O (g per GJ fuel) | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | B | 11
| Particles (g per GJ fuel) | 5 | 5 | 5 | 5 |  |  |  |  | B | 11
Financial data
| Specific investment (M€/MW) | 0.39 | 0.3783 | 0.3627 | 0.3432 | 0.30264 | 0.45396 | 0.24024 | 0.44616 | C, D | 19
| - of which equipment | 0.3042 | 0.29507 | 0.28291 | 0.2677 | [5 empty] | 20
| - of which installation | 0.0858 | 0.083226 | 0.079794 | 0.075504 | [5 empty] | 20
Fixed O&M (€/MW/year)
Variable O&M (€/MWh)
Startup cost (€/MW/startup)
Technology specific data
Notes:
A | Value indicate the estimated change from the correspondent value of natural gas fuelled plant (unit is the same as the paramter).
B | Emission values for Gas Oil. If Residual Oil used, SO2 emissions increased to 100g, NOx reduced to 138g and Particles to 3g.
C | Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016. Same development as natural gas fuelled plant, since the technology is the same.
D | The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
References:
11 | Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
18 | Phone interview with Siemens Turbomachinery UK
19 | Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
20 | ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009