## Index
INDEX | Technology Data for Industrial Process Heat
HP APP POT overlap | All cost data is in 2019€
301.1a heat pump 60 C 40 K
301.1b heat pump 70 C 50 K
301.1c heat pump 80 C 60 K
301.2 heat_cool hp 80 C 75 K
302.a High temp. hp Up to 125 C | Date | Sheet | Change | Notes
302.b High temp. hp Up to 150 | 2022-12-15 | 310.1a-310.2b | Electric boilers replaced and updated
303 Booster hp 150 C 130 K | 2021-11-01 | 401-403 CC | Carbon capture removed and transferred to the Technology Catalogue for Carbon Capture, Transport and Storage
304 Heat driven hp 80 C | 2020-10-01 | 401-403 CC | Carbon capture added
305 MVR 5 K
306 Thermal gasification
307 Hotdisc
308 Dielectric heating
309 Infrared (IR)
310.1a Electric boiler steam
310.1b Electric boiler steam
310.2a Electric boiler hot water
310.2b Electric boiler hot water
311.1a Steam boiler Coal
311.1b Steam boiler Oil
311.1c Steam boiler Gas
311.1d Steam boiler Gas cond
311.1e Steam boiler Wood
311.1f Steam boiler Wood cond
311.2a Hot water boiler, Coal
311.2b Hot water boiler Oil
311.2c Hot water boiler Gas
311.d Hot water boiler Gas cond
311.2e Hot water boiler Wood
311.2fHot waterboiler Wood cond
312.a Direct firing Natural Gas
312.b Direct firing Sold Fuels
312.c Direct firing Electricity
This file contains the technology data sheets related to industrial process heat. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. Dates and descriptions of updates are listed in the ammendment sheet below.

## HP APP POT overlap
Heat pump application potential overlap | [17 empty] | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Technology | Notes | [16 empty] | Current application potential | Full application potential | Current application potential | Full application potential | Current application potential | Full application potential | Current application potential | Full application potential | Current application potential | Full application potential
Heat pump, up to 60 °C, Temp lift = 40 K | [17 empty] | 4% | 16% | 4% | 16% | 3.25% | 13% | 1.75% | 7% | 2.75% | 11%
Heat pump, up to 70 °C, Temp lift = 50 K | [17 empty] | 4.75% | 19% | 4.75% | 19% | 3.5% | 14% | 2.75% | 11% | 3% | 12%
Heat pump, up to 80 °C, Temp lift = 60 K | [17 empty] | 5.25% | 21% | 5.5% | 22% | 3.75% | 15% | 3.5% | 14% | 3.5% | 14%
Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | [17 empty] | 3% | 12% | 0.5% | 2% | 0% | 0% | 1.25% | 5% | 0% | 0%
High temperature heat pumps, up to 125 °C | [17 empty] | 5.75% | 23% | 6.5% | 26% | 4% | 16% | 4.25% | 17% | 4% | 16%
High temperature heat pumps, up to 150 °C | A, B | [16 empty] | 2.25% | 9% | 2.5% | 10% | 0.75% | 3% | 1.25% | 5% | 1.75% | 7%
Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | [17 empty] | 15.75% | 63% | 9% | 36% | 5.75% | 23% | 16.5% | 66% | 11.75% | 47%
Heat driven heat pumps, up to 80 °C | [17 empty] | 2% | 2% | 2% | 2% | 1% | 1% | 1% | 1% | 1% | 1%
|  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150
Temperature [°C]
Notes
| A | 0: The potential is limited by the available heat source at 80 °C
| B | 0: The heat pump can potentially cover, 24 %, 32 %, 17 %, 17 %, 18 %, of medium temperature in-direct for the five sectors 1., 2., 3., 4., 5, respectively

## alldata_flat
ws | technology | tech | cat | par | par_short | info | unit | priceyear | note | ref | est | year | val
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2020 | 3
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2030 | 3
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2040 | 3
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2050 | 3
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Lower | 2030 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Upper | 2030 | 5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Lower | 2050 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Upper | 2050 | 5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2020 | 533
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2030 | 548.99
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2040 | 559.9698
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2050 | 565.5695
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Lower | 2030 | 533
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Upper | 2030 | 559.65
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Lower | 2050 | 548.6024
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Upper | 2050 | 576.8809
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2020 | 528
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2030 | 543.99
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2040 | 554.9698
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2050 | 560.5695
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Lower | 2030 | 528
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Upper | 2030 | 554.65
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Lower | 2050 | 543.6024
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Upper | 2050 | 571.8809
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2020 | 2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2030 | 2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2040 | 2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2050 | 2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Lower | 2030 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Upper | 2030 | 4
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Lower | 2050 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Upper | 2050 | 4
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2020 | 0
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2030 | 0
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2040 | 0
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2050 | 0
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Lower | 2030 | 0
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Upper | 2030 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Lower | 2050 | 0
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Upper | 2050 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2020 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2030 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2040 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2050 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Lower | 2030 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Upper | 2030 | 2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Lower | 2050 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Upper | 2050 | 2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 15
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 30
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 15
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 30
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2020 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2030 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2040 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2050 | 0.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2030 | 0.3
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2030 | 0.7
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2050 | 0.3
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2050 | 0.7
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2020 | 10
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2030 | 10
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2040 | 10
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2050 | 10
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2020 | 0.25
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2030 | 0.25
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2040 | 0.25
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2050 | 0.25
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 1
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2020 | 0.73
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2030 | 0.65
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2040 | 0.6
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2050 | 0.58
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2020 | 60
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2030 | 60
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2040 | 60
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2050 | 60
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2020 | 40
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2030 | 40
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2040 | 40
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2050 | 40
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2020 | 2000
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2030 | 2000
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2040 | 2000
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2050 | 2000
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 3.26
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 3.2
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 3.16
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 3.12
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2020 | 1.46
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2030 | 1.5
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2040 | 1.52
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2050 | 1.52
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 1.8
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 1.7
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 1.65
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 1.6
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2020 | 0.146
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2030 | 0.13
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2040 | 0.12
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2050 | 0.116
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2020 | 30
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2030 | 30
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2040 | 30
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2050 | 30
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2020 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2030 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2040 | 20
301.1a heat pump 60 C 40 K | Heat pump, up to 60 °C, Temp lift = 40 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2050 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2020 | 3
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2030 | 3
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2040 | 3
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2050 | 3
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Lower | 2030 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Upper | 2030 | 5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Lower | 2050 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Upper | 2050 | 5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2020 | 447
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2030 | 460.41
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2040 | 469.6182
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2050 | 474.3144
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Lower | 2030 | 447
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Upper | 2030 | 469.35
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Lower | 2050 | 460.085
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Upper | 2050 | 483.8007
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2020 | 442
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2030 | 455.41
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2040 | 464.6182
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2050 | 469.3144
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Lower | 2030 | 442
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Upper | 2030 | 464.35
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Lower | 2050 | 455.085
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Upper | 2050 | 478.8007
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2020 | 2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2030 | 2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2040 | 2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2050 | 2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Lower | 2030 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Upper | 2030 | 4
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Lower | 2050 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Upper | 2050 | 4
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2020 | 0
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2030 | 0
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2040 | 0
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2050 | 0
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Lower | 2030 | 0
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Upper | 2030 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Lower | 2050 | 0
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Upper | 2050 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2020 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2030 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2040 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2050 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Lower | 2030 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Upper | 2030 | 2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Lower | 2050 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Upper | 2050 | 2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 15
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 30
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 15
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 30
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2020 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2030 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2040 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2050 | 0.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2030 | 0.3
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2030 | 0.7
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2050 | 0.3
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2050 | 0.7
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2020 | 10
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2030 | 10
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2040 | 10
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2050 | 10
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2020 | 0.25
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2030 | 0.25
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2040 | 0.25
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2050 | 0.25
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 1
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2020 | 0.73
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2030 | 0.65
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2040 | 0.6
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2050 | 0.58
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2020 | 60
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2030 | 60
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2040 | 60
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2050 | 60
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2020 | 40
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2030 | 40
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2040 | 40
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2050 | 40
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2020 | 2000
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2030 | 2000
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2040 | 2000
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2050 | 2000
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 3.26
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 3.2
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 3.16
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 3.12
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2020 | 1.46
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2030 | 1.5
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2040 | 1.52
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2050 | 1.52
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 1.8
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 1.7
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 1.65
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 1.6
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2020 | 0.146
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2030 | 0.13
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2040 | 0.12
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2050 | 0.116
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2020 | 30
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2030 | 30
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2040 | 30
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2050 | 30
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2020 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2030 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2040 | 20
301.1b heat pump 70 C 50 K | Heat pump, up to 70 °C, Temp lift = 50 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2050 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2020 | 3
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2030 | 3
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2040 | 3
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | ctrl | 2050 | 3
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Lower | 2030 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Upper | 2030 | 5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Lower | 2050 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1, 3 | Upper | 2050 | 5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2020 | 388
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2030 | 399.64
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2040 | 407.6328
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | ctrl | 2050 | 411.7091
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Lower | 2030 | 388
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Upper | 2030 | 407.4
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Lower | 2050 | 399.3579
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1, 3 | Upper | 2050 | 419.9433
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2020 | 383
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2030 | 394.64
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2040 | 402.6328
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | ctrl | 2050 | 406.7091
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Lower | 2030 | 383
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Upper | 2030 | 402.4
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Lower | 2050 | 394.3579
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B,C |  | Upper | 2050 | 414.9433
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2020 | 2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2030 | 2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2040 | 2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | ctrl | 2050 | 2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Lower | 2030 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Upper | 2030 | 4
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Lower | 2050 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1.4 | Upper | 2050 | 4
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2020 | 0
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2030 | 0
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2040 | 0
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | ctrl | 2050 | 0
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Lower | 2030 | 0
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Upper | 2030 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Lower | 2050 | 0
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D |  | Upper | 2050 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2020 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2030 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2040 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | ctrl | 2050 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Lower | 2030 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Upper | 2030 | 2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Lower | 2050 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1.4 | Upper | 2050 | 2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 15
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 30
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 15
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 30
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2020 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2030 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2040 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2050 | 0.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2030 | 0.3
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2030 | 0.7
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2050 | 0.3
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2050 | 0.7
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2020 | 10
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2030 | 10
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2040 | 10
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2050 | 10
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2020 | 0.25
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2030 | 0.25
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2040 | 0.25
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 4 | ctrl | 2050 | 0.25
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 1
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2020 | 0.73
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2030 | 0.65
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2040 | 0.6
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2050 | 0.58
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2020 | 60
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2030 | 60
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2040 | 60
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 6 | ctrl | 2050 | 60
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2020 | 40
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2030 | 40
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2040 | 40
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | F | 6 | ctrl | 2050 | 40
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2020 | 2000
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2030 | 2000
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2040 | 2000
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4.5 | ctrl | 2050 | 2000
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 3.26
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 3.2
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 3.16
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 3.12
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2020 | 1.46
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2030 | 1.5
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2040 | 1.52
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 4 | ctrl | 2050 | 1.52
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 1.8
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 1.7
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 1.65
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 1.6
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2020 | 0.146
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2030 | 0.13
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2040 | 0.12
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2050 | 0.116
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2020 | 30
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2030 | 30
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2040 | 30
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2050 | 30
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2020 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2030 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2040 | 20
301.1c heat pump 80 C 60 K | Heat pump, up to 80 °C, Temp lift = 60 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2050 | 20
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | ctrl | 2020 | 3
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | ctrl | 2030 | 3
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | ctrl | 2040 | 3
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | ctrl | 2050 | 3
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | Lower | 2030 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | Upper | 2030 | 5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | Lower | 2050 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1,3 | Upper | 2050 | 5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | ctrl | 2020 | 333
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | ctrl | 2030 | 342.99
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | ctrl | 2040 | 349.8498
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | ctrl | 2050 | 353.3483
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | Lower | 2030 | 333
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | Upper | 2030 | 349.65
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | Lower | 2050 | 342.7478
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 1,3 | Upper | 2050 | 360.4153
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2020 | 328
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2030 | 337.99
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2040 | 344.8498
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2050 | 348.3483
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Lower | 2030 | 328
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Upper | 2030 | 344.65
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Lower | 2050 | 337.7478
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Upper | 2050 | 355.4153
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | ctrl | 2020 | 2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | ctrl | 2030 | 2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | ctrl | 2040 | 2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | ctrl | 2050 | 2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | Lower | 2030 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | Upper | 2030 | 4
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | Lower | 2050 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 4 | Upper | 2050 | 4
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | ctrl | 2020 | 0
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | ctrl | 2030 | 0
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | ctrl | 2040 | 0
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | ctrl | 2050 | 0
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | Lower | 2030 | 0
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | Upper | 2030 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | Lower | 2050 | 0
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 4 | Upper | 2050 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | ctrl | 2020 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | ctrl | 2030 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | ctrl | 2040 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | ctrl | 2050 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | Lower | 2030 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | Upper | 2030 | 2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | Lower | 2050 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E | 1 | Upper | 2050 | 2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2020 | 20
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2030 | 20
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2040 | 20
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2050 | 20
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Lower | 2030 | 15
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Upper | 2030 | 30
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Lower | 2050 | 15
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Upper | 2050 | 30
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2020 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2030 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2040 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | ctrl | 2050 | 0.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2030 | 0.3
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2030 | 0.7
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Lower | 2050 | 0.3
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 4 | Upper | 2050 | 0.7
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0.25
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0.25
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0.25
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0.25
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 1
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1,5 | ctrl | 2020 | 0.73
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1,5 | ctrl | 2030 | 0.65
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1,5 | ctrl | 2040 | 0.6
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1,5 | ctrl | 2050 | 0.58
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | F | 6 | ctrl | 2020 | 60
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | F | 6 | ctrl | 2030 | 60
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | F | 6 | ctrl | 2040 | 60
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | F | 6 | ctrl | 2050 | 60
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | G | 6 | ctrl | 2020 | 40
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | G | 6 | ctrl | 2030 | 40
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | G | 6 | ctrl | 2040 | 40
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | G | 6 | ctrl | 2050 | 40
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4,6 | ctrl | 2020 | 2000
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4,6 | ctrl | 2030 | 2000
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4,6 | ctrl | 2040 | 2000
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 4,6 | ctrl | 2050 | 2000
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 3.26
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 3.2
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 3.16
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 3.12
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H |  | ctrl | 2020 | 1.46
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H |  | ctrl | 2030 | 1.5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H |  | ctrl | 2040 | 1.52
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H |  | ctrl | 2050 | 1.52
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2020 | 1.8
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2030 | 1.7
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2040 | 1.65
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 4 | ctrl | 2050 | 1.6
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | K |  | ctrl | 2020 | 15
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | K |  | ctrl | 2030 | 15
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | K |  | ctrl | 2040 | 15
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | K |  | ctrl | 2050 | 15
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | K |  | ctrl | 2020 | 5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | K |  | ctrl | 2030 | 5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | K |  | ctrl | 2040 | 5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | K |  | ctrl | 2050 | 5
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | K |  | ctrl | 2020 | 2.0991
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | K |  | ctrl | 2030 | 2.1253
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | K |  | ctrl | 2040 | 2.1425
301.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | K |  | ctrl | 2050 | 2.151
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 1.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 1.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 1.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 1.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 0.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 0.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2020 | 260
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2030 | 275
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2040 | 285
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2050 | 290
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Lower | 2030 | 260
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Upper | 2030 | 302.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Lower | 2050 | 260
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Upper | 2050 | 319
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2020 | 255
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2030 | 270
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2040 | 280
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2050 | 285
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Lower | 2030 | 255
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Upper | 2030 | 297.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Lower | 2050 | 255
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Upper | 2050 | 314
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2020 | 2
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2030 | 2
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2040 | 2
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2050 | 2
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Lower | 2030 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Upper | 2030 | 7
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Lower | 2050 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Upper | 2050 | 7
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2020 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2030 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2040 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2050 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Lower | 2030 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Upper | 2030 | 0.01
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Lower | 2050 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Upper | 2050 | 0.01
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 0.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 0.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 0.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 0.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 0
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 20
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 20
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 20
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 20
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 15
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 30
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 15
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 30
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2020 | 0.6
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2030 | 0.6
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2040 | 0.6
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2050 | 0.6
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Lower | 2030 | 0.4
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Upper | 2030 | 0.8
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Lower | 2050 | 0.4
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Upper | 2050 | 0.8
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2020 | 25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2030 | 25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2040 | 25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2050 | 25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2020 | 0.25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2030 | 0.25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2040 | 0.25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2050 | 0.25
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2020 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2030 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2040 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2050 | 1
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1, 3, 4 | ctrl | 2020 | 0.8712
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1, 3, 4 | ctrl | 2030 | 0.7788
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1, 3, 4 | ctrl | 2040 | 0.73
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1, 3, 4 | ctrl | 2050 | 0.7
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 4 | ctrl | 2020 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 4 | ctrl | 2030 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 4 | ctrl | 2040 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 4 | ctrl | 2050 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 4 | ctrl | 2020 | 60
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 4 | ctrl | 2030 | 60
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 4 | ctrl | 2040 | 60
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 4 | ctrl | 2050 | 60
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2020 | 970
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2030 | 870
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2040 | 800
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2050 | 720
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 3.26
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 3.2
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 3.22
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 3.12
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F | 3 | ctrl | 2020 | 1.46
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F | 3 | ctrl | 2030 | 1.5
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F | 3 | ctrl | 2040 | 1.52
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F | 3 | ctrl | 2050 | 1.52
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2020 | 1.8
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2030 | 1.7
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2040 | 1.7
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2050 | 1.6
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2020 | 0.17424
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2030 | 0.15576
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2040 | 0.146
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2050 | 0.14
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | H |  | ctrl | 2020 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | H |  | ctrl | 2030 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | H |  | ctrl | 2040 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | H |  | ctrl | 2050 | 40
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | H |  | ctrl | 2020 | 10
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | H |  | ctrl | 2030 | 10
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | H |  | ctrl | 2040 | 10
302.a High temp. hp Up to 125 C | High temperature heat pumps, up to 125 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | H |  | ctrl | 2050 | 10
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 1.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 1.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 1.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 1.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 0.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 0.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2020 | 300
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2030 | 310
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2040 | 320
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | ctrl | 2050 | 325
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Lower | 2030 | 310
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Upper | 2030 | 341
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Lower | 2050 | 310
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1.5 | Upper | 2050 | 357.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2020 | 295
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2030 | 305
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2040 | 315
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | ctrl | 2050 | 320
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Lower | 2030 | 305
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Upper | 2030 | 336
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Lower | 2050 | 305
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | B |  | Upper | 2050 | 352.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2020 | 2
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2030 | 2
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2040 | 2
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2050 | 2
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Lower | 2030 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Upper | 2030 | 7
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Lower | 2050 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Upper | 2050 | 7
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2020 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2030 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2040 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | ctrl | 2050 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Lower | 2030 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Upper | 2030 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Lower | 2050 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 2 | Upper | 2050 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 0.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 0.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 0.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 0.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 0
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 20
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 20
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 20
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 20
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 15
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 30
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 15
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 30
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2020 | 0.6
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2030 | 0.6
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2040 | 0.6
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | ctrl | 2050 | 0.6
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Lower | 2030 | 0.4
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Upper | 2030 | 0.8
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Lower | 2050 | 0.4
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | D | 2 | Upper | 2050 | 0.8
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2020 | 25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2030 | 25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2040 | 25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | E | 4 | ctrl | 2050 | 25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2020 | 0.25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2030 | 0.25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2040 | 0.25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2050 | 0.25
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2020 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2030 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2040 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 9 | ctrl | 2050 | 1
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F | 1, 3, 4 | ctrl | 2020 | 1.0454
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F | 1, 3, 4 | ctrl | 2030 | 0.93456
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F | 1, 3, 4 | ctrl | 2040 | 0.876
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F | 1, 3, 4 | ctrl | 2050 | 0.84
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which equipment | - of which equipment | - of which equipment | M€ per MW | 2019 |  | 4 | ctrl | 2020 | 40
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which equipment | - of which equipment | - of which equipment | M€ per MW | 2019 |  | 4 | ctrl | 2030 | 40
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which equipment | - of which equipment | - of which equipment | M€ per MW | 2019 |  | 4 | ctrl | 2040 | 40
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which equipment | - of which equipment | - of which equipment | M€ per MW | 2019 |  | 4 | ctrl | 2050 | 40
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which installation | - of which installation | - of which installation | M€ per MW | 2019 |  | 4 | ctrl | 2020 | 60
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which installation | - of which installation | - of which installation | M€ per MW | 2019 |  | 4 | ctrl | 2030 | 60
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which installation | - of which installation | - of which installation | M€ per MW | 2019 |  | 4 | ctrl | 2040 | 60
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which installation | - of which installation | - of which installation | M€ per MW | 2019 |  | 4 | ctrl | 2050 | 60
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2020 | 970
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2030 | 870
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2040 | 800
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 5 | ctrl | 2050 | 720
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 3.26
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 3.2
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 3.22
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 3.12
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2020 | 1.46
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2030 | 1.5
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2040 | 1.52
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2050 | 1.52
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2020 | 1.8
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2030 | 1.7
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2040 | 1.7
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2050 | 1.6
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2020 | 0.20909
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2030 | 0.18691
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2040 | 0.1752
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2050 | 0.168
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2020 | 80
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2030 | 80
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2040 | 80
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | I |  | ctrl | 2050 | 80
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2020 | 50
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2030 | 50
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2040 | 50
302.b High temp. hp Up to 150 | High temperature heat pumps, up to 150 °C |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | I |  | ctrl | 2050 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 10
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 15
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | ctrl | 2020 | 198
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | ctrl | 2030 | 203.94
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | ctrl | 2040 | 208.0188
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | ctrl | 2050 | 210.099
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | Lower | 2030 | 198
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | Upper | 2030 | 207.9
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | Lower | 2050 | 203.796
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C |  | Upper | 2050 | 214.301
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2020 | 193
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2030 | 198.94
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2040 | 203.0188
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | ctrl | 2050 | 205.099
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Lower | 2030 | 193
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Upper | 2030 | 202.9
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Lower | 2050 | 198.796
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | D |  | Upper | 2050 | 209.301
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | ctrl | 2020 | 2
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | ctrl | 2030 | 2
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | ctrl | 2040 | 2
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | ctrl | 2050 | 2
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | Lower | 2030 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | Upper | 2030 | 4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | Lower | 2050 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | E |  | Upper | 2050 | 4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | ctrl | 2020 | 0
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | ctrl | 2030 | 0
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | ctrl | 2040 | 0
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | ctrl | 2050 | 0
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | Lower | 2030 | 0
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | Upper | 2030 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | Lower | 2050 | 0
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | E |  | Upper | 2050 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | ctrl | 2020 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | ctrl | 2030 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | ctrl | 2040 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | ctrl | 2050 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | Lower | 2030 | 0.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | Upper | 2030 | 2
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | Lower | 2050 | 0.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | E |  | Upper | 2050 | 2
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | ctrl | 2020 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | ctrl | 2030 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | ctrl | 2040 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | ctrl | 2050 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | Lower | 2030 | 15
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | Upper | 2030 | 30
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | Lower | 2050 | 15
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 | E |  | Upper | 2050 | 30
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | ctrl | 2020 | 0.6
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | ctrl | 2030 | 0.6
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | ctrl | 2040 | 0.6
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | ctrl | 2050 | 0.6
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | Lower | 2030 | 0.4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | Upper | 2030 | 0.8
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | Lower | 2050 | 0.4
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | F |  | Upper | 2050 | 0.8
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | E |  | ctrl | 2020 | 0.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | E |  | ctrl | 2030 | 0.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | E |  | ctrl | 2040 | 0.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | E |  | ctrl | 2050 | 0.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | E |  | ctrl | 2020 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | E |  | ctrl | 2030 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | E |  | ctrl | 2040 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | E |  | ctrl | 2050 | 1
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2020 | 1.6321
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2030 | 1.3231
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2040 | 1.037
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | G |  | ctrl | 2050 | 0.93368
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | H |  | ctrl | 2020 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | H |  | ctrl | 2030 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | H |  | ctrl | 2040 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | H |  | ctrl | 2050 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | I |  | ctrl | 2020 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | I |  | ctrl | 2030 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | I |  | ctrl | 2040 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | I |  | ctrl | 2050 | 50
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | E |  | ctrl | 2020 | 2000
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | E |  | ctrl | 2030 | 2000
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | E |  | ctrl | 2040 | 2000
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | E |  | ctrl | 2050 | 2000
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 3.44
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 3.37
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 3.335
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 3.28
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J |  | ctrl | 2020 | 1.46
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J |  | ctrl | 2030 | 1.5
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J |  | ctrl | 2040 | 1.52
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J |  | ctrl | 2050 | 1.52
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | K |  | ctrl | 2020 | 1.98
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | K |  | ctrl | 2030 | 1.87
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | K |  | ctrl | 2040 | 1.815
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | K |  | ctrl | 2050 | 1.76
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | L |  | ctrl | 2020 | 0.32641
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | L |  | ctrl | 2030 | 0.26462
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | L |  | ctrl | 2040 | 0.2074
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | L |  | ctrl | 2050 | 0.18674
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | N |  | ctrl | 2020 | 30
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | N |  | ctrl | 2030 | 30
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | N |  | ctrl | 2040 | 30
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source supply (°C) | Temperature heat source supply (°C) | Temperature heat source supply (°C) | °C | 2019 | N |  | ctrl | 2050 | 30
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | N |  | ctrl | 2020 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | N |  | ctrl | 2030 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | N |  | ctrl | 2040 | 20
303 Booster hp 150 C 130 K | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam |  | Technology specific data | Temperature heat source return (°C) | Temperature heat source return (°C) | Temperature heat source return (°C) | °C | 2019 | N |  | ctrl | 2050 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | ctrl | 2020 | 12
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | ctrl | 2030 | 12
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | ctrl | 2040 | 12
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | ctrl | 2050 | 12
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | Lower | 2030 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | Upper | 2030 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | Lower | 2050 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A,B | 1 | Upper | 2050 | 30
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2020 | 170
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2030 | 171
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2040 | 172
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2050 | 173
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Lower | 2030 | 170
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Upper | 2030 | 180
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Lower | 2050 | 170
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Upper | 2050 | 180
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | ctrl | 2020 | 168
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | ctrl | 2030 | 169
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | ctrl | 2040 | 170
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | ctrl | 2050 | 171
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | Lower | 2030 | 168
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | Upper | 2030 | 178
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | Lower | 2050 | 168
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | C |  | Upper | 2050 | 178
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2020 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2030 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2040 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2050 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Lower | 2030 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Upper | 2030 | 3
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Lower | 2050 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Upper | 2050 | 3
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2020 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2030 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2040 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2050 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Lower | 2030 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Upper | 2030 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Lower | 2050 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Upper | 2050 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2020 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2030 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2040 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2050 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2030 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2030 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2050 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2050 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 30
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 20
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 30
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2020 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2030 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2040 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2050 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2030 | 0.3
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2030 | 0.7
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2050 | 0.3
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2050 | 0.7
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0.5
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized heat
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2020 | 0.56
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2030 | 0.51
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2040 | 0.48
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1 | ctrl | 2050 | 0.46
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2020 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2030 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2040 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2050 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2020 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2030 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2040 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2050 | 50
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2020 | 2000
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2030 | 2000
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2040 | 2000
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2050 | 2000
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2020 | 1.01
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2030 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2040 | 1
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2050 | 0.99
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2020 | 0.73
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2030 | 0.75
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2040 | 0.76
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2050 | 0.76
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2020 | 0.28
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2030 | 0.25
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2040 | 0.24
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2050 | 0.23
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized heat
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | F |  | ctrl | 2020 | 4.9412
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | F |  | ctrl | 2030 | 4.9825
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | F |  | ctrl | 2040 | 5.0233
304 Heat driven hp 80 C | Heat driven heat pumps, up to 80 °C |  | Technology specific data | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | Cooling generation capacity for one unit (MW) | MW | 2019 | F |  | ctrl | 2050 | 5.0636
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2020 | 20
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2030 | 20
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2040 | 20
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2050 | 20
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2030 | 5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2030 | 50
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2050 | 5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2050 | 50
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | ctrl | 2020 | 1260
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | ctrl | 2030 | 1320
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | ctrl | 2040 | 1380
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | ctrl | 2050 | 1430
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | Lower | 2030 | 1000
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | Upper | 2030 | 1512
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | Lower | 2050 | 1056
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 1 | Upper | 2050 | 1716
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2020 | 1210
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2030 | 1270
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2040 | 1330
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2050 | 1380
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Lower | 2030 | 950
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Upper | 2030 | 1462
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Lower | 2050 | 1006
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Upper | 2050 | 1666
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 2
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 2
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2020 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2030 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2040 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2050 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2030 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2030 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2050 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2050 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 0
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | ctrl | 2020 | 25
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | ctrl | 2030 | 25
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | ctrl | 2040 | 25
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | ctrl | 2050 | 25
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | Lower | 2030 | 15
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | Upper | 2030 | 35
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | Lower | 2050 | 15
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1.2 | Upper | 2050 | 35
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | ctrl | 2020 | 0.1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | ctrl | 2030 | 0.1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | ctrl | 2040 | 0.1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | ctrl | 2050 | 0.1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | Lower | 2030 | 0.05
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | Upper | 2030 | 0.2
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | Lower | 2050 | 0.05
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1.3 | Upper | 2050 | 0.2
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2020 | 15
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2030 | 15
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2040 | 15
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 4 | ctrl | 2050 | 15
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.5
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 1
305 MVR 5 K | Mechanical vapor recompression |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1.5 | ctrl | 2020 | 0.35
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1.5 | ctrl | 2030 | 0.33
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1.5 | ctrl | 2040 | 0.32
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 |  | 1.5 | ctrl | 2050 | 0.31
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 1.5 | ctrl | 2020 | 60
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 1.5 | ctrl | 2030 | 60
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 1.5 | ctrl | 2040 | 60
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 1.5 | ctrl | 2050 | 60
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 1.5 | ctrl | 2020 | 40
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 1.5 | ctrl | 2030 | 40
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 1.5 | ctrl | 2040 | 40
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 1.5 | ctrl | 2050 | 40
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2 | ctrl | 2020 | 2000
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2 | ctrl | 2030 | 2000
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2 | ctrl | 2040 | 200
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2 | ctrl | 2050 | 2000
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2020 | 2.53
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2030 | 2.45
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2040 | 2.46
305 MVR 5 K | Mechanical vapor recompression |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2050 | 2.36
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 2 | ctrl | 2020 | 0.73
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 2 | ctrl | 2030 | 0.75
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 2 | ctrl | 2040 | 0.76
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 2 | ctrl | 2050 | 0.76
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2020 | 1.8
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2030 | 1.7
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2040 | 1.7
305 MVR 5 K | Mechanical vapor recompression |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2 | ctrl | 2050 | 1.6
305 MVR 5 K | Mechanical vapor recompression |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | ctrl | 2020 | 5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | ctrl | 2030 | 5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | ctrl | 2040 | 5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | ctrl | 2050 | 5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | Lower | 2030 | 2
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | Upper | 2030 | 20
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | Lower | 2050 | 2
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 1 | Upper | 2050 | 20
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | ctrl | 2020 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | ctrl | 2030 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | ctrl | 2040 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | ctrl | 2050 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | Lower | 2030 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | Upper | 2030 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | Lower | 2050 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 1 | Upper | 2050 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | ctrl | 2020 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | ctrl | 2030 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | ctrl | 2040 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | ctrl | 2050 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | Lower | 2030 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | Upper | 2030 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | Lower | 2050 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 1 | Upper | 2050 | 100
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2020 | 0.035
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2030 | 0.035
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2040 | 0.035
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | ctrl | 2050 | 0.035
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Lower | 2030 | 0.02
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Upper | 2030 | 0.05
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Lower | 2050 | 0.02
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 2 | Upper | 2050 | 0.05
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2020 | 0.3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2030 | 0.3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2040 | 0.3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2050 | 0.3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2030 | 0
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2030 | 1
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2050 | 0
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2050 | 1
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 2.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 2.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 2.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 2.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 2
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 2
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 20
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 20
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 20
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 20
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 15
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 25
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 15
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 25
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2020 | 1.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2030 | 1.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2040 | 1.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2050 | 1.5
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Lower | 2030 | 1
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Upper | 2030 | 2
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Lower | 2050 | 1
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Upper | 2050 | 2
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2020 | 10
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2030 | 10
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2040 | 10
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2050 | 10
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 3
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 30
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 30
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 30
306 Thermal gasification | Thermal Gasification |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 30
306 Thermal gasification | Thermal Gasification |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Depends on fuel and operation
306 Thermal gasification | Thermal Gasification |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B, E | 1, 2 | ctrl | 2020 | 2
306 Thermal gasification | Thermal Gasification |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B, E | 1, 2 | ctrl | 2030 | 1.8
306 Thermal gasification | Thermal Gasification |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B, E | 1, 2 | ctrl | 2040 | 1.6
306 Thermal gasification | Thermal Gasification |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B, E | 1, 2 | ctrl | 2050 | 1.5
306 Thermal gasification | Thermal Gasification |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2020 | 70
306 Thermal gasification | Thermal Gasification |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2030 | 70
306 Thermal gasification | Thermal Gasification |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2040 | 70
306 Thermal gasification | Thermal Gasification |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2050 | 70
306 Thermal gasification | Thermal Gasification |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2020 | 30
306 Thermal gasification | Thermal Gasification |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2030 | 30
306 Thermal gasification | Thermal Gasification |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2040 | 30
306 Thermal gasification | Thermal Gasification |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2050 | 30
306 Thermal gasification | Thermal Gasification |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | B, D | 1, 2 | ctrl | 2020 | 13500
306 Thermal gasification | Thermal Gasification |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | B, D | 1, 2 | ctrl | 2030 | 12375
306 Thermal gasification | Thermal Gasification |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | B, D | 1, 2 | ctrl | 2040 | 11250
306 Thermal gasification | Thermal Gasification |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | B, D | 1, 2 | ctrl | 2050 | 10125
306 Thermal gasification | Thermal Gasification |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1, 2 | ctrl | 2020 | 1.0255
306 Thermal gasification | Thermal Gasification |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1, 2 | ctrl | 2030 | 0.94292
306 Thermal gasification | Thermal Gasification |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1, 2 | ctrl | 2040 | 0.85993
306 Thermal gasification | Thermal Gasification |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1, 2 | ctrl | 2050 | 0.7766
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 1, 2 | ctrl | 2020 | 0.02555
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 1, 2 | ctrl | 2030 | 0.02625
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 1, 2 | ctrl | 2040 | 0.0266
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | C | 1, 2 | ctrl | 2050 | 0.0266
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | B | 1, 2 | ctrl | 2020 | 1
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | B | 1, 2 | ctrl | 2030 | 0.91667
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | B | 1, 2 | ctrl | 2040 | 0.83333
306 Thermal gasification | Thermal Gasification |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | B | 1, 2 | ctrl | 2050 | 0.75
306 Thermal gasification | Thermal Gasification |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
306 Thermal gasification | Thermal Gasification |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
306 Thermal gasification | Thermal Gasification |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
306 Thermal gasification | Thermal Gasification |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2020 | 50
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2030 | 50
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2040 | 50
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2050 | 50
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2030 | 10
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2030 | 100
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2050 | 10
307 Hotdisc | Hotdisc |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2050 | 100
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2020 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2030 | 91
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2040 | 92
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | ctrl | 2050 | 93
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Lower | 2030 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Upper | 2030 | 98
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Lower | 2050 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1 | Upper | 2050 | 98
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | ctrl | 2020 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | ctrl | 2030 | 91
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | ctrl | 2040 | 92
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | ctrl | 2050 | 93
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | Lower | 2030 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | Upper | 2030 | 98
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | Lower | 2050 | 90
307 Hotdisc | Hotdisc |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1 | Upper | 2050 | 98
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2020 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2030 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2040 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | ctrl | 2050 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Lower | 2030 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Upper | 2030 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Lower | 2050 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1 | Upper | 2050 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2020 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2030 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2040 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | ctrl | 2050 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Lower | 2030 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Upper | 2030 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Lower | 2050 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1 | Upper | 2050 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2020 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2030 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2040 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2050 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2030 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2030 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2050 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2050 | 4
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2020 | 20
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2030 | 20
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2040 | 20
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | ctrl | 2050 | 20
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Lower | 2030 | 20
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Upper | 2030 | 30
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Lower | 2050 | 20
307 Hotdisc | Hotdisc |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 1 | Upper | 2050 | 30
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2020 | 0.75
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2030 | 0.75
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2040 | 0.75
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2050 | 0.75
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2030 | 0.75
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2030 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2050 | 0.75
307 Hotdisc | Hotdisc |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2050 | 1
307 Hotdisc | Hotdisc |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2020 | 10
307 Hotdisc | Hotdisc |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2030 | 10
307 Hotdisc | Hotdisc |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2040 | 10
307 Hotdisc | Hotdisc |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2050 | 10
307 Hotdisc | Hotdisc |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0
307 Hotdisc | Hotdisc |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | B | 1 | ctrl | 2020 | 54
307 Hotdisc | Hotdisc |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | B | 1 | ctrl | 2030 | 54
307 Hotdisc | Hotdisc |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | B | 1 | ctrl | 2040 | 54
307 Hotdisc | Hotdisc |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | B | 1 | ctrl | 2050 | 54
307 Hotdisc | Hotdisc |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2020 | 8.3
307 Hotdisc | Hotdisc |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2030 | 8.3
307 Hotdisc | Hotdisc |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2040 | 8.3
307 Hotdisc | Hotdisc |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2050 | 8.3
307 Hotdisc | Hotdisc |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2020 | 0.29
307 Hotdisc | Hotdisc |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2030 | 0.29
307 Hotdisc | Hotdisc |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2040 | 0.29
307 Hotdisc | Hotdisc |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 | C | 2 | ctrl | 2050 | 0.29
307 Hotdisc | Hotdisc |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2020 | 56
307 Hotdisc | Hotdisc |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2030 | 45
307 Hotdisc | Hotdisc |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2040 | 28
307 Hotdisc | Hotdisc |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2050 | 11
307 Hotdisc | Hotdisc |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2020 | 0.1
307 Hotdisc | Hotdisc |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2030 | 0.1
307 Hotdisc | Hotdisc |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2040 | 0.1
307 Hotdisc | Hotdisc |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2050 | 0.1
307 Hotdisc | Hotdisc |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2020 | 1
307 Hotdisc | Hotdisc |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2030 | 1
307 Hotdisc | Hotdisc |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2040 | 1
307 Hotdisc | Hotdisc |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 | C | 3 | ctrl | 2050 | 1
307 Hotdisc | Hotdisc |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D |  | ctrl | 2020 | 0.5
307 Hotdisc | Hotdisc |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D |  | ctrl | 2030 | 0.465
307 Hotdisc | Hotdisc |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D |  | ctrl | 2040 | 0.485
307 Hotdisc | Hotdisc |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D |  | ctrl | 2050 | 0.45
307 Hotdisc | Hotdisc |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  |  | ctrl | 2020 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  |  | ctrl | 2030 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  |  | ctrl | 2040 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  |  | ctrl | 2050 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  |  | ctrl | 2020 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  |  | ctrl | 2030 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  |  | ctrl | 2040 | 50
307 Hotdisc | Hotdisc |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  |  | ctrl | 2050 | 50
307 Hotdisc | Hotdisc |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2020 | 400
307 Hotdisc | Hotdisc |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2030 | 400
307 Hotdisc | Hotdisc |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2040 | 400
307 Hotdisc | Hotdisc |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2050 | 400
307 Hotdisc | Hotdisc |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 1.175
307 Hotdisc | Hotdisc |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 1.195
307 Hotdisc | Hotdisc |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 1.205
307 Hotdisc | Hotdisc |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 1.205
307 Hotdisc | Hotdisc |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 0.73
307 Hotdisc | Hotdisc |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 0.75
307 Hotdisc | Hotdisc |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 0.76
307 Hotdisc | Hotdisc |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 0.76
307 Hotdisc | Hotdisc |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 0.445
307 Hotdisc | Hotdisc |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 0.445
307 Hotdisc | Hotdisc |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 0.445
307 Hotdisc | Hotdisc |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 0.445
307 Hotdisc | Hotdisc |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2020 | 0.18
307 Hotdisc | Hotdisc |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2030 | 0.18
307 Hotdisc | Hotdisc |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2040 | 0.18
307 Hotdisc | Hotdisc |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2050 | 0.18
307 Hotdisc | Hotdisc |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 | F | 4,5 | ctrl | 2020 | 90
307 Hotdisc | Hotdisc |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 | F | 4,5 | ctrl | 2030 | 90
307 Hotdisc | Hotdisc |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 | F | 4,5 | ctrl | 2040 | 90
307 Hotdisc | Hotdisc |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 | F | 4,5 | ctrl | 2050 | 90
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2020 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2030 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2040 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2050 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2030 | 0.01
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2030 | 0.2
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2050 | 0.01
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2050 | 0.2
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | ctrl | 2020 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | ctrl | 2030 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | ctrl | 2040 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | ctrl | 2050 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | Lower | 2030 | 85
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | Upper | 2030 | 100
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | Lower | 2050 | 85
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 2 | Upper | 2050 | 100
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2020 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2030 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2040 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2050 | 95
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Lower | 2030 | 85
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Upper | 2030 | 100
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Lower | 2050 | 85
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Upper | 2050 | 100
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 0.2
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 0.2
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2020 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2030 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2040 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2050 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2030 | 0.2
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2050 | 0.2
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2020 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2040 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2030 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2050 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 30
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 30
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 30
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 30
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 20
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 35
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 20
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 35
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2020 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2030 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2040 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2050 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Lower | 2030 | 0.05
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Upper | 2030 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Lower | 2050 | 0.05
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Upper | 2050 | 0.1
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 5 | ctrl | 2020 | 10
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 5 | ctrl | 2030 | 10
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 5 | ctrl | 2040 | 10
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 5 | ctrl | 2050 | 10
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2020 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2040 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2020 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2040 | 0
308 Dielectric heating | Dielectric heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
308 Dielectric heating | Dielectric heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 6,7,8 | ctrl | 2020 | 2.7
308 Dielectric heating | Dielectric heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 6,7,8 | ctrl | 2030 | 2.619
308 Dielectric heating | Dielectric heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 6,7,8 | ctrl | 2040 | 2.538
308 Dielectric heating | Dielectric heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 6,7,8 | ctrl | 2050 | 2.43
308 Dielectric heating | Dielectric heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 9 | ctrl | 2020 | 85
308 Dielectric heating | Dielectric heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 9 | ctrl | 2030 | 85
308 Dielectric heating | Dielectric heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 9 | ctrl | 2040 | 85
308 Dielectric heating | Dielectric heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 9 | ctrl | 2050 | 85
308 Dielectric heating | Dielectric heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 9 | ctrl | 2020 | 15
308 Dielectric heating | Dielectric heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 9 | ctrl | 2030 | 15
308 Dielectric heating | Dielectric heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 9 | ctrl | 2040 | 15
308 Dielectric heating | Dielectric heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 9 | ctrl | 2050 | 15
308 Dielectric heating | Dielectric heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2020 | 0
308 Dielectric heating | Dielectric heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2030 | 0
308 Dielectric heating | Dielectric heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2040 | 0
308 Dielectric heating | Dielectric heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2050 | 0
308 Dielectric heating | Dielectric heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 45.823
308 Dielectric heating | Dielectric heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 45.825
308 Dielectric heating | Dielectric heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 45.826
308 Dielectric heating | Dielectric heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 45.826
308 Dielectric heating | Dielectric heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E |  | ctrl | 2020 | 0.073
308 Dielectric heating | Dielectric heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E |  | ctrl | 2030 | 0.075
308 Dielectric heating | Dielectric heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E |  | ctrl | 2040 | 0.076
308 Dielectric heating | Dielectric heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E |  | ctrl | 2050 | 0.076
308 Dielectric heating | Dielectric heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 6 | ctrl | 2020 | 45.75
308 Dielectric heating | Dielectric heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 6 | ctrl | 2030 | 45.75
308 Dielectric heating | Dielectric heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 6 | ctrl | 2040 | 45.75
308 Dielectric heating | Dielectric heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 6 | ctrl | 2050 | 45.75
308 Dielectric heating | Dielectric heating |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2020 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2030 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2040 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | ctrl | 2050 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2030 | 0.01
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2030 | 0.2
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Lower | 2050 | 0.01
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 1 | Upper | 2050 | 0.2
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | ctrl | 2020 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | ctrl | 2030 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | ctrl | 2040 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | ctrl | 2050 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | Lower | 2030 | 90
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | Upper | 2030 | 100
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | Lower | 2050 | 90
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B,C | 2 | Upper | 2050 | 100
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2020 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2030 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2040 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | ctrl | 2050 | 96
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Lower | 2030 | 90
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Upper | 2030 | 100
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Lower | 2050 | 90
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  |  | Upper | 2050 | 100
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 0.2
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 0.2
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2020 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2030 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2040 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2050 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2030 | 0.2
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2050 | 0.2
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2020 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2040 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2030 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2050 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 30
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 30
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 30
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 30
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 20
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 35
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 20
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 35
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2020 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2030 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2040 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | ctrl | 2050 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Lower | 2030 | 0.05
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Upper | 2030 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Lower | 2050 | 0.05
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 3 | Upper | 2050 | 0.1
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | D |  | ctrl | 2020 | 10
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | D |  | ctrl | 2030 | 10
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | D |  | ctrl | 2040 | 10
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | D |  | ctrl | 2050 | 10
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0
309 Infrared (IR) | Infrared heating |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
309 Infrared (IR) | Infrared heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 1 | ctrl | 2020 | 0.35
309 Infrared (IR) | Infrared heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 1 | ctrl | 2030 | 0.34
309 Infrared (IR) | Infrared heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 1 | ctrl | 2040 | 0.33
309 Infrared (IR) | Infrared heating |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 1 | ctrl | 2050 | 0.315
309 Infrared (IR) | Infrared heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 2 | ctrl | 2020 | 85
309 Infrared (IR) | Infrared heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 2 | ctrl | 2030 | 85
309 Infrared (IR) | Infrared heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 2 | ctrl | 2040 | 85
309 Infrared (IR) | Infrared heating |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 | E | 2 | ctrl | 2050 | 85
309 Infrared (IR) | Infrared heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | E | 2 | ctrl | 2020 | 15
309 Infrared (IR) | Infrared heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | E | 2 | ctrl | 2030 | 15
309 Infrared (IR) | Infrared heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | E | 2 | ctrl | 2040 | 15
309 Infrared (IR) | Infrared heating |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 | E | 2 | ctrl | 2050 | 15
309 Infrared (IR) | Infrared heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2020 | 0
309 Infrared (IR) | Infrared heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2030 | 0
309 Infrared (IR) | Infrared heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2040 | 0
309 Infrared (IR) | Infrared heating |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  |  | ctrl | 2050 | 0
309 Infrared (IR) | Infrared heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 117.073
309 Infrared (IR) | Infrared heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 117.075
309 Infrared (IR) | Infrared heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 117.076
309 Infrared (IR) | Infrared heating |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 117.076
309 Infrared (IR) | Infrared heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F |  | ctrl | 2020 | 0.073
309 Infrared (IR) | Infrared heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F |  | ctrl | 2030 | 0.075
309 Infrared (IR) | Infrared heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F |  | ctrl | 2040 | 0.076
309 Infrared (IR) | Infrared heating |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | F |  | ctrl | 2050 | 0.076
309 Infrared (IR) | Infrared heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | G | 1 | ctrl | 2020 | 117
309 Infrared (IR) | Infrared heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | G | 1 | ctrl | 2030 | 117
309 Infrared (IR) | Infrared heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | G | 1 | ctrl | 2040 | 117
309 Infrared (IR) | Infrared heating |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | G | 1 | ctrl | 2050 | 117
309 Infrared (IR) | Infrared heating |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2030 | 100
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2050 | 100
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2030 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2050 | 99
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2020 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2030 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2040 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2050 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2030 | 0.1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2030 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2050 | 0.1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2050 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2020 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2030 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2040 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2050 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2030 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2030 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2050 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2050 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 0.2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 20
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 20
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2020 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2030 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2040 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2050 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2030 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2030 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2050 | 0.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2050 | 1
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2020 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2030 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2040 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2050 | 2
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0.03
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0.03
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0.03
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0.03
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0.17
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0.17
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0.17
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0.17
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2020 | 0.21296
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2030 | 0.18634
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2040 | 0.18634
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2050 | 0.18634
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2, 4 | ctrl | 2020 | 75
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2, 4 | ctrl | 2030 | 75
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2, 4 | ctrl | 2040 | 75
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2, 4 | ctrl | 2050 | 75
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2, 4 | ctrl | 2020 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2, 4 | ctrl | 2030 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2, 4 | ctrl | 2040 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2, 4 | ctrl | 2050 | 25
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2020 | 1230.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2030 | 1173
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2040 | 1115.5
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2050 | 1058
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 0.94
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 0.92313
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 0.90126
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 0.87439
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2020 | 0.365
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2030 | 0.375
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2040 | 0.38
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2050 | 0.38
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2020 | 0.575
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2030 | 0.54813
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2040 | 0.52126
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2050 | 0.49439
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2020 | 0.055556
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2030 | 0.048611
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2040 | 0.048611
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2050 | 0.048611
310.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 60
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 60
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2030 | 100
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2050 | 100
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2030 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2050 | 99
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2020 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2030 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2040 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2050 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2030 | 0.1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2030 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2050 | 0.1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2050 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2020 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2030 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2040 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2050 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2030 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2030 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2050 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2050 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 0.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 25
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 25
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 25
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 25
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 20
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 25
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 20
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 25
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2020 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2030 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2040 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2050 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2030 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2030 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2050 | 0.5
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2050 | 1
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2020 | 2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2030 | 2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2040 | 2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 2 | ctrl | 2050 | 2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0.03
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0.03
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0.03
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0.03
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0.17
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0.17
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0.17
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0.17
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2020 | 0.095556
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2030 | 0.083611
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2040 | 0.083611
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2050 | 0.083611
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2020 | 85
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2030 | 85
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2040 | 85
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2050 | 85
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2020 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2030 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2040 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2050 | 15
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2020 | 1107.45
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2030 | 1055.7
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2040 | 1003.95
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 2,3,4 | ctrl | 2050 | 952.2
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 0.8825
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 0.86832
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 0.84914
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 0.82495
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2020 | 0.365
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2030 | 0.375
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2040 | 0.38
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2050 | 0.38
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2020 | 0.5175
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2030 | 0.49332
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2040 | 0.46914
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2050 | 0.44495
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2020 | 0.017645
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2030 | 0.01544
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2040 | 0.01544
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2050 | 0.01544
310.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2030 | 100
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2050 | 100
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2030 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2050 | 99
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2020 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2030 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2040 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2050 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2030 | 0.1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2030 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2050 | 0.1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2050 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2020 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2030 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2040 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2050 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2030 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2030 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2050 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2050 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2020 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2030 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2040 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2050 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2030 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2030 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2050 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2050 | 0.2
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 20
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 20
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2020 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2030 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2040 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2050 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2030 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2030 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2050 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2050 | 1
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2020 | 5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2030 | 5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2040 | 5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2050 | 5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0.008
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0.008
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0.008
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0.008
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0.08
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0.08
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0.08
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0.08
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2020 | 0.18634
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2030 | 0.15972
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2040 | 0.15972
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2050 | 0.15972
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2020 | 75
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2030 | 75
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2040 | 75
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2050 | 75
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2020 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2030 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2040 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2050 | 25
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2020 | 1070
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2030 | 1020
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2040 | 970
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1 | ctrl | 2050 | 920
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 0.865
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 0.85164
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 0.83327
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 0.80991
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2020 | 0.365
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2030 | 0.375
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2040 | 0.38
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2050 | 0.38
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2020 | 0.5
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2030 | 0.47664
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2040 | 0.45327
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2050 | 0.42991
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2020 | 0.093171
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2030 | 0.079861
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2040 | 0.079861
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2050 | 0.079861
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2020 | 0.048611
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2030 | 0.041667
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2040 | 0.041667
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2050 | 0.041667
310.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2020 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2030 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2040 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | ctrl | 2050 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2030 | 5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2030 | 60
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Lower | 2050 | 5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A |  | Upper | 2050 | 60
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2030 | 100
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 1,2 | Upper | 2050 | 100
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2020 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2030 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2040 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | ctrl | 2050 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2030 | 98
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2030 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Lower | 2050 | 98
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 1,2 | Upper | 2050 | 99
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2020 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2030 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2040 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | ctrl | 2050 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2030 | 0.1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2030 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Lower | 2050 | 0.1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 1,2 | Upper | 2050 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2020 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2030 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2040 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | ctrl | 2050 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2030 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2030 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Lower | 2050 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 1,2 | Upper | 2050 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2020 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2030 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2040 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | ctrl | 2050 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2030 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2030 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Lower | 2050 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 1 | Upper | 2050 | 0.2
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2020 | 25
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2030 | 25
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2040 | 25
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | ctrl | 2050 | 25
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2030 | 20
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2030 | 25
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Lower | 2050 | 20
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2 | Upper | 2050 | 25
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2020 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2030 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2040 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | ctrl | 2050 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2030 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2030 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Lower | 2050 | 0.5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 1 | Upper | 2050 | 1
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2020 | 5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2030 | 5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2040 | 5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 1 | ctrl | 2050 | 5
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0.008
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0.008
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0.008
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0.008
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2020 | 0.08
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2030 | 0.08
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2040 | 0.08
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 1 | ctrl | 2050 | 0.08
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2020 | 0.083611
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2030 | 0.071667
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2040 | 0.071667
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B,C | 1,2,4 | ctrl | 2050 | 0.071667
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2020 | 85
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2030 | 85
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2040 | 85
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 2 | ctrl | 2050 | 85
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2020 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2030 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2040 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 2 | ctrl | 2050 | 15
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1,2,4 | ctrl | 2020 | 963
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1,2,4 | ctrl | 2030 | 918
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1,2,4 | ctrl | 2040 | 873
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 1,2,4 | ctrl | 2050 | 828
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2020 | 0.815
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2030 | 0.80397
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2040 | 0.78794
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  |  | ctrl | 2050 | 0.76692
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2020 | 0.365
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2030 | 0.375
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2040 | 0.38
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D |  | ctrl | 2050 | 0.38
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2020 | 0.45
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2030 | 0.42897
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2040 | 0.40794
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 2,3,4 | ctrl | 2050 | 0.38692
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2020 | 0.041806
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2030 | 0.035833
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2040 | 0.035833
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2050 | 0.035833
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2020 | 0.01544
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2030 | 0.013234
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2040 | 0.013234
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | Additional investments cost for 12-16 bar boilers (M€ per MW) | M€ per MW | 2019 |  |  | ctrl | 2050 | 0.013234
310.2b Electric boiler hot wate | Electric boiler, 10 kV, hot water, 1-12 bar |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2020 | 20
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2030 | 20
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2040 | 20
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2050 | 20
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Lower | 2030 | 1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Upper | 2030 | 50
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Lower | 2050 | 1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Upper | 2050 | 50
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 90
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 90
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 91
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 92
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 88
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 91.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 88
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 93.84
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 89
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 89
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 90
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 91
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 87
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 90.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 87
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 92.84
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2020 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2030 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2040 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2050 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2030 | 1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2030 | 1.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2050 | 1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2050 | 1.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2020 | 1.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2030 | 1.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2040 | 1.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2050 | 1.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2030 | 0.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2030 | 2.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2050 | 0.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2050 | 2.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2020 | 0.9
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2030 | 0.9
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2040 | 0.9
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2050 | 0.9
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2030 | 0.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2030 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2050 | 0.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2050 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.1a Steam boiler Coal | Steam boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2020 | 8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2030 | 8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2040 | 8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2050 | 8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 2.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 2.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 2.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 2.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 35
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 35
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 35
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 35
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 1.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 1.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 0.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 0.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 0.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 0.8
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2020 | 0.5
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2030 | 0.46576
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2040 | 0.446
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2050 | 0.44046
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 33700
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 32600
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 31600
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 30600
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.903
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.925
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.936
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.936
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2020 | 0.803
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2030 | 0.825
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2040 | 0.836
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2050 | 0.836
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.1
311.1a Steam boiler Coal | Steam boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.1a Steam boiler Coal | Steam boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.1a Steam boiler Coal | Steam boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.1a Steam boiler Coal | Steam boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 95
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 96
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 97
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 97
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 90
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 98
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 90
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 98
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 94
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 95
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 96
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 96
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 89
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 97
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 89
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 97
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2020 | 0.14
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2030 | 0.12
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2040 | 0.11
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2050 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2030 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2030 | 0.14
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2050 | 0.08
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2050 | 0.12
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2020 | 1.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2030 | 1.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2040 | 1.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2050 | 1.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2030 | 0.09
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2030 | 2.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2050 | 0.09
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2050 | 2.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2020 | 0.6
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2030 | 0.6
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2040 | 0.6
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2050 | 0.6
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2030 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2030 | 0.8
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2050 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2050 | 0.8
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.1b Steam boiler Oil | Steam boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2020 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2030 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2040 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2050 | 0.5
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 0.1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 25
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 20
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 18
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 15
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 0
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2020 | 0.055
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2030 | 0.046576
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2040 | 0.0446
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2050 | 0.044046
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 1800
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 1700
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 1600
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 1500
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.9
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.9
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.9
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2020 | 0.1022
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2030 | 0.09
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2040 | 0.0836
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2050 | 0.076
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 0.8978
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.81
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.8164
311.1b Steam boiler Oil | Steam boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.824
311.1b Steam boiler Oil | Steam boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.1b Steam boiler Oil | Steam boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.1b Steam boiler Oil | Steam boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.1b Steam boiler Oil | Steam boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 93
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 94
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 94
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 95
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 90
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 96
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 90
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 97
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 92
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 93
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 93
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 94
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 89
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 95
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 89
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 96
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 0.14
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 0.12
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 0.11
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 0.14
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0.08
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 0.12
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2020 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2030 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2040 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2050 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2030 | 0.08
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2030 | 2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2050 | 0.08
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2050 | 2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2020 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2030 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2040 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2050 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2030 | 0.3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2030 | 0.6
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2050 | 0.3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2050 | 0.6
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 25
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 25
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2020 | 0.3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2030 | 0.3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2040 | 0.3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2050 | 0.3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 0.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 9
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 7
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 6
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 2
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2020 | 0.054545
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2030 | 0.045455
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2040 | 0.045455
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2050 | 0.045455
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 2000
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 1900
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 1800
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 1700
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2020 | 0.1022
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2030 | 0.09
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2040 | 0.0836
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2050 | 0.076
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 0.9978
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.91
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.9164
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.924
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.1c Steam boiler Gas | Steam boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2020 | 103
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2030 | 104
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2040 | 104
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2050 | 104
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Lower | 2030 | 95
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Upper | 2030 | 106
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Lower | 2050 | 96
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Upper | 2050 | 107
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 101
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 103
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 103
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 103
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 94
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 105
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 95
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 106
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 0.14
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 0.12
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 0.11
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 0.14
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0.08
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 0.12
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2020 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2030 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2040 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2050 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2030 | 0.08
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2030 | 2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2050 | 0.08
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2050 | 2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2020 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2030 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2040 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2050 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2030 | 0.3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2030 | 0.6
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2050 | 0.3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2050 | 0.6
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2020 | 0.3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2030 | 0.3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2040 | 0.3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2050 | 0.3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 0.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 9
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 7
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 6
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 2
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2020 | 0.06
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2030 | 0.05
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2040 | 0.05
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2050 | 0.05
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 65
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 65
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 65
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 65
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 35
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 35
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 35
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 35
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 2000
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 1900
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 1800
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 1700
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2020 | 0.1022
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2030 | 0.09
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2040 | 0.0836
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2050 | 0.076
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 0.9978
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.91
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.9164
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.924
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.1d Steam boiler Gas cond | Steam boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 91
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 89
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 92
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 93
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 89
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 89
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 89
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 88
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 91
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 89
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 92
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2020 | 2.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2030 | 2.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2040 | 2.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2050 | 2.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2030 | 2.2
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2030 | 2.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2050 | 1.8
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2050 | 2.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2020 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2030 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2040 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2050 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2030 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2030 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2050 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2050 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2020 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2030 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2040 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2050 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2030 | 2.6
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2030 | 3.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2050 | 2.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2050 | 3.8
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 35
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 35
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 1.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 1.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 20
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.5
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2020 | 11
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2030 | 11
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2040 | 11
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2050 | 11
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 10
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 10
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 10
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 10
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 63
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 49
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 46
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 41
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 11
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 8
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 4
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 3
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H,I | 3,10 | ctrl | 2020 | 0.61818
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H,I | 3,10 | ctrl | 2030 | 0.59091
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H,I | 3,10 | ctrl | 2040 | 0.56364
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H,I | 3,10 | ctrl | 2050 | 0.53636
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | I | 3 | ctrl | 2020 | 33700
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | I | 3 | ctrl | 2030 | 35900
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | I | 3 | ctrl | 2040 | 34800
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | I | 3 | ctrl | 2050 | 33700
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 2.779
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 2.825
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 2.848
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 2.848
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J | 3 | ctrl | 2020 | 1.679
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J | 3 | ctrl | 2030 | 1.725
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J | 3 | ctrl | 2040 | 1.748
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | J | 3 | ctrl | 2050 | 1.748
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.1
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.1e Steam boiler Wood | Steam boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2020 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2030 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2040 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2050 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Lower | 2030 | 88
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Upper | 2030 | 117
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Lower | 2050 | 88
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Upper | 2050 | 117
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2020 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2030 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2040 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2050 | 116.1896
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Lower | 2030 | 88
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Upper | 2030 | 117
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Lower | 2050 | 88
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Upper | 2050 | 117
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2020 | 2.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2030 | 2.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2040 | 2.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2050 | 2.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Lower | 2030 | 2.2
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Upper | 2030 | 2.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Lower | 2050 | 1.8
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Upper | 2050 | 2.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2020 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2030 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2040 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2050 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Lower | 2030 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Upper | 2030 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Lower | 2050 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Upper | 2050 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2020 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2030 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2040 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2050 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Lower | 2030 | 2.6
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Upper | 2030 | 3.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Lower | 2050 | 2.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Upper | 2050 | 3.8
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 35
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 35
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 1.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 1.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 20
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.5
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2020 | 11
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2030 | 11
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2040 | 11
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2050 | 11
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 10
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 10
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 10
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 10
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 63
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 49
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 46
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 41
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 11
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 8
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 4
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 3
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G,H | 3,10 | ctrl | 2020 | 0.68
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G,H | 3,10 | ctrl | 2030 | 0.65
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G,H | 3,10 | ctrl | 2040 | 0.62
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G,H | 3,10 | ctrl | 2050 | 0.59
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 65
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 65
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 65
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 65
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 35
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 35
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 35
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 35
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2020 | 37000
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2030 | 35900
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2040 | 34800
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2050 | 33700
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 2.779
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 2.825
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 2.848
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 2.848
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2020 | 1.679
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2030 | 1.725
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2040 | 1.748
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2050 | 1.748
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.1
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.1f Steam boiler Wood cond | Steam boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2020 | 20
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2030 | 20
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2040 | 20
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | ctrl | 2050 | 20
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Lower | 2030 | 1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Upper | 2030 | 50
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Lower | 2050 | 1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3 | Upper | 2050 | 50
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 91
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 92
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 88
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 91.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 88
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 92.92
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 89
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 89
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 91
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 87
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 90.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 87
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 91.92
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2020 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2030 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2040 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2050 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Lower | 2030 | 1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Upper | 2030 | 1.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Lower | 2050 | 1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Upper | 2050 | 1.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2020 | 1.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2030 | 1.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2040 | 1.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2050 | 1.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Lower | 2030 | 0.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Upper | 2030 | 2.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Lower | 2050 | 0.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Upper | 2050 | 2.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2020 | 0.9
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2030 | 0.9
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2040 | 0.9
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2050 | 0.9
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Lower | 2030 | 0.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Upper | 2030 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Lower | 2050 | 0.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Upper | 2050 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2020 | 8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2030 | 8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2040 | 8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2050 | 8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 2.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 2.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 2.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 2.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 35
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 35
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 35
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 35
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 1.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 1.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 0.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 0.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 0.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 0.8
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F | 3,10 | ctrl | 2020 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F | 3,10 | ctrl | 2030 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F | 3,10 | ctrl | 2040 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F | 3,10 | ctrl | 2050 | 0.5
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 33700
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 32600
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 31600
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 30600
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.903
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.925
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.936
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.936
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2020 | 0.803
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2030 | 0.825
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2040 | 0.836
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | G | 3 | ctrl | 2050 | 0.836
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.1
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2020 | 0.035
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2030 | 0.03
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2040 | 0.03
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | H |  | ctrl | 2050 | 0.03
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.2a Hot water boiler, Coal | Hot water boiler, Coal |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 96
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 97
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 98
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 98
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 90
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 98
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 90
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 98
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 95
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 96
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 97
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 97
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 89
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 97
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 89
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 97
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2020 | 0.14
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2030 | 0.12
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2040 | 0.11
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2050 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2030 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2030 | 0.14
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2050 | 0.08
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2050 | 0.12
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2020 | 1.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2030 | 1.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2040 | 1.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2050 | 1.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2030 | 0.09
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2030 | 2.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2050 | 0.09
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2050 | 2.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2020 | 0.6
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2030 | 0.6
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2040 | 0.6
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2050 | 0.6
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2030 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2030 | 0.8
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2050 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2050 | 0.8
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2020 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2030 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2040 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2050 | 0.5
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 0.1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 25
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 20
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 18
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 15
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 0
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2020 | 0.044
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2030 | 0.037261
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2040 | 0.03568
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2050 | 0.035236
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 1800
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 1700
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 1600
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 1500
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.9
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.9
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.9
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2020 | 0.1022
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2030 | 0.09
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2040 | 0.0836
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2050 | 0.076
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 0.8978
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.81
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.8164
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.824
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2020 | 0.035
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2030 | 0.03
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2040 | 0.03
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2050 | 0.03
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.2b Hot water boiler Oil | Hot water boiler, Oil |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 94
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 95
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 95
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 96
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 90
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 96
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 90
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 98
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 93
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 94
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 94
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 95
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 89
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 95
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 89
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 97
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 0.14
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 0.12
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 0.11
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 0.14
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0.08
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 0.12
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2020 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2030 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2040 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2050 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2030 | 0.08
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2030 | 2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2050 | 0.08
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2050 | 2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2020 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2030 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2040 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2050 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2030 | 0.3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2030 | 0.6
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2050 | 0.3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2050 | 0.6
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 25
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 25
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2020 | 0.3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2030 | 0.3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2040 | 0.3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | C | 3, 9 | ctrl | 2050 | 0.3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 0.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 9
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 7
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 6
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 2
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2020 | 0.043636
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2030 | 0.036364
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2040 | 0.036364
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | D | 3,10 | ctrl | 2050 | 0.036364
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 2000
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 1900
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 1800
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 1700
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2020 | 0.1022
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2030 | 0.09
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2040 | 0.0836
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | E | 3 | ctrl | 2050 | 0.076
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 0.9978
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.91
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.9164
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.924
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | F |  | ctrl | 2020 | 0.035
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | F |  | ctrl | 2030 | 0.03
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | F |  | ctrl | 2040 | 0.03
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | F |  | ctrl | 2050 | 0.03
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.2c Hot water boiler Gas | Hot water boiler, Natural gas or biogas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2020 | 103
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2030 | 104
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2040 | 104
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | ctrl | 2050 | 104
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Lower | 2030 | 95
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Upper | 2030 | 106
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Lower | 2050 | 96
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 |  | 5,6,7,8,10 | Upper | 2050 | 107
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 101
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 103
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 103
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 103
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 94
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 105
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 95
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 106
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2020 | 0.14
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2030 | 0.12
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2040 | 0.11
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | ctrl | 2050 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2030 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2030 | 0.14
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Lower | 2050 | 0.08
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 3 | Upper | 2050 | 0.12
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2020 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2030 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2040 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | ctrl | 2050 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2030 | 0.08
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2030 | 2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Lower | 2050 | 0.08
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 3 | Upper | 2050 | 2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2020 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2030 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2040 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | ctrl | 2050 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2030 | 0.3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2030 | 0.6
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Lower | 2050 | 0.3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 3 | Upper | 2050 | 0.6
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 30
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 30
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 0.5
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 0.5
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 0.5
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 0.5
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 0.7
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 0.7
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 15
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 15
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 15
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 15
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.4
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2020 | 0.3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2030 | 0.3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2040 | 0.3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | B | 3, 9 | ctrl | 2050 | 0.3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 0.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 9
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 7
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 6
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 2
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2020 | 0.048
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2030 | 0.04
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2040 | 0.04
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | C | 3,10 | ctrl | 2050 | 0.04
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 65
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 65
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 65
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 65
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 35
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 35
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 35
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 35
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2020 | 2000
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2030 | 1900
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2040 | 1800
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 |  | 3 | ctrl | 2050 | 1700
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2020 | 0.1022
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2030 | 0.09
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2040 | 0.0836
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 3 | ctrl | 2050 | 0.076
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 0.9978
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 0.91
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 0.9164
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 0.924
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2020 | 0.035
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2030 | 0.03
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2040 | 0.03
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | E |  | ctrl | 2050 | 0.03
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.d Hot water boiler Gas cond | Hot water boiler, Natural gas or biogas (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2020 | 91
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2030 | 91
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2040 | 91
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | ctrl | 2050 | 92
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2030 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2030 | 93
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Lower | 2050 | 91
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | B | 5,6,7,8 | Upper | 2050 | 94
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2020 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2030 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2040 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | ctrl | 2050 | 91
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2030 | 89
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2030 | 92
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Lower | 2050 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 |  | 5,6,7,8 | Upper | 2050 | 93
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2020 | 2.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2030 | 2.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2040 | 2.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | ctrl | 2050 | 2.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2030 | 2.2
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2030 | 2.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Lower | 2050 | 1.8
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | C | 3 | Upper | 2050 | 2.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2020 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2030 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2040 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | ctrl | 2050 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2030 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2030 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Lower | 2050 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | D | 3 | Upper | 2050 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2020 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2030 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2040 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | ctrl | 2050 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2030 | 2.6
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2030 | 3.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Lower | 2050 | 2.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | D | 3 | Upper | 2050 | 3.8
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 35
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 35
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 1.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 1.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 20
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.5
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2020 | 11
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2030 | 11
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2040 | 11
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | E | 3, 9 | ctrl | 2050 | 11
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 10
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 10
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 10
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 10
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 63
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 49
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 46
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 41
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 11
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 8
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 4
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 3
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2020 | 0.61818
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2030 | 0.59091
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2040 | 0.56364
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | F,G,H | 3,10 | ctrl | 2050 | 0.53636
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 60
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 60
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 60
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 60
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 40
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 40
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 40
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 40
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2020 | 33700
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2030 | 35900
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2040 | 34800
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | H | 3 | ctrl | 2050 | 33700
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 2.779
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 2.825
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 2.848
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 2.848
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2020 | 1.679
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2030 | 1.725
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2040 | 1.748
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | I | 3 | ctrl | 2050 | 1.748
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.1
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2020 | 0.035
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2030 | 0.03
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2040 | 0.03
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | J |  | ctrl | 2050 | 0.03
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.2e Hot water boiler Wood | Hot water boiler, Wood Chips |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2020 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2030 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2040 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | ctrl | 2050 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2030 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2030 | 50
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Lower | 2050 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 | A | 3, 10 | Upper | 2050 | 50
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2020 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2030 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2040 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | ctrl | 2050 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Lower | 2030 | 88
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Upper | 2030 | 117
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Lower | 2050 | 88
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | L,M | 11 | Upper | 2050 | 117
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2020 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2030 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2040 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | ctrl | 2050 | 116.1896
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Lower | 2030 | 88
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Upper | 2030 | 117
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Lower | 2050 | 88
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | L,M | 11 | Upper | 2050 | 117
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2020 | 2.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2030 | 2.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2040 | 2.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | ctrl | 2050 | 2.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Lower | 2030 | 2.2
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Upper | 2030 | 2.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Lower | 2050 | 1.8
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 3 | Upper | 2050 | 2.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2020 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2030 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2040 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | ctrl | 2050 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Lower | 2030 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Upper | 2030 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Lower | 2050 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | C | 3 | Upper | 2050 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2020 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2030 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2040 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | ctrl | 2050 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Lower | 2030 | 2.6
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Upper | 2030 | 3.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Lower | 2050 | 2.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | C | 3 | Upper | 2050 | 3.8
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2020 | 25
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2030 | 25
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2040 | 25
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | ctrl | 2050 | 25
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2030 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2030 | 35
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Lower | 2050 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 3,5,8 | Upper | 2050 | 35
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2020 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2030 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2040 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | ctrl | 2050 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2030 | 0.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2030 | 1.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Lower | 2050 | 0.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  |  | Upper | 2050 | 1.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2020 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2030 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2040 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 3 | ctrl | 2050 | 20
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2020 | 0.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2030 | 0.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2040 | 0.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 3 | ctrl | 2050 | 0.5
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2020 | 11
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2030 | 11
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2040 | 11
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 | D | 3, 9 | ctrl | 2050 | 11
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2020 | 10
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2030 | 10
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2040 | 10
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 9 | ctrl | 2050 | 10
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 63
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 49
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 46
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 41
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 11
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 8
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 6
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 4
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2020 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2030 | 3
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2040 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 3, 9 | ctrl | 2050 | 1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G | 3,10 | ctrl | 2020 | 0.68
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G | 3,10 | ctrl | 2030 | 0.65
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G | 3,10 | ctrl | 2040 | 0.62
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E,F,G | 3,10 | ctrl | 2050 | 0.59
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2020 | 65
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2030 | 65
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2040 | 65
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 3 | ctrl | 2050 | 65
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2020 | 35
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2030 | 35
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2040 | 35
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 3 | ctrl | 2050 | 35
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | G | 3 | ctrl | 2020 | 37000
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | G | 3 | ctrl | 2030 | 35900
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | G | 3 | ctrl | 2040 | 34800
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | G | 3 | ctrl | 2050 | 33700
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 2.779
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 2.825
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 2.848
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 2.848
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H | 3 | ctrl | 2020 | 1.679
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H | 3 | ctrl | 2030 | 1.725
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H | 3 | ctrl | 2040 | 1.748
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | H | 3 | ctrl | 2050 | 1.748
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2020 | 1.1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2030 | 1.1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2040 | 1.1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 |  | 3 | ctrl | 2050 | 1.1
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | I |  | ctrl | 2020 | 0.035
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | I |  | ctrl | 2030 | 0.03
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | I |  | ctrl | 2040 | 0.03
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | Indirect investments cost (M€ per MW) | M€ per MW | 2019 | I |  | ctrl | 2050 | 0.03
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2020 | 90
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2030 | 90
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2040 | 90
311.2fHot waterboiler Wood cond | Hot water boiler, Wood chips (Condensing) |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 3 | ctrl | 2050 | 90
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | ctrl | 2020 | 2.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | ctrl | 2030 | 2.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | ctrl | 2040 | 2.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | ctrl | 2050 | 2.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | Lower | 2030 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | Upper | 2030 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | Lower | 2050 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 2 | Upper | 2050 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2020 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2030 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2040 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2050 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Lower | 2030 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Upper | 2030 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Lower | 2050 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Upper | 2050 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2020 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2030 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2040 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2050 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Lower | 2030 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Upper | 2030 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Lower | 2050 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Upper | 2050 | 100
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | ctrl | 2020 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | ctrl | 2030 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | ctrl | 2040 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | ctrl | 2050 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | Lower | 2030 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | Upper | 2030 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | Lower | 2050 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 |  | 8, 9 | Upper | 2050 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2020 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2030 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2040 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2050 | 0.25
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2030 | 0
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2030 | 0.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2050 | 0
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2050 | 0.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2020 | 0.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2030 | 0.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2040 | 0.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | ctrl | 2050 | 0.5
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2030 | 0
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2030 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Lower | 2050 | 0
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 2 | Upper | 2050 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 15
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 15
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 15
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 15
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 20
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 20
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2020 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2030 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2040 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | ctrl | 2050 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Lower | 2030 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Upper | 2030 | 0.04
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Lower | 2050 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 2 | Upper | 2050 | 0.04
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2020 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2030 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2040 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2050 | 10
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2020 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2030 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2040 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 2 | ctrl | 2050 | 0.01
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2020 | 0.3
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2030 | 0.3
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2040 | 0.3
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2050 | 0.3
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2020 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2030 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2040 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | PM2.5 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2050 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2020 | 9
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2030 | 7
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2040 | 6
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | NOX (g per GJ fuel) | NOX (g per GJ fuel) | NOX (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2050 | 6
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2020 | 3
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2030 | 2
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2040 | 2
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | CH4 (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2050 | 2
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2020 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2030 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2040 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | N2O (g per GJ fuel) | N2O (g per GJ fuel) | N2O (g per GJ fuel) | g per GJ fuel | 2019 |  | 1 | ctrl | 2050 | 1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B | 4, 7 | ctrl | 2020 | 0.015
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B | 4, 7 | ctrl | 2030 | 0.015
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B | 4, 7 | ctrl | 2040 | 0.015
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | B | 4, 7 | ctrl | 2050 | 0.015
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2020 | 66.6667
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2030 | 66.6667
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2040 | 66.6667
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2050 | 66.6667
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2020 | 33.3333
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2030 | 33.3333
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2040 | 33.3333
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2050 | 33.3333
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2020 | 181.8182
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2030 | 177.2727
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2040 | 172.7273
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2050 | 154.5455
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2020 | 0.2825
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2030 | 0.2775
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2040 | 0.28
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 1 | ctrl | 2050 | 0.28
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2020 | 0.1825
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2030 | 0.1875
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2040 | 0.19
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2050 | 0.19
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 1 | ctrl | 2020 | 0.1
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 1 | ctrl | 2030 | 0.09
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 1 | ctrl | 2040 | 0.09
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 1 | ctrl | 2050 | 0.09
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2020 | 90
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2030 | 90
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2040 | 90
312.a Direct firing Natural Gas | Direct Firing, Natural Gas |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2050 | 90
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | ctrl | 2020 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | ctrl | 2030 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | ctrl | 2040 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | ctrl | 2050 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | Lower | 2030 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | Upper | 2030 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | Lower | 2050 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  |  | Upper | 2050 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2020 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2030 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2040 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2050 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Lower | 2030 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Upper | 2030 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Lower | 2050 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Upper | 2050 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2020 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2030 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2040 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2050 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Lower | 2030 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Upper | 2030 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Lower | 2050 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Upper | 2050 | 100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | ctrl | 2020 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | ctrl | 2030 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | ctrl | 2040 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | ctrl | 2050 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | Lower | 2030 | 0.1
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | Upper | 2030 | 1
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | Lower | 2050 | 0.1
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 8, 9 | Upper | 2050 | 1
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2020 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2030 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2040 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | ctrl | 2050 | 0.25
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2030 | 0
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2030 | 0.5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Lower | 2050 | 0
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 |  | 2 | Upper | 2050 | 0.5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | ctrl | 2020 | 3.5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | ctrl | 2030 | 3.5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | ctrl | 2040 | 3.5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | ctrl | 2050 | 3.5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | Lower | 2030 | 2
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | Upper | 2030 | 5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | Lower | 2050 | 2
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 |  | 4 | Upper | 2050 | 5
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | ctrl | 2020 | 15
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | ctrl | 2030 | 15
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | ctrl | 2040 | 15
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | ctrl | 2050 | 15
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | Lower | 2030 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | Upper | 2030 | 20
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | Lower | 2050 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 2, 4 | Upper | 2050 | 20
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | ctrl | 2020 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | ctrl | 2030 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | ctrl | 2040 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | ctrl | 2050 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | Lower | 2030 | 0.001
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | Upper | 2030 | 0.015
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | Lower | 2050 | 0.001
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 | I | 2, 4 | Upper | 2050 | 0.015
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2020 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2030 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2040 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 |  | 6 | ctrl | 2050 | 10
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2020 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2030 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2040 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2050 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2020 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2030 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2040 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 | F | 2 | ctrl | 2050 | 0.01
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Depends on Fuel Mix
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E, G, H | 4, 7 | ctrl | 2020 | 0.22
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E, G, H | 4, 7 | ctrl | 2030 | 0.22
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E, G, H | 4, 7 | ctrl | 2040 | 0.22
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E, G, H | 4, 7 | ctrl | 2050 | 0.22
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2020 | 66.6667
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2030 | 66.6667
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2040 | 66.6667
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 7 | ctrl | 2050 | 66.6667
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2020 | 33.3333
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2030 | 33.3333
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2040 | 33.3333
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 7 | ctrl | 2050 | 33.3333
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2020 | 3400
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2030 | 3300
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2040 | 3200
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | C | 2, 1 | ctrl | 2050 | 3100
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 7 | ctrl | 2020 | 0.3253
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 7 | ctrl | 2030 | 0.3303
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 7 | ctrl | 2040 | 0.3328
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 7 | ctrl | 2050 | 0.3328
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2020 | 0.1825
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2030 | 0.1875
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2040 | 0.19
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 7 | ctrl | 2050 | 0.19
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 7 | ctrl | 2020 | 0.1428
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 7 | ctrl | 2030 | 0.1428
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 7 | ctrl | 2040 | 0.1428
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | C | 7 | ctrl | 2050 | 0.1428
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2020 | 90
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2030 | 90
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2040 | 90
312.b Direct firing Sold Fuels | Direct Firing Solid Fuels |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  | 5 | ctrl | 2050 | 90
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | ctrl | 2020 | 5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | ctrl | 2030 | 5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | ctrl | 2040 | 5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | ctrl | 2050 | 5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | Lower | 2030 | 1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | Upper | 2030 | 10
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | Lower | 2050 | 1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | Heat generation capacity for one unit (MW) | MW | 2019 |  | 4 | Upper | 2050 | 10
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2020 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2030 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2040 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | ctrl | 2050 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Lower | 2030 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Upper | 2030 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Lower | 2050 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | Total efficiency, net (%), nominel load | % | 2019 | A | 2 | Upper | 2050 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2020 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2030 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2040 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | ctrl | 2050 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Lower | 2030 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Upper | 2030 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Lower | 2050 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | Total efficiency, net (%), annual average | % | 2019 | A | 2 | Upper | 2050 | 100
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | ctrl | 2020 | 0.25
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | ctrl | 2030 | 0.25
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | ctrl | 2040 | 0.25
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | ctrl | 2050 | 0.25
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | Lower | 2030 | 0.1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | Upper | 2030 | 1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | Lower | 2050 | 0.1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | Auxiliary electricity consumption (% of heat gen) | % of heat gen | 2019 | B | 6, 7 | Upper | 2050 | 1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | ctrl | 2020 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | ctrl | 2030 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | ctrl | 2040 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | ctrl | 2050 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | Lower | 2030 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | Upper | 2030 | 0.5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | Lower | 2050 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Forced outage (%) | Forced outage (%) | Forced outage (%) | % | 2019 | F | 4 | Upper | 2050 | 0.5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | ctrl | 2020 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | ctrl | 2030 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | ctrl | 2040 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | ctrl | 2050 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | Lower | 2030 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | Upper | 2030 | 1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | Lower | 2050 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Planned outage (weeks per year) | Planned outage (weeks per year) | Planned outage (weeks per year) | weeks per year | 2019 | F | 4 | Upper | 2050 | 1
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2020 | 12.5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2030 | 12.5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2040 | 12.5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | ctrl | 2050 | 12.5
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2030 | 10
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2030 | 15
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Lower | 2050 | 10
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Technical lifetime (years) | Technical lifetime (years) | Technical lifetime (years) | years | 2019 |  | 4 | Upper | 2050 | 15
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | ctrl | 2020 | 0.04
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | ctrl | 2030 | 0.04
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | ctrl | 2040 | 0.04
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | ctrl | 2050 | 0.04
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | Lower | 2030 | 0.02
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | Upper | 2030 | 0.06
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | Lower | 2050 | 0.02
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Construction time (years) | Construction time (years) | Construction time (years) | years | 2019 |  | 5 | Upper | 2050 | 0.06
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 4 | ctrl | 2020 | 15
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 4 | ctrl | 2030 | 15
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 4 | ctrl | 2040 | 15
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Minimum load (% of full load) | Minimum load (% of full load) | Minimum load (% of full load) | % of full load | 2019 | C | 4 | ctrl | 2050 | 15
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2020 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2030 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2040 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Warm start-up time (hours) | Warm start-up time (hours) | Warm start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2050 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2020 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2030 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2040 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Energy/technical data | Cold start-up time (hours) | Cold start-up time (hours) | Cold start-up time (hours) | hours | 2019 |  | 5 | ctrl | 2050 | 0.01
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | SO2 (g per GJ fuel) | g per GJ fuel | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 4, 5 | ctrl | 2020 | 0.06
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 4, 5 | ctrl | 2030 | 0.06
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 4, 5 | ctrl | 2040 | 0.06
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | Nominal investment (M€ per MW) | M€ per MW | 2019 | E | 4, 5 | ctrl | 2050 | 0.06
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 5 | ctrl | 2020 | 66.6667
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 5 | ctrl | 2030 | 66.6667
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 5 | ctrl | 2040 | 66.6667
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which equipment (%) | - of which equipment (%) | - of which equipment (%) | % | 2019 |  | 5 | ctrl | 2050 | 66.6667
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 5 | ctrl | 2020 | 33.3333
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 5 | ctrl | 2030 | 33.3333
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 5 | ctrl | 2040 | 33.3333
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which installation (%) | - of which installation (%) | - of which installation (%) | % | 2019 |  | 5 | ctrl | 2050 | 33.3333
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | F | 4 | ctrl | 2020 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | F | 4 | ctrl | 2030 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | F | 4 | ctrl | 2040 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | Fixed O&M (€/MJ/s/year) | €/MJ/s/year | 2019 | F | 4 | ctrl | 2050 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 5 | ctrl | 2020 | 0.1825
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 5 | ctrl | 2030 | 0.1875
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 5 | ctrl | 2040 | 0.19
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | Variable O&M (€/MWh) | Variable O&M (€/MWh) | Variable O&M (€/MWh) | €/MWh | 2019 |  | 2, 5 | ctrl | 2050 | 0.19
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 5 | ctrl | 2020 | 0.1825
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 5 | ctrl | 2030 | 0.1875
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 5 | ctrl | 2040 | 0.19
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | - of which is electricity costs (€/MWh) | €/MWh | 2019 | D | 5 | ctrl | 2050 | 0.19
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 4 | ctrl | 2020 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 4 | ctrl | 2030 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 4 | ctrl | 2040 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Environment | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | - of which is other O&M costs (€/MWh) | €/MWh | 2019 | F | 4 | ctrl | 2050 | 0
312.c Direct firing Electricity | Direct Firing, Electricity |  | Technology specific data | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | Carbon capture removal of CO2 emissions (% of emission) | % of emission | 2019 |  |  | ctrl | 2020 | Cf. the utilized electricity

## Ref
technology | description
301.1a heat pump 60 C 40 K | 1. Viegand Maagøe, 2019.
301.1a heat pump 60 C 40 K | 2. Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
301.1a heat pump 60 C 40 K | 3. EHPA, Large Scale heat pumps in Europe, 2019
301.1a heat pump 60 C 40 K | 4. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
301.1a heat pump 60 C 40 K | 5. http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
301.1a heat pump 60 C 40 K | 6. Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
301.1b heat pump 70 C 50 K | 1. Viegand Maagøe, 2019.
301.1b heat pump 70 C 50 K | 2. Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
301.1b heat pump 70 C 50 K | 3. EHPA, Large Scale heat pumps in Europe, 2019
301.1b heat pump 70 C 50 K | 4. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
301.1b heat pump 70 C 50 K | 5. http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
301.1b heat pump 70 C 50 K | 6. Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
301.1c heat pump 80 C 60 K | 1. Viegand Maagøe, 2019.
301.1c heat pump 80 C 60 K | 2. Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
301.1c heat pump 80 C 60 K | 3. EHPA, Large Scale heat pumps in Europe, 2019
301.1c heat pump 80 C 60 K | 4. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
301.1c heat pump 80 C 60 K | 5. http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
301.1c heat pump 80 C 60 K | 6. Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
301.2 heat_cool hp 80 C 75 K | 1. Viegand Maagøe, 2019.
301.2 heat_cool hp 80 C 75 K | 2. Energistyrelsen, Technological data for energy plants (Compressions Heat Pumps for DH), 2017
301.2 heat_cool hp 80 C 75 K | 3. EHPA, Large Scale heat pumps in Europe, 2019
301.2 heat_cool hp 80 C 75 K | 4. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
301.2 heat_cool hp 80 C 75 K | 5. Pieper, H. et al., Allocation of investment costs for large-scale heat pumps supplying district heating, 2018
301.2 heat_cool hp 80 C 75 K | 6. http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
301.2 heat_cool hp 80 C 75 K | 7. Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
302.a High temp. hp Up to 125 C | 1. Viegand Maagøe, 2019
302.a High temp. hp Up to 125 C | 2. http://www.planenergi.dk/varmepumper/.
302.a High temp. hp Up to 125 C | 3. Teknologisk instutut, Hybridvarmepumpe til fjernvarme, 2018
302.a High temp. hp Up to 125 C | 4. Energiforskning, Højtemperatur varmepumper kan bruge lavtemperatur spildvarme, 2013
302.a High temp. hp Up to 125 C | 5. Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
302.b High temp. hp Up to 150 | 1. Viegand Maagøe, 2019
302.b High temp. hp Up to 150 | 2. http://www.planenergi.dk/varmepumper/.
302.b High temp. hp Up to 150 | 3. Teknologisk instutut, Hybridvarmepumpe til fjernvarme, 2018
302.b High temp. hp Up to 150 | 4. Energiforskning, Højtemperatur varmepumper kan bruge lavtemperatur spildvarme, 2013
302.b High temp. hp Up to 150 | 5. Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
303 Booster hp 150 C 130 K | 1. https://www.sciencedirect.com/topics/engineering/partial-load
303 Booster hp 150 C 130 K | 2. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
303 Booster hp 150 C 130 K | 3. Van der Spek, et. Al., Challenges and uncertainties of ex ante techno-economic analysis of low TRL CO2 capture technology: Lessons from a case study of an NGCC with exhaust gas recycle and electric swing adsorption, 2017
304 Heat driven hp 80 C | 1. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
304 Heat driven hp 80 C | 2. Viegand Maagøe, 2019.
305 MVR 5 K | 1. Viegand Maagøe, MVR, 2018
305 MVR 5 K | 2. Technological data for energi plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
305 MVR 5 K | 3. Viegand Maagøe, 2019
305 MVR 5 K | 4. EPCON, EVAPORATION TECHNOLOGY, 2019
305 MVR 5 K | 5. EPCON investment cost offer, 2017.
306 Thermal gasification | 1. Viegand Maagøe, Thermal Gasification Direct in Process v01, 2018
306 Thermal gasification | 2. Dall Energy, Correspondance 2019
306 Thermal gasification | 3. IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
307 Hotdisc | 1. FLSmidth, Personal communication, 2019
307 Hotdisc | 2. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
307 Hotdisc | 3. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
307 Hotdisc | 4. European Commision, The potential for CCS and CCU in Europe, 2019
307 Hotdisc | 5. Sampo Kour, et Al., The potential for CCUS in selected industrial sectors – summary ofconcept evaluations in Finland, 2017
308 Dielectric heating | 1. Thermex Thermatron, https://thermex-thermatron.com/industrial-microwave-generators/, 2019
308 Dielectric heating | 2. Technological Institute, https://www.dti.dk/industrial-microwave-processing/
308 Dielectric heating | 3. Viegand Maagøe, 2019
308 Dielectric heating | 4. Cellencor, https://www.cellencor.com, 2019
308 Dielectric heating | 5. Bi.Elle, http://www.microwaves.it/ing/company.htm, 2019
308 Dielectric heating | 6. A.M. Hasna, Microwave Processing Applications in Chemical Engineering: Cost Analysis, 2011
308 Dielectric heating | 7. Tony Koral, Considerations for Commercial Success, 2013 in new RF and Microwave Industrial Heating Applications
308 Dielectric heating | 8. Bi.Elle, Personal communication, 2019
308 Dielectric heating | 9. Beyond Zero Emissions Inc, Zero Carbon Industry Plan Electrifying Industry, 2018
309 Infrared (IR) | 1. Netek IR System A/S, Personal communication, 2019
309 Infrared (IR) | 2. Beyond Zero Emissions Inc, Zero Carbon Industry Plan Electrifying Industry, 2018
309 Infrared (IR) | 3. Viegand Maagøe, 2019
309 Infrared (IR) | 4. IG Infrared, https://www.ig-infrared.com, 2019
309 Infrared (IR) | 5. American Society of. Heating, Refrigerating and Air-Conditioning Engineers, ASHRAE Handbook – Heating, Ventilating, and Air-Conditioning Systems and Equipment (I-P Edition), 2008
310.1a Electric boiler steam | 1. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
310.1a Electric boiler steam | 2. AS:scan, Personal communication, 2022
310.1a Electric boiler steam | 3. Tjæreborg Industri, Personal communication, 2019
310.1a Electric boiler steam | 4. Nordheat, Personal communication, 2022
310.1b Electric boiler steam | 1. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
310.1b Electric boiler steam | 2. AS:scan, Personal communication, 2022
310.1b Electric boiler steam | 3. Tjæreborg Industri, Personal communication, 2022
310.1b Electric boiler steam | 4. Nordheat, Personal communication, 2022
310.2a Electric boiler hot wate | 1. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
310.2a Electric boiler hot wate | 2. AS:scan, Personal communication, 2022
310.2a Electric boiler hot wate | 3. Tjæreborg Industri, Personal communication, 2019
310.2a Electric boiler hot wate | 4. Nordheat, Personal communication, 2022
310.2b Electric boiler hot wate | 1. Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
310.2b Electric boiler hot wate | 2. AS:scan, Personal communication, 2022
310.2b Electric boiler hot wate | 3. Tjæreborg Industri, Personal communication, 2022
310.2b Electric boiler hot wate | 4. Nordheat, Personal communication, 2022
311.1a Steam boiler Coal | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1a Steam boiler Coal | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.1a Steam boiler Coal | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.1a Steam boiler Coal | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.1a Steam boiler Coal | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.1a Steam boiler Coal | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.1a Steam boiler Coal | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1a Steam boiler Coal | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.1a Steam boiler Coal | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.1a Steam boiler Coal | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.1b Steam boiler Oil | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1b Steam boiler Oil | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.1b Steam boiler Oil | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.1b Steam boiler Oil | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.1b Steam boiler Oil | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.1b Steam boiler Oil | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.1b Steam boiler Oil | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1b Steam boiler Oil | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.1b Steam boiler Oil | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.1b Steam boiler Oil | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.1c Steam boiler Gas | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1c Steam boiler Gas | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.1c Steam boiler Gas | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.1c Steam boiler Gas | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.1c Steam boiler Gas | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.1c Steam boiler Gas | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.1c Steam boiler Gas | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1c Steam boiler Gas | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.1c Steam boiler Gas | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.1c Steam boiler Gas | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.1d Steam boiler Gas cond | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1d Steam boiler Gas cond | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.1d Steam boiler Gas cond | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.1d Steam boiler Gas cond | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.1d Steam boiler Gas cond | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.1d Steam boiler Gas cond | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.1d Steam boiler Gas cond | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1d Steam boiler Gas cond | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.1d Steam boiler Gas cond | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.1d Steam boiler Gas cond | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.1e Steam boiler Wood | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1e Steam boiler Wood | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.1e Steam boiler Wood | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.1e Steam boiler Wood | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.1e Steam boiler Wood | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.1e Steam boiler Wood | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.1e Steam boiler Wood | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1e Steam boiler Wood | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.1e Steam boiler Wood | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.1e Steam boiler Wood | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.1f Steam boiler Wood cond | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1f Steam boiler Wood cond | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.1f Steam boiler Wood cond | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.1f Steam boiler Wood cond | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.1f Steam boiler Wood cond | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.1f Steam boiler Wood cond | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.1f Steam boiler Wood cond | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.1f Steam boiler Wood cond | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.1f Steam boiler Wood cond | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.1f Steam boiler Wood cond | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.1f Steam boiler Wood cond | 11. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. Used for estimation of the efficiency for technology "09a Wood Chips HOP" heat only boilers, woodchips 6W in the Technology Data - Energy Plants for Electricity and District heating generation, version 0007 January 2020
311.2a Hot water boiler, Coal | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2a Hot water boiler, Coal | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.2a Hot water boiler, Coal | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.2a Hot water boiler, Coal | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.2a Hot water boiler, Coal | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.2a Hot water boiler, Coal | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.2a Hot water boiler, Coal | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2a Hot water boiler, Coal | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.2a Hot water boiler, Coal | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.2a Hot water boiler, Coal | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.2b Hot water boiler Oil | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2b Hot water boiler Oil | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.2b Hot water boiler Oil | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.2b Hot water boiler Oil | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.2b Hot water boiler Oil | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.2b Hot water boiler Oil | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.2b Hot water boiler Oil | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2b Hot water boiler Oil | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.2b Hot water boiler Oil | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.2b Hot water boiler Oil | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.2c Hot water boiler Gas | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2c Hot water boiler Gas | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.2c Hot water boiler Gas | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.2c Hot water boiler Gas | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.2c Hot water boiler Gas | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.2c Hot water boiler Gas | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.2c Hot water boiler Gas | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2c Hot water boiler Gas | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.2c Hot water boiler Gas | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.2c Hot water boiler Gas | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.d Hot water boiler Gas cond | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.d Hot water boiler Gas cond | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.d Hot water boiler Gas cond | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.d Hot water boiler Gas cond | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.d Hot water boiler Gas cond | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.d Hot water boiler Gas cond | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.d Hot water boiler Gas cond | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.d Hot water boiler Gas cond | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.d Hot water boiler Gas cond | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.d Hot water boiler Gas cond | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.2e Hot water boiler Wood | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2e Hot water boiler Wood | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.2e Hot water boiler Wood | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.2e Hot water boiler Wood | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.2e Hot water boiler Wood | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.2e Hot water boiler Wood | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.2e Hot water boiler Wood | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2e Hot water boiler Wood | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.2e Hot water boiler Wood | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.2e Hot water boiler Wood | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.2fHot waterboiler Wood cond | 1. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2fHot waterboiler Wood cond | 2. Danish Energy Agency, Heating installations, 2016 (updated 2018).
311.2fHot waterboiler Wood cond | 3. Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
311.2fHot waterboiler Wood cond | 4. Applied Technologies of New York, Steam vs hot water boiler, 2016.
311.2fHot waterboiler Wood cond | 5. ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
311.2fHot waterboiler Wood cond | 6. Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
311.2fHot waterboiler Wood cond | 7. Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
311.2fHot waterboiler Wood cond | 8. EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
311.2fHot waterboiler Wood cond | 9. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
311.2fHot waterboiler Wood cond | 10. Tjærborg Industri, Olie og gas kedler, 2019
311.2fHot waterboiler Wood cond | 11. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. Used for estimation of the efficiency for technology "09a Wood Chips HOP" heat only boilers, woodchips 6W in the Technology Data - Energy Plants for Electricity and District heating generation, version 0007 January 2020
312.a Direct firing Natural Gas | 1. Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
312.a Direct firing Natural Gas | 2. Viegand Maagøe, Direct Firing, 2018
312.a Direct firing Natural Gas | 3. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
312.a Direct firing Natural Gas | 4. Milton Megatherm, Correspondance 2019
312.a Direct firing Natural Gas | 5. IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
312.a Direct firing Natural Gas | 6. Eclipse, Vortometric Burner Series Datasheet 128-3, 20/2/2015
312.a Direct firing Natural Gas | 7. Viegand Maagøe assessment, 2019
312.a Direct firing Natural Gas | 8. Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
312.a Direct firing Natural Gas | 9. Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
312.b Direct firing Sold Fuels | 1. Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
312.b Direct firing Sold Fuels | 2. Viegand Maagøe, Direct Firing, 2018
312.b Direct firing Sold Fuels | 3. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
312.b Direct firing Sold Fuels | 4. FLSmidth - Burner & PLM for HOTDISC, Correspondance 2019
312.b Direct firing Sold Fuels | 5. IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
312.b Direct firing Sold Fuels | 6. FCT International Burners, Correspondance 2019.
312.b Direct firing Sold Fuels | 7. Viegand Maagøe assessment, 2019
312.b Direct firing Sold Fuels | 8. Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
312.b Direct firing Sold Fuels | 9. Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
312.c Direct firing Electricity | 1. Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
312.c Direct firing Electricity | 2. Viegand Maagøe, Direct Firing, 2018
312.c Direct firing Electricity | 3. Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
312.c Direct firing Electricity | 4. SAN Electro Heat A/S , Correspondance 2019
312.c Direct firing Electricity | 5. Viegand Maagøe assessment, 2019
312.c Direct firing Electricity | 6. Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
312.c Direct firing Electricity | 7. Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010

## Notes
technology | description
301.1a heat pump 60 C 40 K | A. 0,5-5 MW
301.1a heat pump 60 C 40 K | B. Estimated based on cases presented in [3]
301.1a heat pump 60 C 40 K | C. Based on lost produktion during startup/shutdown
301.1a heat pump 60 C 40 K | D. May vary depending on heat source availability
301.1a heat pump 60 C 40 K | E. Very individual, can vary ÷ 20 %
301.1a heat pump 60 C 40 K | F. Very individual, can vary + 20 %
301.1a heat pump 60 C 40 K | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
301.1a heat pump 60 C 40 K | H. Going from current implementation to potential
301.1a heat pump 60 C 40 K | I. Uses waste heat
301.1b heat pump 70 C 50 K | A. 0,5-5 MW
301.1b heat pump 70 C 50 K | B. Estimated based on cases presented in [3]
301.1b heat pump 70 C 50 K | C. Based on lost produktion during startup/shutdown
301.1b heat pump 70 C 50 K | D. May vary depending on heat source availability
301.1b heat pump 70 C 50 K | E. Very individual, can vary ÷ 20 %
301.1b heat pump 70 C 50 K | F. Very individual, can vary + 20 %
301.1b heat pump 70 C 50 K | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
301.1b heat pump 70 C 50 K | H. Going from current implementation to potential
301.1b heat pump 70 C 50 K | I. Uses waste heat
301.1c heat pump 80 C 60 K | A. 0,5-5 MW
301.1c heat pump 80 C 60 K | B. Estimated based on cases presented in [3]
301.1c heat pump 80 C 60 K | C. Based on lost produktion during startup/shutdown
301.1c heat pump 80 C 60 K | D. May vary depending on heat source availability
301.1c heat pump 80 C 60 K | E. Very individual, can vary ÷ 20 %
301.1c heat pump 80 C 60 K | F. Very individual, can vary + 20 %
301.1c heat pump 80 C 60 K | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
301.1c heat pump 80 C 60 K | H. Going from current implementation to potential
301.1c heat pump 80 C 60 K | I. Uses waste heat
301.2 heat_cool hp 80 C 75 K | A. 0,5-5 MW
301.2 heat_cool hp 80 C 75 K | B. Estimated based on cases presented in [3]
301.2 heat_cool hp 80 C 75 K | C. Manufacturer software calculations
301.2 heat_cool hp 80 C 75 K | D. Based on lost production during startup/shutdown
301.2 heat_cool hp 80 C 75 K | E. May vary depending on heat source
301.2 heat_cool hp 80 C 75 K | F. Very individual, can vary ÷ 20 %
301.2 heat_cool hp 80 C 75 K | G. Very individual, can vary + 20 %
301.2 heat_cool hp 80 C 75 K | H. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
301.2 heat_cool hp 80 C 75 K | I. Going from simple implementation to potential
301.2 heat_cool hp 80 C 75 K | J. Not relevant to this technology
301.2 heat_cool hp 80 C 75 K | K. Process cooling
302.a High temp. hp Up to 125 C | A. 0,5-5 MW
302.a High temp. hp Up to 125 C | B. Calculated from start-up loss
302.a High temp. hp Up to 125 C | C. May vary depending on heat source availability
302.a High temp. hp Up to 125 C | D. Slightly higher than large heat pumps [11]
302.a High temp. hp Up to 125 C | E. Theoretically as low as 10 %. For screw as low as 25 %, lower than that will affect the performance drastically.
302.a High temp. hp Up to 125 C | F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
302.a High temp. hp Up to 125 C | G. Going from current implementation to potential
302.a High temp. hp Up to 125 C | H. Uses waste heat
302.b High temp. hp Up to 150 | A. 0,5-5 MW
302.b High temp. hp Up to 150 | B. Calculated from start-up loss
302.b High temp. hp Up to 150 | C. May vary depending on heat source availability
302.b High temp. hp Up to 150 | D. Slightly higher than large heat pumps [11]
302.b High temp. hp Up to 150 | E. Theoretically as low as 10 %. For screw as low as 25 %, lower than that will affect the performance drastically.
302.b High temp. hp Up to 150 | F. Corrected to technology readiness level (Not commercially avaiable at the moment)
302.b High temp. hp Up to 150 | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
302.b High temp. hp Up to 150 | H. Going from current implementation to potential
302.b High temp. hp Up to 150 | I. Uses waste heat
303 Booster hp 150 C 130 K | A. 1-15 MW
303 Booster hp 150 C 130 K | B. Utilising waste heat above 30 °C will increase COP. Waste heat up to 75 °C can be utilised
303 Booster hp 150 C 130 K | C. Calculated from manufacturer software and manufacturer offer.
303 Booster hp 150 C 130 K | D. Based on lost production during startup/shutdown
303 Booster hp 150 C 130 K | E. Assumed similar to electrical compression heat pump and mechanical vapor recompression technologies
303 Booster hp 150 C 130 K | F. Assumed similar to high temperature heat pump technologies
303 Booster hp 150 C 130 K | G. From [2], cost correlations and learing curves [3] (Not commercially avaiable at the moment)
303 Booster hp 150 C 130 K | H. Very individual, can vary ÷ 10 %
303 Booster hp 150 C 130 K | I. Very individual, can vary + 10 %
303 Booster hp 150 C 130 K | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
303 Booster hp 150 C 130 K | K. Assumed 10 % higher than electrical compression heat pump. The turbo compressors have low O&M
303 Booster hp 150 C 130 K | L. Going from simple implementation to potential
303 Booster hp 150 C 130 K | M. Not relevant to this technology
303 Booster hp 150 C 130 K | N. Uses waste heat
304 Heat driven hp 80 C | A. 1-30 MW
304 Heat driven hp 80 C | B. A single unit is roughly limited to 6 MW, due to size, but the units are often connected to one unit at the site. Giving the possibility for larger capacities.
304 Heat driven hp 80 C | C. Based on lost production during startup/shutdown
304 Heat driven hp 80 C | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
304 Heat driven hp 80 C | E. Not relevant to this technology
304 Heat driven hp 80 C | F. Only relevant if heat source are process cooling
305 MVR 5 K | A. 5-50 MW
305 MVR 5 K | B. Assumed temperature lift of 5 K (saturation temperatur)
305 MVR 5 K | C. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
305 MVR 5 K | D. Not relevant
306 Thermal gasification | A. The efficiency of the thermal gasifier is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
306 Thermal gasification | B. Parameter based on current prices, since the technology is still not mature a 25% reduction is expected over the next 30 years. Projections have been carried out by Viegand Maagøe.
306 Thermal gasification | C. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
306 Thermal gasification | D. If the unit is used at temperatures above 1000 °C additional costs has to be introduced as wear on the insulation will increase.
306 Thermal gasification | E. Prices include both gasifier, biomass storage and direct firing unit.
306 Thermal gasification | F. The indirect costs will be too strong a function of the process to put into a single value across all industries.
307 Hotdisc | A. 10-100 MW
307 Hotdisc | B. 36-72 hours
307 Hotdisc | C. Assumed equal to waste used in incineration power plant
307 Hotdisc | D. Includes retrofit to existing system
307 Hotdisc | E. If a rebuillt of the system is necessary, this cost need to be included. E.g. if a cement oven is a separate line and not inline system.
307 Hotdisc | F. Typically engineered to remove 80-90 %, above 95 % is possible
307 Hotdisc | G. The fuel is waste and the waste needs minimum pre-handling. Large pieces of waste can be fired directly in the Hotdisc. Cost of waste will be lower than at an inceration plant
308 Dielectric heating | A. 0,01-0,2 MW
308 Dielectric heating | B. Cooling system account for a small loss
308 Dielectric heating | C. The capacity is often specifically regulated to product flow
308 Dielectric heating | D. Can vary quite significantly, as different applications requires different additional subsystems.
308 Dielectric heating | E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
308 Dielectric heating | F. The magnatron (microwave generator) has a lifetime of around 10.000 hours of operation. Replacement of magnatron are included here.
308 Dielectric heating | G. Not relevant
308 Dielectric heating | H. Infrared will have non energy gains, but it has not been possible to estimate.
308 Dielectric heating | I. Treatment times are up to 20 times faster than traditional systems.
309 Infrared (IR) | A. 0,01-0,2 MW
309 Infrared (IR) | B. The electricity to heat efficiency is 100 %, but not all of the electricity is converted to radiant energy [5]
309 Infrared (IR) | C. A part of the electricity is conveted to convective heat, and some of it is lost to surrounding.
309 Infrared (IR) | D. A system often consist of mulitiple emitters, giving the possiblity in turn emitters off individually.
309 Infrared (IR) | E. Can vary quite significantly, as different applications requires different additional subsystems.
309 Infrared (IR) | F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
309 Infrared (IR) | G. The emitters have a lifetime of 10.000 to 15.000 hours of operation. Replacement of emitters are included here.
309 Infrared (IR) | H. Not relevant
309 Infrared (IR) | I. Infrared will have non energy gains, but it has not been possible to estimate.
309 Infrared (IR) | J. Heating time is 7 to 40 times faster than convective ovens. Uptake much less space which enable possible expansion.
310.1a Electric boiler steam | A. 1-5 MW
310.1a Electric boiler steam | B. Electrode boilers at low voltage typically needs a transformer from distribution grid. Costs for the transformer are included in the equipment costs.
310.1a Electric boiler steam | C. Investment cost is slightly higher than for a hot water boiler.
310.1a Electric boiler steam | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
310.1a Electric boiler steam | E. Not relevant to this technology
310.1b Electric boiler steam | A. 5-60 MW
310.1b Electric boiler steam | B. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
310.1b Electric boiler steam | C. Investment cost is slightly higher than for a hot water boiler.
310.1b Electric boiler steam | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
310.1b Electric boiler steam | E. Not relevant to this technology
310.2a Electric boiler hot wate | A. 1-5 MW
310.2a Electric boiler hot wate | B. Electrode boilers at low voltage typically needs a transformer from distribution grid. Costs for the transformer are included in the equipment costs.
310.2a Electric boiler hot wate | C. Investment cost is slightly lower than for a steam boiler.
310.2a Electric boiler hot wate | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
310.2a Electric boiler hot wate | E. Going from current implementation to potential
310.2b Electric boiler hot wate | A. 5-60 MW
310.2b Electric boiler hot wate | B. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
310.2b Electric boiler hot wate | C. Investment cost is slightly lower than for a steam boiler.
310.2b Electric boiler hot wate | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
310.2b Electric boiler hot wate | E. Going from current implementation to potential
311.1a Steam boiler Coal | A. Only a few plant of this type is in operation in Denmark. Nordic Suger operates a 33 MW - which is considered above average
311.1a Steam boiler Coal | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.1a Steam boiler Coal | C. Assumed slightly higher than gas boiler
311.1a Steam boiler Coal | D. Estimated based on gas boiler and coal CHP plant
311.1a Steam boiler Coal | E. Will be reduced if carbon capture in installed
311.1a Steam boiler Coal | F. Viegand Maagøe A/S experience
311.1a Steam boiler Coal | G. Future cost prediction is based on average cost development of other similar technologies.
311.1a Steam boiler Coal | H. 20 %-point lower for hot water boiler
311.1a Steam boiler Coal | I. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.1a Steam boiler Coal | J. Not relevant to this technology
311.1b Steam boiler Oil | A. Only a few plant of this type is in operation in Denmark. Tjærborg Industri have boiler range up to 50 MW
311.1b Steam boiler Oil | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.1b Steam boiler Oil | C. Assumed equal to gasboiler
311.1b Steam boiler Oil | D. Estimated based on gas boiler and coal CHP plant
311.1b Steam boiler Oil | E. Will be reduced if carbon capture in installed
311.1b Steam boiler Oil | F. Viegand Maagøe A/S experience
311.1b Steam boiler Oil | G. Future cost prediction is based on average cost development of other similar technologies.
311.1b Steam boiler Oil | H. 20 %-point lower for hot water boiler
311.1b Steam boiler Oil | I. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.1b Steam boiler Oil | J. Not relevant to this technology
311.1c Steam boiler Gas | A. Ranges from 0,5 to 50. Typical value of 20 MW
311.1c Steam boiler Gas | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.1c Steam boiler Gas | C. Will be reduced if carbon capture in installed
311.1c Steam boiler Gas | D. 20 %-point lower for hot water boiler
311.1c Steam boiler Gas | E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.1c Steam boiler Gas | F. Not relevant to this technology
311.1d Steam boiler Gas cond | A. Ranges from 0,5 to 50. Typical value of 20 MW
311.1d Steam boiler Gas cond | B. Will be reduced if carbon capture in installed
311.1d Steam boiler Gas cond | C. 20 %-point lower for hot water boiler
311.1d Steam boiler Gas cond | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.1d Steam boiler Gas cond | E. Not relevant to this technology
311.1e Steam boiler Wood | A. Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
311.1e Steam boiler Wood | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.1e Steam boiler Wood | C. Assumed slightly higher than gas boiler
311.1e Steam boiler Wood | D. Estimated based on gas boiler and wood CHP plant
311.1e Steam boiler Wood | E. Will be reduced if carbon capture in installed
311.1e Steam boiler Wood | F. Viegand Maagøe A/S experience
311.1e Steam boiler Wood | G. Future cost prediction is based on average cost development of other similar technologies.
311.1e Steam boiler Wood | H. 20 %-point lower for hot water boiler
311.1e Steam boiler Wood | I. 5 % higher for wood pellet
311.1e Steam boiler Wood | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.1e Steam boiler Wood | K. Not relevant to this technology
311.1f Steam boiler Wood cond | A. Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
311.1f Steam boiler Wood cond | B. Assumed slightly higher than gas boiler
311.1f Steam boiler Wood cond | C. Estimated based on gas boiler and wood CHP plant
311.1f Steam boiler Wood cond | D. Will be reduced if carbon capture in installed
311.1f Steam boiler Wood cond | E. Viegand Maagøe A/S experience
311.1f Steam boiler Wood cond | F. Future cost prediction is based on average cost development of other similar technologies.
311.1f Steam boiler Wood cond | G. 20 %-point lower for hot water boiler
311.1f Steam boiler Wood cond | H. 5 % higher for wood pellet
311.1f Steam boiler Wood cond | I. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.1f Steam boiler Wood cond | J. Not relevant to this technology
311.2a Hot water boiler, Coal | A. Only a few plant of this type is in operation in Denmark. Nordic Suger operates a 33 MW - which is considered above average
311.2a Hot water boiler, Coal | B. Assumed slightly higher than gas boiler
311.2a Hot water boiler, Coal | C. Estimated based on gas boiler and coal CHP plant
311.2a Hot water boiler, Coal | D. Will be reduced if carbon capture in installed
311.2a Hot water boiler, Coal | E. Viegand Maagøe A/S experience
311.2a Hot water boiler, Coal | F. Future cost prediction is based on average cost development of other similar technologies.
311.2a Hot water boiler, Coal | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.2a Hot water boiler, Coal | H. Relevant for hot water boiler, going from current potential to full potential
311.2a Hot water boiler, Coal | I. Not relevant to this technology
311.2b Hot water boiler Oil | A. Only a few plant of this type is in operation in Denmark. Tjærborg Industri have boiler range up to 50 MW
311.2b Hot water boiler Oil | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.2b Hot water boiler Oil | C. Assumed equal to gasboiler
311.2b Hot water boiler Oil | D. Estimated based on gas boiler and coal CHP plant
311.2b Hot water boiler Oil | E. Will be reduced if carbon capture in installed
311.2b Hot water boiler Oil | F. Viegand Maagøe A/S experience
311.2b Hot water boiler Oil | G. Future cost prediction is based on average cost development of other similar technologies.
311.2b Hot water boiler Oil | H. 20 %-point lower for hot water boiler
311.2b Hot water boiler Oil | I. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.2b Hot water boiler Oil | J. Relevant for hot water boiler, going from current potential to full potential
311.2b Hot water boiler Oil | K. Not relevant to this technology
311.2c Hot water boiler Gas | A. Ranges from 0,5 to 50. Typical value of 20 MW
311.2c Hot water boiler Gas | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.2c Hot water boiler Gas | C. Will be reduced if carbon capture in installed
311.2c Hot water boiler Gas | D. 20 %-point lower for hot water boiler
311.2c Hot water boiler Gas | E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.2c Hot water boiler Gas | F. Relevant for hot water boiler, going from current potential to full potential
311.2c Hot water boiler Gas | G. Not relevant to this technology
311.d Hot water boiler Gas cond | A. Ranges from 0,5 to 50. Typical value of 20 MW
311.d Hot water boiler Gas cond | B. Will be reduced if carbon capture in installed
311.d Hot water boiler Gas cond | C. 20 %-point lower for hot water boiler
311.d Hot water boiler Gas cond | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.d Hot water boiler Gas cond | E. Relevant for hot water boiler, going from current potential to full potential
311.d Hot water boiler Gas cond | F. Not relevant to this technology
311.2e Hot water boiler Wood | A. Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
311.2e Hot water boiler Wood | B. 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
311.2e Hot water boiler Wood | C. Assumed slightly higher than gas boiler
311.2e Hot water boiler Wood | D. Estimated based on gas boiler and wood CHP plant
311.2e Hot water boiler Wood | E. Will be reduced if carbon capture in installed
311.2e Hot water boiler Wood | F. Viegand Maagøe A/S experience
311.2e Hot water boiler Wood | G. Future cost prediction is based on average cost development of other similar technologies.
311.2e Hot water boiler Wood | H. 5 % higher for wood pellet
311.2e Hot water boiler Wood | I. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.2e Hot water boiler Wood | J. Relevant for hot water boiler, going from current potential to full potential
311.2e Hot water boiler Wood | K. Not relevant to this technology
311.2fHot waterboiler Wood cond | A. Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
311.2fHot waterboiler Wood cond | B. Assumed slightly higher than gas boiler
311.2fHot waterboiler Wood cond | C. Estimated based on gas boiler and wood CHP plant
311.2fHot waterboiler Wood cond | D. Will be reduced if carbon capture in installed
311.2fHot waterboiler Wood cond | E. Viegand Maagøe A/S experience
311.2fHot waterboiler Wood cond | F. Future cost prediction is based on average cost development of other similar technologies.
311.2fHot waterboiler Wood cond | G. 5 % higher for wood pellet
311.2fHot waterboiler Wood cond | H. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
311.2fHot waterboiler Wood cond | I. Relevant for hot water boiler, going from current potential to full potential
311.2fHot waterboiler Wood cond | J. Not relevant to this technology
312.a Direct firing Natural Gas | A. The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
312.a Direct firing Natural Gas | B. Unit price is based on Miton Megatherms 2.5 MW burner, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
312.a Direct firing Natural Gas | C. Assumed to be equal to 10% of the boiler O&M from [1].
312.a Direct firing Natural Gas | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
312.a Direct firing Natural Gas | E. The indirect costs will be too strong a function of the process to put into a single value across all industries.
312.b Direct firing Sold Fuels | A. The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
312.b Direct firing Sold Fuels | B. Auxilliary consumption based on gas burner as the fan power is comparable. Electricity for fuel feed systems are not included.
312.b Direct firing Sold Fuels | C. Assumed to be equal to 10% of the coal boiler O&M from [1]. With gaseous or liquid fuels the O&M will be lower.
312.b Direct firing Sold Fuels | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
312.b Direct firing Sold Fuels | E. Unit price from FLSmidth, installed price and auxilliary equipment assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
312.b Direct firing Sold Fuels | F. The burner itself can start up quickly. However, in e.g. Cement industry the process equipment will limit the startup time to between 8 (warm) and 72 (cold) hours.
312.b Direct firing Sold Fuels | G. Capacity increase in multifuel burners comes with an attractive economy of scale. Going up 10 times in size will correspond toa 150% increase in pricing .
312.b Direct firing Sold Fuels | H. Auxilliary systems for solid fuels has been included, these correspond to a large part of the investment and will be a function of the chosen fuel.
312.b Direct firing Sold Fuels | I. Corresponds to a burner change, establishing a feed system has a longer construction period.
312.b Direct firing Sold Fuels | J. The indirect costs will be too strong a function of the process to put into a single value across all industries.
312.c Direct firing Electricity | A. Transformer electricity losses are not included, and the efficiency will thus be 100%.
312.c Direct firing Electricity | B. Auxilliary consumption based on gas burner as the fan power is comparable. Any pretreatment (grinding, etc.) of the fuel is not included.
312.c Direct firing Electricity | C. The regulation is dependant on the flow conditions and the subsequent surface temperature, the chosen value is an average.
312.c Direct firing Electricity | D. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
312.c Direct firing Electricity | E. Unit price from San Electro Heat, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
312.c Direct firing Electricity | F. Units are composed of multiple heating elements, each unit is installed with backup elements that can be enabled if some of the elements fail, resulting in minimal downtime and O&M during the lifetime of the equipment.
312.c Direct firing Electricity | G. The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 301.1a heat pump 60 C 40 K
Technology | Heat pump, up to 60 °C, Temp lift = 40 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1, 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 533 | 548.99 | 559.9698 | 565.5695 | 533 | 559.65 | 548.6024 | 576.8809 | B | 1, 3 | Heat pump, up to 60 °C, Temp lift = 40 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat pump, up to 60 °C, Temp lift = 40 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 528 | 543.99 | 554.9698 | 560.5695 | 528 | 554.65 | 543.6024 | 571.8809 | B,C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 1.4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16% | 0% | 16% | 0% | 13% | 0% | 7% | 0% | 11% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4% | 0% | 4% | 0% | 3.25% | 0% | 1.75% | 0% | 2.75%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1.4 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | [13 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 4 |  | Room heat | 12. spatial heating | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 4
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | E | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | F | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 4
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | 0.146 | 0.13 | 0.12 | 0.116 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | I
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019.
2 | Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
6 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 301.1b heat pump 70 C 50 K
Technology | Heat pump, up to 70 °C, Temp lift = 50 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1, 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 447 | 460.41 | 469.6182 | 474.3144 | 447 | 469.35 | 460.085 | 483.8007 | B | 1, 3 | Heat pump, up to 70 °C, Temp lift = 50 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat pump, up to 70 °C, Temp lift = 50 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 442 | 455.41 | 464.6182 | 469.3144 | 442 | 464.35 | 455.085 | 478.8007 | B,C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 1.4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 19% | 0% | 19% | 0% | 14% | 0% | 11% | 0% | 12% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4.75% | 0% | 4.75% | 0% | 3.5% | 0% | 2.75% | 0% | 3%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1.4 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 4 |  | Room heat | 12. spatial heating | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 4
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | E | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | F | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 4
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | 0.146 | 0.13 | 0.12 | 0.116 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | I
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019.
2 | Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
6 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 301.1c heat pump 80 C 60 K
Technology | Heat pump, up to 80 °C, Temp lift = 60 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1, 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 388 | 399.64 | 407.6328 | 411.7091 | 388 | 407.4 | 399.3579 | 419.9433 | B | 1, 3 | Heat pump, up to 80 °C, Temp lift = 60 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat pump, up to 80 °C, Temp lift = 60 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 383 | 394.64 | 402.6328 | 406.7091 | 383 | 402.4 | 394.3579 | 414.9433 | B,C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 1.4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 22% | 0% | 15% | 0% | 14% | 0% | 14% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 5.25% | 0% | 5.5% | 0% | 3.75% | 0% | 3.5% | 0% | 3.5%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1.4 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 4
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | E | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | F | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 4
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | 0.146 | 0.13 | 0.12 | 0.116 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | I
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019.
2 | Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
6 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 301.2 heat_cool hp 80 C 75 K
Technology | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1,3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 333 | 342.99 | 349.8498 | 353.3483 | 333 | 349.65 | 342.7478 | 360.4153 | B,C | 1,3 | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 328 | 337.99 | 344.8498 | 348.3483 | 328 | 344.65 | 337.7478 | 355.4153 | D |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 4 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 12% | 0% | 2% | 0% | 0% | 0% | 5% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 3% | 0% | 0.5% | 0% | 0% | 0% | 1.25% | 0% | 0%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | E | 1 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 1 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | [9 empty] | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 1
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1,5
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | F | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | G | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4,6
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | H
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | [8 empty] | I
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 15 | 15 | 15 | 15 |  |  |  |  | K
Temperature heat source return (°C) | 5 | 5 | 5 | 5 |  |  |  |  | K
Cooling generation capacity for one unit (MW) | 2.0991 | 2.1253 | 2.1425 | 2.151 |  |  |  |  | K
References
1 | Viegand Maagøe, 2019.
2 | Energistyrelsen, Technological data for energy plants (Compressions Heat Pumps for DH), 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | Pieper, H. et al., Allocation of investment costs for large-scale heat pumps supplying district heating, 2018
6 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
7 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Manufacturer software calculations
D | Based on lost production during startup/shutdown
E | May vary depending on heat source
F | Very individual, can vary ÷ 20 %
G | Very individual, can vary + 20 %
H | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
I | Going from simple implementation to potential
J | Not relevant to this technology
K | Process cooling

## 302.a High temp. hp Up to 125 C
Technology | High temperature heat pumps, up to 125 °C | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 1.5 | 1.5 | 1.5 | 1.5 | 0.5 | 5 | 0.5 | 5 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 260 | 275 | 285 | 290 | 260 | 302.5 | 260 | 319 |  | 1.5 | High temperature heat pumps, up to 125 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | High temperature heat pumps, up to 125 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 255 | 270 | 280 | 285 | 255 | 297.5 | 255 | 314 | B |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 7 | 1 | 7 |  | 2 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | C | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 23% | 0% | 26% | 0% | 16% | 0% | 17% | 0% | 16% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 5.75% | 0% | 6.5% | 0% | 4% | 0% | 4.25% | 0% | 4%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.4 | 0.8 | D | 2 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 25 | 25 | 25 | 25 |  |  |  |  | E | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 9
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 9
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.8712 | 0.7788 | 0.73 | 0.7 | [5 empty] | 1, 3, 4
- of which equipment (%) | 40 | 40 | 40 | 40 | [5 empty] | 4
- of which installation (%) | 60 | 60 | 60 | 60 | [5 empty] | 4
Fixed O&M (€/MJ/s/year) | 970 | 870 | 800 | 720 | [5 empty] | 5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.22 | 3.12
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | F | 3
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.7 | 1.6 | [5 empty] | 2
Technology specific data
Indirect investments cost (M€ per MW) | 0.17424 | 0.15576 | 0.146 | 0.14 |  |  |  |  | G
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 40 | 40 | 40 | 40 |  |  |  |  | H
Temperature heat source return (°C) | 10 | 10 | 10 | 10 |  |  |  |  | H
Cooling generation capacity for one unit (MW)
References
1 | Viegand Maagøe, 2019
2 | http://www.planenergi.dk/varmepumper/.
3 | Teknologisk instutut, Hybridvarmepumpe til fjernvarme, 2018
4 | Energiforskning, Højtemperatur varmepumper kan bruge lavtemperatur spildvarme, 2013
5 | Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
Notes
A | 0,5-5 MW
B | Calculated from start-up loss
C | May vary depending on heat source availability
D | Slightly higher than large heat pumps [11]
E | Theoretically as low as 10 %. For screw as low as 25 %, lower than that will affect the performance drastically.
F | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
G | Going from current implementation to potential
H | Uses waste heat

## 302.b High temp. hp Up to 150
Technology | High temperature heat pumps, up to 150 °C | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 1.5 | 1.5 | 1.5 | 1.5 | 0.5 | 5 | 0.5 | 5 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 300 | 310 | 320 | 325 | 310 | 341 | 310 | 357.5 |  | 1.5 | High temperature heat pumps, up to 150 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | High temperature heat pumps, up to 150 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 295 | 305 | 315 | 320 | 305 | 336 | 305 | 352.5 | B |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 7 | 1 | 7 |  | 2 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | C | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 9% | 0% | 10% | 0% | 3% | 0% | 5% | 0% | 7% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 2.25% | 0% | 2.5% | 0% | 0.75% | 0% | 1.25% | 0% | 1.75%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.4 | 0.8 | D | 2 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 25 | 25 | 25 | 25 |  |  |  |  | E | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 9
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 9 | Notes
Environment | [10 empty] | I | The potential is limited by the available heat source at 80 °C, of which the efficiencies are valied.
SO2 (g per GJ fuel) | Cf. the utilized electricity | [9 empty] | J | The heat pump can potentially cover, 24 %, 32 %, 17 %, 17 %, 18 %, of medium temperature in-direct for the five sectors 1., 2., 3., 4., 5, respectively. But if these potentials are used, the efficiencies needs to be corrected
PM2.5 (g per GJ fuel) | [10 empty] | K | More information on the application potential can be found in the sheet tab "HP APP POT overlap"
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 1.0454 | 0.93456 | 0.876 | 0.84 |  |  |  |  | F | 1, 3, 4
- of which equipment | 40 | 40 | 40 | 40 | [5 empty] | 4
- of which installation | 60 | 60 | 60 | 60 | [5 empty] | 4
Fixed O&M (€/MJ/s/year) | 970 | 870 | 800 | 720 | [5 empty] | 5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.22 | 3.12
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 3
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.7 | 1.6 | [5 empty] | 2
Technology specific data
Indirect investments cost (M€ per MW) | 0.20909 | 0.18691 | 0.1752 | 0.168 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 80 | 80 | 80 | 80 |  |  |  |  | I
Temperature heat source return (°C) | 50 | 50 | 50 | 50 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019
2 | http://www.planenergi.dk/varmepumper/.
3 | Teknologisk instutut, Hybridvarmepumpe til fjernvarme, 2018
4 | Energiforskning, Højtemperatur varmepumper kan bruge lavtemperatur spildvarme, 2013
5 | Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
Notes
A | 0,5-5 MW
B | Calculated from start-up loss
C | May vary depending on heat source availability
D | Slightly higher than large heat pumps [11]
E | Theoretically as low as 10 %. For screw as low as 25 %, lower than that will affect the performance drastically.
F | Corrected to technology readiness level (Not commercially avaiable at the moment)
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 303 Booster hp 150 C 130 K
Technology | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 4 | 4 | 4 | 4 | 1 | 10 | 1 | 15 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 198 | 203.94 | 208.0188 | 210.099 | 198 | 207.9 | 203.796 | 214.301 | B,C |  | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 193 | 198.94 | 203.0188 | 205.099 | 193 | 202.9 | 198.796 | 209.301 | D |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 | E |  |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | E |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 63% | 0% | 36% | 0% | 23% | 0% | 66% | 0% | 47% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 15.75% | 0% | 9% | 0% | 5.75% | 0% | 16.5% | 0% | 11.75%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | E |  |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 | E |  |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.4 | 0.8 | F |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | [9 empty] | 1 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E
Cold start-up time (hours) | 1 | 1 | 1 | 1 |  |  |  |  | E
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 1.6321 | 1.3231 | 1.037 | 0.93368 |  |  |  |  | G
- of which equipment (%) | 50 | 50 | 50 | 50 |  |  |  |  | H
- of which installation (%) | 50 | 50 | 50 | 50 |  |  |  |  | I
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 |  |  |  |  | E
Variable O&M (€/MWh) | 3.44 | 3.37 | 3.335 | 3.28
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | J
- of which is other O&M costs (€/MWh) | 1.98 | 1.87 | 1.815 | 1.76 |  |  |  |  | K
Technology specific data
Indirect investments cost (M€ per MW) | 0.32641 | 0.26462 | 0.2074 | 0.18674 |  |  |  |  | L
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | M
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | N
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | N
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | https://www.sciencedirect.com/topics/engineering/partial-load
2 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
3 | Van der Spek, et. Al., Challenges and uncertainties of ex ante techno-economic analysis of low TRL CO2 capture technology: Lessons from a case study of an NGCC with exhaust gas recycle and electric swing adsorption, 2017
Notes
A | 1-15 MW
B | Utilising waste heat above 30 °C will increase COP. Waste heat up to 75 °C can be utilised
C | Calculated from manufacturer software and manufacturer offer.
D | Based on lost production during startup/shutdown
E | Assumed similar to electrical compression heat pump and mechanical vapor recompression technologies
F | Assumed similar to high temperature heat pump technologies
G | From [2], cost correlations and learing curves [3] (Not commercially avaiable at the moment)
H | Very individual, can vary ÷ 10 %
I | Very individual, can vary + 10 %
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
K | Assumed 10 % higher than electrical compression heat pump. The turbo compressors have low O&M
L | Going from simple implementation to potential
M | Not relevant to this technology
N | Uses waste heat

## 304 Heat driven hp 80 C
Technology | Heat driven heat pumps, up to 80 °C | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 12 | 12 | 12 | 12 | 1 | 20 | 1 | 30 | A,B | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 170 | 171 | 172 | 173 | 170 | 180 | 170 | 180 |  | 1 | Heat driven heat pumps, up to 80 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat driven heat pumps, up to 80 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 168 | 169 | 170 | 171 | 168 | 178 | 168 | 178 | C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 3 |  | 1 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 1 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 2% | 0% | 2% | 0% | 1% | 0% | 1% | 0% | 1% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 2% | 0% | 2% | 0% | 1% | 0% | 1% | 0% | 1%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 1 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 20 | 30 | 20 | 30 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 1 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | [9 empty] | 1 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 1
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized heat
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.56 | 0.51 | 0.48 | 0.46 | [5 empty] | 1
- of which equipment (%) | 50 | 50 | 50 | 50 | [5 empty] | 2
- of which installation (%) | 50 | 50 | 50 | 50 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1
Variable O&M (€/MWh) | 1.01 | 1 | 1 | 0.99 | [5 empty] | 1
- of which is electricity costs (€/MWh) | 0.73 | 0.75 | 0.76 | 0.76 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.28 | 0.25 | 0.24 | 0.23 | [5 empty] | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | E
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized heat
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | 4.9412 | 4.9825 | 5.0233 | 5.0636 |  |  |  |  | F
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
2 | Viegand Maagøe, 2019.
Notes
A | 1-30 MW
B | A single unit is roughly limited to 6 MW, due to size, but the units are often connected to one unit at the site. Giving the possibility for larger capacities.
C | Based on lost production during startup/shutdown
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology
F | Only relevant if heat source are process cooling

## 305 MVR 5 K
Technology | Mechanical vapor recompression | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 5 | 50 | 5 | 50 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 1260 | 1320 | 1380 | 1430 | 1000 | 1512 | 1056 | 1716 | B | 1 | Mechanical vapor recompression | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Mechanical vapor recompression | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 1210 | 1270 | 1330 | 1380 | 950 | 1462 | 1006 | 1666 |  |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 31% | 0% | 5% | 0% | 37% | 0% | 41% | 0% | 6% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 31% | 0% | 5% | 0% | 37% | 0% | 41% | 0% | 6%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 15 | 35 | 15 | 35 |  | 1.2 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | 1.3 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 4 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.35 | 0.33 | 0.32 | 0.31 | [5 empty] | 1.5
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 1.5
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 1.5
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 200 | 2000 | [5 empty] | 2
Variable O&M (€/MWh) | 2.53 | 2.45 | 2.46 | 2.36 | [5 empty] | 2
- of which is electricity costs (€/MWh) | 0.73 | 0.75 | 0.76 | 0.76 |  |  |  |  | C | 2
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.7 | 1.6 | [5 empty] | 2
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | D
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | D
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, MVR, 2018
2 | Technological data for energi plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | Viegand Maagøe, 2019
4 | EPCON, EVAPORATION TECHNOLOGY, 2019
5 | EPCON investment cost offer, 2017.
Notes
A | 5-50 MW
B | Assumed temperature lift of 5 K (saturation temperatur)
C | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
D | Not relevant

## 306 Thermal gasification
Technology | Thermal Gasification | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 5 | 5 | 5 | 5 | 2 | 20 | 2 | 20 |  | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 1 | Thermal Gasification | High temperature | 6. Firing /Sintering | x | 0% | 0% | 75% | 0% | 50% | 0% | 20% | 0% | 60% | 0% | Thermal Gasification | High temperature | 6. Firing /Sintering | x | 0% | 0% | 30% | 0% | 0% | 0% | 20% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 1 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.035 | 0.035 | 0.035 | 0.035 | 0.02 | 0.05 | 0.02 | 0.05 |  | 2 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 1 | 0 | 1 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 75% | 0% | 80% | 0% | 60% | 0% | 60% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 30% | 0% | 30% | 0% | 30% | 0% | 30% | 0%
Planned outage (weeks per year) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 2 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 3 | 3 | 3 | 3 | [5 empty] | 2
Cold start-up time (hours) | 30 | 30 | 30 | 30 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Depends on fuel and operation
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 2 | 1.8 | 1.6 | 1.5 |  |  |  |  | B, E | 1, 2
- of which equipment (%) | 70 | 70 | 70 | 70 | [5 empty] | 2
- of which installation (%) | 30 | 30 | 30 | 30 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 13500 | 12375 | 11250 | 10125 |  |  |  |  | B, D | 1, 2
Variable O&M (€/MWh) | 1.0255 | 0.94292 | 0.85993 | 0.7766 | [5 empty] | 1, 2
- of which is electricity costs (€/MWh) | 0.02555 | 0.02625 | 0.0266 | 0.0266 |  |  |  |  | C | 1, 2
- of which is other O&M costs (€/MWh) | 1 | 0.91667 | 0.83333 | 0.75 |  |  |  |  | B | 1, 2
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | F | -
Non energy gains (M€ per MW) | - | - | - | - | [5 empty] | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, Thermal Gasification Direct in Process v01, 2018
2 | Dall Energy, Correspondance 2019
3 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
Notes
A | The efficiency of the thermal gasifier is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Parameter based on current prices, since the technology is still not mature a 25% reduction is expected over the next 30 years. Projections have been carried out by Viegand Maagøe.
C | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
D | If the unit is used at temperatures above 1000 °C additional costs has to be introduced as wear on the insulation will increase.
E | Prices include both gasifier, biomass storage and direct firing unit.
F | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 307 Hotdisc
Technology | Hotdisc | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 50 | 50 | 50 | 50 | 10 | 100 | 10 | 100 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 91 | 92 | 93 | 90 | 98 | 90 | 98 |  | 1 | Hotdisc | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 15% | 0% | 0% | 0% | 0% | 0% | Hotdisc | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 90 | 91 | 92 | 93 | 90 | 98 | 90 | 98 |  | 1 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 1 |  | Medium temperature | 2. Heating/Boiling |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 1 |  |  | 3. Drying | [13 empty] | 3. Drying
Technical lifetime (years) | 20 | 20 | 20 | 20 | 20 | 30 | 20 | 30 |  | 1 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 1 | 0.75 | 1 |  | 1 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | [13 empty] | 8.Other processes <150⁰C,
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 1 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 1
Cold start-up time (hours) | 54 | 54 | 54 | 54 |  |  |  |  | B | 1
Environment
SO2 (g per GJ fuel) | 8.3 | 8.3 | 8.3 | 8.3 |  |  |  |  | C | 2
PM2.5 (g per GJ fuel) | 0.29 | 0.29 | 0.29 | 0.29 |  |  |  |  | C | 2
NOX (g per GJ fuel) | 56 | 45 | 28 | 11 |  |  |  |  | C | 3
CH4 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | C | 3
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 |  |  |  |  | C | 3
Financial data
Nominal investment (M€ per MW) | 0.5 | 0.465 | 0.485 | 0.45 |  |  |  |  | D
- of which equipment (%) | 50 | 50 | 50 | 50
- of which installation (%) | 50 | 50 | 50 | 50
Fixed O&M (€/MJ/s/year) | 400 | 400 | 400 | 400
Variable O&M (€/MWh) | 1.175 | 1.195 | 1.205 | 1.205
- of which is electricity costs (€/MWh) | 0.73 | 0.75 | 0.76 | 0.76
- of which is other O&M costs (€/MWh) | 0.445 | 0.445 | 0.445 | 0.445
Technology specific data
Indirect investments cost (M€ per MW) | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup)
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 |  |  |  |  | F | 4,5
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | FLSmidth, Personal communication, 2019
2 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
3 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
4 | European Commision, The potential for CCS and CCU in Europe, 2019
5 | Sampo Kour, et Al., The potential for CCUS in selected industrial sectors – summary ofconcept evaluations in Finland, 2017
Notes
A | 10-100 MW
B | 36-72 hours
C | Assumed equal to waste used in incineration power plant
D | Includes retrofit to existing system
E | If a rebuillt of the system is necessary, this cost need to be included. E.g. if a cement oven is a separate line and not inline system.
F | Typically engineered to remove 80-90 %, above 95 % is possible
G | The fuel is waste and the waste needs minimum pre-handling. Large pieces of waste can be fired directly in the Hotdisc. Cost of waste will be lower than at an inceration plant

## 308 Dielectric heating
Technology | Dielectric heating | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.2 | 0.01 | 0.2 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 95 | 95 | 95 | 95 | 85 | 100 | 85 | 100 | B | 2 | Dielectric heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Dielectric heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 95 | 95 | 95 | 95 | 85 | 100 | 85 | 100 |  |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 5% | 2% | 3% | 1% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 5% | 2% | 3% | 1% | 0% | 0%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 30 | 30 | 30 | 30 | 20 | 35 | 20 | 35 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.1 | 0.05 | 0.1 |  | 3 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | [13 empty] | 8.Other processes <150⁰C,
Minimum load (% of full load) | 10 | 10 | 10 | 10 |  |  |  |  | C | 5 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 5
Cold start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 5
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 2.7 | 2.619 | 2.538 | 2.43 |  |  |  |  | D | 6,7,8
- of which equipment (%) | 85 | 85 | 85 | 85 | [5 empty] | 9
- of which installation (%) | 15 | 15 | 15 | 15 | [5 empty] | 9
Fixed O&M (€/MJ/s/year) | 0 | 0 | 0 | 0
Variable O&M (€/MWh) | 45.823 | 45.825 | 45.826 | 45.826
- of which is electricity costs (€/MWh) | 0.073 | 0.075 | 0.076 | 0.076 |  |  |  |  | E
- of which is other O&M costs (€/MWh) | 45.75 | 45.75 | 45.75 | 45.75 |  |  |  |  | F | 6
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | G
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | H,I
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Thermex Thermatron, https://thermex-thermatron.com/industrial-microwave-generators/, 2019
2 | Technological Institute, https://www.dti.dk/industrial-microwave-processing/
3 | Viegand Maagøe, 2019
4 | Cellencor, https://www.cellencor.com, 2019
5 | Bi.Elle, http://www.microwaves.it/ing/company.htm, 2019
6 | A.M. Hasna, Microwave Processing Applications in Chemical Engineering: Cost Analysis, 2011
7 | Tony Koral, Considerations for Commercial Success, 2013 in new RF and Microwave Industrial Heating Applications
8 | Bi.Elle, Personal communication, 2019
9 | Beyond Zero Emissions Inc, Zero Carbon Industry Plan Electrifying Industry, 2018
Notes
A | 0,01-0,2 MW
B | Cooling system account for a small loss
C | The capacity is often specifically regulated to product flow
D | Can vary quite significantly, as different applications requires different additional subsystems.
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
F | The magnatron (microwave generator) has a lifetime of around 10.000 hours of operation. Replacement of magnatron are included here.
G | Not relevant
H | Infrared will have non energy gains, but it has not been possible to estimate.
I | Treatment times are up to 20 times faster than traditional systems.

## 309 Infrared (IR)
Technology | Infrared heating | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.2 | 0.01 | 0.2 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 96 | 96 | 96 | 96 | 90 | 100 | 90 | 100 | B,C | 2 | Infrared heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Infrared heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 96 | 96 | 96 | 96 | 90 | 100 | 90 | 100 |  |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 3% | 2% | 3% | 1% | 0% | 5% |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 3% | 2% | 3% | 1% | 0% | 5%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 30 | 30 | 30 | 30 | 20 | 35 | 20 | 35 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.1 | 0.05 | 0.1 |  | 3 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | [13 empty] | 8.Other processes <150⁰C,
Minimum load (% of full load) | 10 | 10 | 10 | 10 |  |  |  |  | D |  |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 2
Cold start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.35 | 0.34 | 0.33 | 0.315 |  |  |  |  | E | 1
- of which equipment (%) | 85 | 85 | 85 | 85 |  |  |  |  | E | 2
- of which installation (%) | 15 | 15 | 15 | 15 |  |  |  |  | E | 2
Fixed O&M (€/MJ/s/year) | 0 | 0 | 0 | 0
Variable O&M (€/MWh) | 117.073 | 117.075 | 117.076 | 117.076
- of which is electricity costs (€/MWh) | 0.073 | 0.075 | 0.076 | 0.076 |  |  |  |  | F
- of which is other O&M costs (€/MWh) | 117 | 117 | 117 | 117 |  |  |  |  | G | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | I,J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Netek IR System A/S, Personal communication, 2019
2 | Beyond Zero Emissions Inc, Zero Carbon Industry Plan Electrifying Industry, 2018
3 | Viegand Maagøe, 2019
4 | IG Infrared, https://www.ig-infrared.com, 2019
5 | American Society of. Heating, Refrigerating and Air-Conditioning Engineers, ASHRAE Handbook – Heating, Ventilating, and Air-Conditioning Systems and Equipment (I-P Edition), 2008
Notes
A | 0,01-0,2 MW
B | The electricity to heat efficiency is 100 %, but not all of the electricity is converted to radiant energy [5]
C | A part of the electricity is conveted to convective heat, and some of it is lost to surrounding.
D | A system often consist of mulitiple emitters, giving the possiblity in turn emitters off individually.
E | Can vary quite significantly, as different applications requires different additional subsystems.
F | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
G | The emitters have a lifetime of 10.000 to 15.000 hours of operation. Replacement of emitters are included here.
H | Not relevant
I | Infrared will have non energy gains, but it has not been possible to estimate.
J | Heating time is 7 to 40 times faster than convective ovens. Uptake much less space which enable possible expansion.

## 310.1a Electric boiler steam
[11 empty] | Current application potential | Type and temperature of process heating supply
Technology | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | [10 empty] | Water/liquid |  |  |  | Steam |  |  |  | Direct
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | End-use | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C
[5 empty] | Lower | Upper | Lower | Upper |  |  | Other processes | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Heat generation capacity for one unit (MW) | 2 | 2 | 2 | 2 | 1 | 5 | 1 | 5 | A |  | Firing /Sintering | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), nominel load | 99 | 99 | 99 | 99 | 98 | 100 | 98 | 100 |  | 1,2 | Distillation | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 |  | 1,2 | Dewatering | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Auxiliary electricity consumption (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1,2 | Heating/Boiling | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 |  | 1,2 | Space heating | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2 | Melting /Casting | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2 | Drying | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
Minimum load (% of full load) | 2 | 2 | 2 | 2 | [5 empty] | 2
Warm start-up time (hours) | 0.03 | 0.03 | 0.03 | 0.03 | [5 empty] | 2
Cold start-up time (hours) | 0.17 | 0.17 | 0.17 | 0.17 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.21296 | 0.18634 | 0.18634 | 0.18634 |  |  |  |  | B,C | 1,2,4
- of which equipment (%) | 75 | 75 | 75 | 75 | [5 empty] | 2, 4
- of which installation (%) | 25 | 25 | 25 | 25 | [5 empty] | 2, 4
Fixed O&M (€/MJ/s/year) | 1230.5 | 1173 | 1115.5 | 1058 | [5 empty] | 2,3,4
Variable O&M (€/MWh) | 0.94 | 0.92313 | 0.90126 | 0.87439
- of which is electricity costs (€/MWh) | 0.365 | 0.375 | 0.38 | 0.38 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.575 | 0.54813 | 0.52126 | 0.49439 | [5 empty] | 2,3,4
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Additional investments cost for 12-16 bar boilers (M€ per MW) | 0.055556 | 0.048611 | 0.048611 | 0.048611
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2019
4 | Nordheat, Personal communication, 2022
Notes
A | 1-5 MW
B | Electrode boilers at low voltage typically needs a transformer from distribution grid. Costs for the transformer are included in the equipment costs.
C | Investment cost is slightly higher than for a hot water boiler.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology

## 310.1b Electric boiler steam
[11 empty] | Current application potential | Type and temperature of process heating supply
Technology | Electric boiler, 10 kV, steam, 1-12 bar | [10 empty] | Water/liquid |  |  |  | Steam |  |  |  | Direct
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | End-use | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C
[5 empty] | Lower | Upper | Lower | Upper |  |  | Other processes | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Heat generation capacity for one unit (MW) | 15 | 15 | 15 | 15 | 5 | 60 | 5 | 60 | A |  | Firing /Sintering | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), nominel load | 99 | 99 | 99 | 99 | 98 | 100 | 98 | 100 |  | 1,2 | Distillation | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 |  | 1,2 | Dewatering | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Auxiliary electricity consumption (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1,2 | Heating/Boiling | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 |  | 1,2 | Space heating | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2 | Melting /Casting | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2 | Drying | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0%
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
Minimum load (% of full load) | 2 | 2 | 2 | 2 | [5 empty] | 2
Warm start-up time (hours) | 0.03 | 0.03 | 0.03 | 0.03 | [5 empty] | 2
Cold start-up time (hours) | 0.17 | 0.17 | 0.17 | 0.17 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.095556 | 0.083611 | 0.083611 | 0.083611 |  |  |  |  | B,C | 1,2,4
- of which equipment (%) | 85 | 85 | 85 | 85 | [5 empty] | 2
- of which installation (%) | 15 | 15 | 15 | 15 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 1107.45 | 1055.7 | 1003.95 | 952.2 | [5 empty] | 2,3,4
Variable O&M (€/MWh) | 0.8825 | 0.86832 | 0.84914 | 0.82495
- of which is electricity costs (€/MWh) | 0.365 | 0.375 | 0.38 | 0.38 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.5175 | 0.49332 | 0.46914 | 0.44495 | [5 empty] | 2,3,4
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Additional investments cost for 12-16 bar boilers (M€ per MW) | 0.017645 | 0.01544 | 0.01544 | 0.01544
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2022
4 | Nordheat, Personal communication, 2022
Notes
A | 5-60 MW
B | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
C | Investment cost is slightly higher than for a hot water boiler.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology

## 310.2a Electric boiler hot wate
[11 empty] | Current application potential | Type and temperature of process heating supply
Technology | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | [10 empty] | Water/liquid |  |  |  | Steam |  |  |  | Direct
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | End-use | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C
[5 empty] | Lower | Upper | Lower | Upper |  |  | Other processes | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Heat generation capacity for one unit (MW) | 2 | 2 | 2 | 2 | 1 | 5 | 1 | 5 | A |  | Firing /Sintering | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), nominel load | 99 | 99 | 99 | 99 | 98 | 100 | 98 | 100 |  | 1,2 | Distillation | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 |  | 1,2 | Dewatering | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Auxiliary electricity consumption (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1,2 | Heating/Boiling | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 |  | 1,2 | Space heating | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 1 | Melting /Casting | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2 | Drying | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
Minimum load (% of full load) | 5 | 5 | 5 | 5 | [5 empty] | 1
Warm start-up time (hours) | 0.008 | 0.008 | 0.008 | 0.008 | [5 empty] | 1
Cold start-up time (hours) | 0.08 | 0.08 | 0.08 | 0.08 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.18634 | 0.15972 | 0.15972 | 0.15972 |  |  |  |  | B,C | 1,2,4
- of which equipment (%) | 75 | 75 | 75 | 75 | [5 empty] | 2
- of which installation (%) | 25 | 25 | 25 | 25 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 1070 | 1020 | 970 | 920 | [5 empty] | 1
Variable O&M (€/MWh) | 0.865 | 0.85164 | 0.83327 | 0.80991
- of which is electricity costs (€/MWh) | 0.365 | 0.375 | 0.38 | 0.38 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.5 | 0.47664 | 0.45327 | 0.42991 | [5 empty] | 2,3,4
Technology specific data
Indirect investments cost (M€ per MW) | 0.093171 | 0.079861 | 0.079861 | 0.079861 |  |  |  |  | E
Additional investments cost for 12-16 bar boilers (M€ per MW) | 0.048611 | 0.041667 | 0.041667 | 0.041667
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2019
4 | Nordheat, Personal communication, 2022
Notes
A | 1-5 MW
B | Electrode boilers at low voltage typically needs a transformer from distribution grid. Costs for the transformer are included in the equipment costs.
C | Investment cost is slightly lower than for a steam boiler.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Going from current implementation to potential

## 310.2b Electric boiler hot wate
[11 empty] | Current application potential | Type and temperature of process heating supply
Technology | Electric boiler, 10 kV, hot water, 1-12 bar | [10 empty] | Water/liquid |  |  |  | Steam |  |  |  | Direct
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | End-use | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C | <100°C | 100-150°C | 150-200°C | >200°C
[5 empty] | Lower | Upper | Lower | Upper |  |  | Other processes | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Heat generation capacity for one unit (MW) | 15 | 15 | 15 | 15 | 5 | 60 | 5 | 60 | A |  | Firing /Sintering | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), nominel load | 99 | 99 | 99 | 99 | 98 | 100 | 98 | 100 |  | 1,2 | Distillation | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 |  | 1,2 | Dewatering | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Auxiliary electricity consumption (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1,2 | Heating/Boiling | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 |  | 1,2 | Space heating | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 1 | Melting /Casting | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2 | Drying | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
Minimum load (% of full load) | 5 | 5 | 5 | 5 | [5 empty] | 1
Warm start-up time (hours) | 0.008 | 0.008 | 0.008 | 0.008 | [5 empty] | 1
Cold start-up time (hours) | 0.08 | 0.08 | 0.08 | 0.08 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.083611 | 0.071667 | 0.071667 | 0.071667 |  |  |  |  | B,C | 1,2,4
- of which equipment (%) | 85 | 85 | 85 | 85 | [5 empty] | 2
- of which installation (%) | 15 | 15 | 15 | 15 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 963 | 918 | 873 | 828 | [5 empty] | 1,2,4
Variable O&M (€/MWh) | 0.815 | 0.80397 | 0.78794 | 0.76692
- of which is electricity costs (€/MWh) | 0.365 | 0.375 | 0.38 | 0.38 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.45 | 0.42897 | 0.40794 | 0.38692 | [5 empty] | 2,3,4
Technology specific data
Indirect investments cost (M€ per MW) | 0.041806 | 0.035833 | 0.035833 | 0.035833 |  |  |  |  | E
Additional investments cost for 12-16 bar boilers (M€ per MW) | 0.01544 | 0.013234 | 0.013234 | 0.013234
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2022
4 | Nordheat, Personal communication, 2022
Notes
A | 5-60 MW
B | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
C | Investment cost is slightly lower than for a steam boiler.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Going from current implementation to potential

## 311.1a Steam boiler Coal
Technology | Steam boiler, Coal | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 90 | 91 | 92 | 88 | 91.8 | 88 | 93.84 | B | 5,6,7,8 | Steam boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 89 | 89 | 90 | 91 | 87 | 90.8 | 87 | 92.84 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1.5 | 1 | 1.5 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.2 | 1.2 | 1.2 | 1.2 | 0.1 | 2.2 | 0.1 | 2.2 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 1.1 | 0.8 | 1.1 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 8 | 8 | 8 | 8 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 2.1 | 2.1 | 2.1 | 2.1 | [5 empty] | 9
NOX (g per GJ fuel) | 35 | 35 | 35 | 35 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.5 | 0.46576 | 0.446 | 0.44046 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 32600 | 31600 | 30600 | [5 empty] | 3
Variable O&M (€/MWh) | 1.903 | 1.925 | 1.936 | 1.936 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.803 | 0.825 | 0.836 | 0.836 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Nordic Suger operates a 33 MW - which is considered above average
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed slightly higher than gas boiler
D | Estimated based on gas boiler and coal CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Not relevant to this technology

## 311.1b Steam boiler Oil
Technology | Steam boiler, Oil | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 95 | 96 | 97 | 97 | 90 | 98 | 90 | 98 | B | 5,6,7,8 | Steam boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 94 | 95 | 96 | 96 | 89 | 97 | 89 | 97 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.1 | 1.1 | 1.1 | 1.1 | 0.09 | 2.1 | 0.09 | 2.1 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.8 | 0.5 | 0.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 25 | 20 | 18 | 15 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.055 | 0.046576 | 0.0446 | 0.044046 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 1800 | 1700 | 1600 | 1500 | [5 empty] | 3
Variable O&M (€/MWh) | 1 | 0.9 | 0.9 | 0.9 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 0.8978 | 0.81 | 0.8164 | 0.824 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Tjærborg Industri have boiler range up to 50 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed equal to gasboiler
D | Estimated based on gas boiler and coal CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Not relevant to this technology

## 311.1c Steam boiler Gas
Technology | Steam boiler, Natural gas or biogas | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 93 | 94 | 94 | 95 | 90 | 96 | 90 | 97 | B | 5,6,7,8 | Steam boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 92 | 93 | 93 | 94 | 89 | 95 | 89 | 96 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 30 | 25 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | C | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.054545 | 0.045455 | 0.045455 | 0.045455 |  |  |  |  | D | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | E | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | F
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | F
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Will be reduced if carbon capture in installed
D | 20 %-point lower for hot water boiler
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
F | Not relevant to this technology

## 311.1d Steam boiler Gas cond
Technology | Steam boiler, Natural gas or biogas (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 103 | 104 | 104 | 104 | 95 | 106 | 96 | 107 |  | 5,6,7,8,10 | Steam boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Steam boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 101 | 103 | 103 | 103 | 94 | 105 | 95 | 106 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | B | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.06 | 0.05 | 0.05 | 0.05 |  |  |  |  | C | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | D | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | E
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | Will be reduced if carbon capture in installed
C | 20 %-point lower for hot water boiler
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology

## 311.1e Steam boiler Wood
Technology | Steam boiler, Wood Chips | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 90 | 90 | 91 | 89 | 92 | 90 | 93 | B | 5,6,7,8 | Steam boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 89 | 89 | 89 | 90 | 88 | 91 | 89 | 92 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.61818 | 0.59091 | 0.56364 | 0.53636 |  |  |  |  | F,G,H,I | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 35900 | 34800 | 33700 |  |  |  |  | I | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | J | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | K
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | K
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed slightly higher than gas boiler
D | Estimated based on gas boiler and wood CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | 5 % higher for wood pellet
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
K | Not relevant to this technology

## 311.1f Steam boiler Wood cond
Technology | Steam boiler, Wood chips (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 | Steam boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Steam boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | B | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | C | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | D | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.68 | 0.65 | 0.62 | 0.59 |  |  |  |  | E,F,G,H | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 37000 | 35900 | 34800 | 33700 |  |  |  |  | H | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
11 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. Used for estimation of the efficiency for technology "09a Wood Chips HOP" heat only boilers, woodchips 6W in the Technology Data - Energy Plants for Electricity and District heating generation, version 0007 January 2020
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | Assumed slightly higher than gas boiler
C | Estimated based on gas boiler and wood CHP plant
D | Will be reduced if carbon capture in installed
E | Viegand Maagøe A/S experience
F | Future cost prediction is based on average cost development of other similar technologies.
G | 20 %-point lower for hot water boiler
H | 5 % higher for wood pellet
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Not relevant to this technology
L. | Assuming that the system is optimised at a inlet temperature of 40°C.
M. | The efficiency is for a plant using woodchips with a water content of 50% and wetting of the combusting air. If other types of wood- biomass is assumed the efficiency should be reduced accordingly.

## 311.2a Hot water boiler, Coal
Technology | Hot water boiler, Coal | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 90 | 91 | 92 | 88 | 91.8 | 88 | 92.92 |  | 5,6,7,8 | Hot water boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 89 | 89 | 90 | 91 | 87 | 90.8 | 87 | 91.92 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1.5 | 1 | 1.5 | B | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.2 | 1.2 | 1.2 | 1.2 | 0.1 | 2.2 | 0.1 | 2.2 | C | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 1.1 | 0.8 | 1.1 | C | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 8 | 8 | 8 | 8 |  |  |  |  | D | 3, 9
PM2.5 (g per GJ fuel) | 2.1 | 2.1 | 2.1 | 2.1 | [5 empty] | 9
NOX (g per GJ fuel) | 35 | 35 | 35 | 35 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E,F | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 32600 | 31600 | 30600 | [5 empty] | 3
Variable O&M (€/MWh) | 1.903 | 1.925 | 1.936 | 1.936 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.803 | 0.825 | 0.836 | 0.836 |  |  |  |  | G | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | I
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Nordic Suger operates a 33 MW - which is considered above average
B | Assumed slightly higher than gas boiler
C | Estimated based on gas boiler and coal CHP plant
D | Will be reduced if carbon capture in installed
E | Viegand Maagøe A/S experience
F | Future cost prediction is based on average cost development of other similar technologies.
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Relevant for hot water boiler, going from current potential to full potential
I | Not relevant to this technology

## 311.2b Hot water boiler Oil
Technology | Hot water boiler, Oil | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 96 | 97 | 98 | 98 | 90 | 98 | 90 | 98 | B | 5,6,7,8 | Hot water boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 95 | 96 | 97 | 97 | 89 | 97 | 89 | 97 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.1 | 1.1 | 1.1 | 1.1 | 0.09 | 2.1 | 0.09 | 2.1 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.8 | 0.5 | 0.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 25 | 20 | 18 | 15 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.044 | 0.037261 | 0.03568 | 0.035236 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 1800 | 1700 | 1600 | 1500 | [5 empty] | 3
Variable O&M (€/MWh) | 1 | 0.9 | 0.9 | 0.9 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 0.8978 | 0.81 | 0.8164 | 0.824 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | K
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Tjærborg Industri have boiler range up to 50 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed equal to gasboiler
D | Estimated based on gas boiler and coal CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Relevant for hot water boiler, going from current potential to full potential
K | Not relevant to this technology

## 311.2c Hot water boiler Gas
Technology | Hot water boiler, Natural gas or biogas | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 94 | 95 | 95 | 96 | 90 | 96 | 90 | 98 | B | 5,6,7,8 | Hot water boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 93 | 94 | 94 | 95 | 89 | 95 | 89 | 97 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 30 | 25 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | C | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.043636 | 0.036364 | 0.036364 | 0.036364 |  |  |  |  | D | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | E | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | F
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | G
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Will be reduced if carbon capture in installed
D | 20 %-point lower for hot water boiler
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
F | Relevant for hot water boiler, going from current potential to full potential
G | Not relevant to this technology

## 311.d Hot water boiler Gas cond
Technology | Hot water boiler, Natural gas or biogas (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 103 | 104 | 104 | 104 | 95 | 106 | 96 | 107 |  | 5,6,7,8,10 | Hot water boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 101 | 103 | 103 | 103 | 94 | 105 | 95 | 106 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 17% | 0% | 0% | 0% | 0% | 0% | 6% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4.25% | 0% | 0% | 0% | 0% | 0% | 1.5% | 0% | 0%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | B | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.048 | 0.04 | 0.04 | 0.04 |  |  |  |  | C | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | D | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | F
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | Will be reduced if carbon capture in installed
C | 20 %-point lower for hot water boiler
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Relevant for hot water boiler, going from current potential to full potential
F | Not relevant to this technology

## 311.2e Hot water boiler Wood
Technology | Hot water boiler, Wood Chips | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 91 | 91 | 91 | 92 | 90 | 93 | 91 | 94 | B | 5,6,7,8 | Hot water boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 90 | 90 | 90 | 91 | 89 | 92 | 90 | 93 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.61818 | 0.59091 | 0.56364 | 0.53636 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 35900 | 34800 | 33700 |  |  |  |  | H | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | K
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed slightly higher than gas boiler
D | Estimated based on gas boiler and wood CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 5 % higher for wood pellet
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Relevant for hot water boiler, going from current potential to full potential
K | Not relevant to this technology

## 311.2fHot waterboiler Wood cond
Technology | Hot water boiler, Wood chips (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 | Hot water boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | B | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 17% | 0% | 0% | 0% | 0% | 0% | 6% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4.25% | 0% | 0% | 0% | 0% | 0% | 1.5% | 0% | 0%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | C | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | D | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.68 | 0.65 | 0.62 | 0.59 |  |  |  |  | E,F,G | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 37000 | 35900 | 34800 | 33700 |  |  |  |  | G | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | H | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | I
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
11 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. Used for estimation of the efficiency for technology "09a Wood Chips HOP" heat only boilers, woodchips 6W in the Technology Data - Energy Plants for Electricity and District heating generation, version 0007 January 2020
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | Assumed slightly higher than gas boiler
C | Estimated based on gas boiler and wood CHP plant
D | Will be reduced if carbon capture in installed
E | Viegand Maagøe A/S experience
F | Future cost prediction is based on average cost development of other similar technologies.
G | 5 % higher for wood pellet
H | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
I | Relevant for hot water boiler, going from current potential to full potential
J | Not relevant to this technology
L. | Assuming that the system is optimised at a inlet temperature of 40°C.
M. | The efficiency is for a plant using woodchips with a water content of 50% and wetting of the combusting air. If other types of wood- biomass is assumed the efficiency should be reduced accordingly.

## 312.a Direct firing Natural Gas
Technology | Direct Firing, Natural Gas | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 2.5 | 2.5 | 2.5 | 2.5 | 1 | 10 | 1 | 10 |  | 2 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 | Direct Firing, Natural Gas | High temperature | 6. Firing /Sintering | x | 100% | 0% | 100% | 0% | 100% | 0% | 20% | 0% | 100% | 0% | Direct Firing, Natural Gas | High temperature | 6. Firing /Sintering | x | 75% | 0% | 75% | 0% | 40% | 0% | 20% | 0% | 10% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 1 | 0.1 | 1 |  | 8, 9 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.5 | 0 | 0.5 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 75% | 0% | 75% | 0% | 30% | 0% | 75% | 0% | 0% | 0%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.04 | 0.01 | 0.04 |  | 2 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 6 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 2
Cold start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 1 | Potential overlap for the full applcaition potential
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 1 | [8 empty] | Nat Gas | 2.425% | 100%
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 1 | [8 empty] | Solid Fuels | 28.63% | 84.15%
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 1 | [8 empty] | Electricity | 0% | 39.31%
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 1
Financial data
Nominal investment (M€ per MW) | 0.015 | 0.015 | 0.015 | 0.015 |  |  |  |  | B | 4, 7
- of which equipment (%) | 66.6667 | 66.6667 | 66.6667 | 66.6667 | [5 empty] | 7
- of which installation (%) | 33.3333 | 33.3333 | 33.3333 | 33.3333 | [5 empty] | 7
Fixed O&M (€/MJ/s/year) | 181.8182 | 177.2727 | 172.7273 | 154.5455 |  |  |  |  | C | 2, 1
Variable O&M (€/MWh) | 0.2825 | 0.2775 | 0.28 | 0.28 | [5 empty] | 1
- of which is electricity costs (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 |  |  |  |  | D | 7
- of which is other O&M costs (€/MWh) | 0.1 | 0.09 | 0.09 | 0.09 |  |  |  |  | C | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E | -
Non energy gains (M€ per MW) | - | - | - | - | [5 empty] | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 5
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | Milton Megatherm, Correspondance 2019
5 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
6 | Eclipse, Vortometric Burner Series Datasheet 128-3, 20/2/2015
7 | Viegand Maagøe assessment, 2019
8 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
9 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
Notes
A | The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Unit price is based on Miton Megatherms 2.5 MW burner, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
C | Assumed to be equal to 10% of the boiler O&M from [1].
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 312.b Direct firing Sold Fuels
Technology | Direct Firing Solid Fuels | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [6 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 | Direct Firing Solid Fuels | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 90% | 0% | 0% | 0% | 0% | 0% | Direct Firing Solid Fuels | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 60% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 1 | 0.1 | 1 | B | 8, 9 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.5 | 0 | 0.5 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 0% | 0% | 70% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 3.5 | 3.5 | 3.5 | 3.5 | 2 | 5 | 2 | 5 |  | 4 |  |  | 3. Drying | x, A | [12 empty] | 3. Drying | x
Technical lifetime (years) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 2, 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.01 | 0.01 | 0.01 | 0.01 | 0.001 | 0.015 | 0.001 | 0.015 | I | 2, 4 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 6 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  |  | F | 2
Cold start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  |  | F | 2 | Notes
Environment | [10 empty] | A | Today, direct firing takes place in the sector 2. Commodity production to dry wood in the wood industry. The technology used here differs from the reviewed technology. The reviewed technology is not appliacable, therefore the application potential is set to zero.
SO2 (g per GJ fuel) | Depends on Fuel Mix | [9 empty] | Potential overlap for the full application potential
PM2.5 (g per GJ fuel) | [18 empty] | Nat Gas | 2.425% | 100%
NOX (g per GJ fuel) | [18 empty] | Solid Fuels | 28.63% | 84.15%
CH4 (g per GJ fuel) | [18 empty] | Electricity | 0% | 39.31%
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.22 | 0.22 | 0.22 | 0.22 |  |  |  |  | E, G, H | 4, 7
- of which equipment (%) | 66.6667 | 66.6667 | 66.6667 | 66.6667 | [5 empty] | 7
- of which installation (%) | 33.3333 | 33.3333 | 33.3333 | 33.3333 | [5 empty] | 7
Fixed O&M (€/MJ/s/year) | 3400 | 3300 | 3200 | 3100 |  |  |  |  | C | 2, 1
Variable O&M (€/MWh) | 0.3253 | 0.3303 | 0.3328 | 0.3328 | [5 empty] | 2, 7
- of which is electricity costs (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 |  |  |  |  | D | 7
- of which is other O&M costs (€/MWh) | 0.1428 | 0.1428 | 0.1428 | 0.1428 |  |  |  |  | C | 7
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J | -
Non energy gains (M€ per MW) | - | - | - | - | [5 empty] | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 5
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | FLSmidth - Burner & PLM for HOTDISC, Correspondance 2019
5 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
6 | FCT International Burners, Correspondance 2019.
7 | Viegand Maagøe assessment, 2019
8 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
9 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
Notes
A | The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Auxilliary consumption based on gas burner as the fan power is comparable. Electricity for fuel feed systems are not included.
C | Assumed to be equal to 10% of the coal boiler O&M from [1]. With gaseous or liquid fuels the O&M will be lower.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Unit price from FLSmidth, installed price and auxilliary equipment assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
F | The burner itself can start up quickly. However, in e.g. Cement industry the process equipment will limit the startup time to between 8 (warm) and 72 (cold) hours.
G | Capacity increase in multifuel burners comes with an attractive economy of scale. Going up 10 times in size will correspond toa 150% increase in pricing .
H | Auxilliary systems for solid fuels has been included, these correspond to a large part of the investment and will be a function of the chosen fuel.
I | Corresponds to a burner change, establishing a feed system has a longer construction period.
J | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 312.c Direct firing Electricity
Technology | Direct Firing, Electricity | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | 2030 |  | 2050 |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 5 | 5 | 5 | 5 | 1 | 10 | 1 | 10 |  | 4 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 | Direct Firing, Electricity | High temperature | 6. Firing /Sintering | x | 100% | 0% | 100% | 0% | 0% | 0% | 20% | 0% | 5% | 0% | Direct Firing, Electricity | High temperature | 6. Firing /Sintering | x | 50% | 0% | 50% | 0% | 0% | 0% | 20% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 1 | 0.1 | 1 | B | 6, 7 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | F | 4 |  | Medium temperature | 2. Heating/Boiling | x | 100% | 0% | 100% | 0% | 50% | 0% | 100% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 50% | 0% | 50% | 0% | 25% | 0% | 40% | 0% | 0% | 0%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | F | 4 |  |  | 3. Drying | x, A | [12 empty] | 3. Drying | x
Technical lifetime (years) | 12.5 | 12.5 | 12.5 | 12.5 | 10 | 15 | 10 | 15 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.04 | 0.04 | 0.04 | 0.04 | 0.02 | 0.06 | 0.02 | 0.06 |  | 5 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 |  |  |  |  | C | 4 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 5
Cold start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 5 | Notes
Environment | [10 empty] | A | Today the melting and hardening process in the metal industry is almost fully supplied by electricity and the potential noted here is just 5%. The potential denoted here is reduced to that which can be delivered by a heating element in an air flow.
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel) | [10 empty] | Potential overlap for the full applcaition potential
NOX (g per GJ fuel)
CH4 (g per GJ fuel) | [18 empty] | Nat Gas | 2.425% | 100%
N2O (g per GJ fuel) | [18 empty] | Solid Fuels | 28.63% | 84.15%
Financial data | [18 empty] | Electricity | 0% | 39.31%
Nominal investment (M€ per MW) | 0.06 | 0.06 | 0.06 | 0.06 |  |  |  |  | E | 4, 5
- of which equipment (%) | 66.6667 | 66.6667 | 66.6667 | 66.6667 | [5 empty] | 5
- of which installation (%) | 33.3333 | 33.3333 | 33.3333 | 33.3333 | [5 empty] | 5
Fixed O&M (€/MJ/s/year) | 0 | 0 | 0 | 0 |  |  |  |  | F | 4
Variable O&M (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 | [5 empty] | 2, 5
- of which is electricity costs (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 |  |  |  |  | D | 5
- of which is other O&M costs (€/MWh) | 0 | 0 | 0 | 0 |  |  |  |  | F | 4
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | G
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | SAN Electro Heat A/S , Correspondance 2019
5 | Viegand Maagøe assessment, 2019
6 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
7 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
Notes
A | Transformer electricity losses are not included, and the efficiency will thus be 100%.
B | Auxilliary consumption based on gas burner as the fan power is comparable. Any pretreatment (grinding, etc.) of the fuel is not included.
C | The regulation is dependant on the flow conditions and the subsequent surface temperature, the chosen value is an average.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Unit price from San Electro Heat, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
F | Units are composed of multiple heating elements, each unit is installed with backup elements that can be enabled if some of the elements fail, resulting in minimal downtime and O&M during the lifetime of the equipment.
G | The indirect costs will be too strong a function of the process to put into a single value across all industries.