## Index
INDEX | Technology Data for Industrial Process Heat
HP APP POT overlap | All cost data is in 2015€
301.1a heat pump 60 C 40 K
301.1b heat pump 70 C 50 K
301.1c heat pump 80 C 60 K
301.2 heat_cool hp 80 C 75 K
302.a High temp. hp Up to 125 C | Date | Sheet | Change | Notes
302.b High temp. hp Up to 150 | 2020-10-01 | 401-403 CC | Carbon capture added
303 Booster hp 150 C 130 K
304 Heat driven hp 80 C
305 MVR 5 K
306 Thermal gasification
307 Hotdisc
308 Dielectric heating
309 Infrared (IR)
310.1 Electric boiler steam
310.2 Electric boiler hot water
311.1a Steam boiler Coal
311.1b Steam boiler Oil
311.1c Steam boiler Gas
311.1d Steam boiler Gas cond
311.1e Steam boiler Wood
311.1f Steam boiler Wood cond
311.2a Hot water boiler, Coal
311.2b Hot water boiler Oil
311.2c Hot water boiler Gas
311.d Hot water boiler Gas cond
311.2e Hot water boiler Wood
311.2fHot waterboiler Wood cond
312.a Direct firing Natural Gas
312.b Direct firing Sold Fuels
312.c Direct firing Electricity
401.a Post comb - small CHP
401.b Post comb - Large biomass
401.c Post comb - Cement kiln
402.a Oxy-fuel- Large Biomass
402.b Oxy-fuel Cement
403.a Direct air capture
This file contains the technology data sheets related to industrial process heat. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. Dates and descriptions of updates are listed in the ammendment sheet below.

## HP APP POT overlap
Heat pump application potential overlap | [17 empty] | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Technology | Notes | [16 empty] | Current application potential | Full application potential | Current application potential | Full application potential | Current application potential | Full application potential | Current application potential | Full application potential | Current application potential | Full application potential
Heat pump, up to 60 °C, Temp lift = 40 K | [17 empty] | 4% | 16% | 4% | 16% | 3.25% | 13% | 1.75% | 7% | 2.75% | 11%
Heat pump, up to 70 °C, Temp lift = 50 K | [17 empty] | 4.75% | 19% | 4.75% | 19% | 3.5% | 14% | 2.75% | 11% | 3% | 12%
Heat pump, up to 80 °C, Temp lift = 60 K | [17 empty] | 5.25% | 21% | 5.5% | 22% | 3.75% | 15% | 3.5% | 14% | 3.5% | 14%
Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | [17 empty] | 3% | 12% | 0.5% | 2% | 0% | 0% | 1.25% | 5% | 0% | 0%
High temperature heat pumps, up to 125 °C | [17 empty] | 5.75% | 23% | 6.5% | 26% | 4% | 16% | 4.25% | 17% | 4% | 16%
High temperature heat pumps, up to 150 °C | A, B | [16 empty] | 2.25% | 9% | 2.5% | 10% | 0.75% | 3% | 1.25% | 5% | 1.75% | 7%
Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | [17 empty] | 15.75% | 63% | 9% | 36% | 5.75% | 23% | 16.5% | 66% | 11.75% | 47%
Heat driven heat pumps, up to 80 °C | [17 empty] | 2% | 2% | 2% | 2% | 1% | 1% | 1% | 1% | 1% | 1%
|  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150
Temperature [°C]
Notes
| A | 0: The potential is limited by the available heat source at 80 °C
| B | 0: The heat pump can potentially cover, 24 %, 32 %, 17 %, 17 %, 18 %, of medium temperature in-direct for the five sectors 1., 2., 3., 4., 5, respectively

## 301.1a heat pump 60 C 40 K
Technology | Heat pump, up to 60 °C, Temp lift = 40 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1, 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 533 | 548.99 | 559.9698 | 565.5695 | 533 | 559.65 | 548.6024 | 576.8809 | B | 1, 3 | Heat pump, up to 60 °C, Temp lift = 40 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat pump, up to 60 °C, Temp lift = 40 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 528 | 543.99 | 554.9698 | 560.5695 | 528 | 554.65 | 543.6024 | 571.8809 | B,C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 1.4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16% | 0% | 16% | 0% | 13% | 0% | 7% | 0% | 11% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4% | 0% | 4% | 0% | 3.25% | 0% | 1.75% | 0% | 2.75%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1.4 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | [13 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 4 |  | Room heat | 12. spatial heating | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 4
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | E | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | F | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 4
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | 0.146 | 0.13 | 0.12 | 0.116 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | I
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019.
2 | Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
6 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 301.1b heat pump 70 C 50 K
Technology | Heat pump, up to 70 °C, Temp lift = 50 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1, 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 447 | 460.41 | 469.6182 | 474.3144 | 447 | 469.35 | 460.085 | 483.8007 | B | 1, 3 | Heat pump, up to 70 °C, Temp lift = 50 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat pump, up to 70 °C, Temp lift = 50 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 442 | 455.41 | 464.6182 | 469.3144 | 442 | 464.35 | 455.085 | 478.8007 | B,C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 1.4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 19% | 0% | 19% | 0% | 14% | 0% | 11% | 0% | 12% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4.75% | 0% | 4.75% | 0% | 3.5% | 0% | 2.75% | 0% | 3%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1.4 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 4 |  | Room heat | 12. spatial heating | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 4
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | E | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | F | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 4
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | 0.146 | 0.13 | 0.12 | 0.116 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | I
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019.
2 | Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
6 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 301.1c heat pump 80 C 60 K
Technology | Heat pump, up to 80 °C, Temp lift = 60 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1, 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 388 | 399.64 | 407.6328 | 411.7091 | 388 | 407.4 | 399.3579 | 419.9433 | B | 1, 3 | Heat pump, up to 80 °C, Temp lift = 60 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat pump, up to 80 °C, Temp lift = 60 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 383 | 394.64 | 402.6328 | 406.7091 | 383 | 402.4 | 394.3579 | 414.9433 | B,C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 1.4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 22% | 0% | 15% | 0% | 14% | 0% | 14% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 5.25% | 0% | 5.5% | 0% | 3.75% | 0% | 3.5% | 0% | 3.5%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1.4 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 4
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | E | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | F | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 4
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | 0.146 | 0.13 | 0.12 | 0.116 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | I
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019.
2 | Technological data for energy plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
6 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 301.2 heat_cool hp 80 C 75 K
Technology | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | 1,3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 333 | 342.99 | 349.8498 | 353.3483 | 333 | 349.65 | 342.7478 | 360.4153 | B,C | 1,3 | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 328 | 337.99 | 344.8498 | 348.3483 | 328 | 344.65 | 337.7478 | 355.4153 | D |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 4 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 4 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 12% | 0% | 2% | 0% | 0% | 0% | 5% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 3% | 0% | 0.5% | 0% | 0% | 0% | 1.25% | 0% | 0%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | E | 1 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 1 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 4 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | [9 empty] | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 1
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.73 | 0.65 | 0.6 | 0.58 | [5 empty] | 1,5
- of which equipment (%) | 60 | 60 | 60 | 60 |  |  |  |  | F | 6
- of which installation (%) | 40 | 40 | 40 | 40 |  |  |  |  | G | 6
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4,6
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.16 | 3.12 | [5 empty] | 4
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | H
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.65 | 1.6 | [5 empty] | 4
Technology specific data
Indirect investments cost (M€ per MW) | [8 empty] | I
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 15 | 15 | 15 | 15 |  |  |  |  | K
Temperature heat source return (°C) | 5 | 5 | 5 | 5 |  |  |  |  | K
Cooling generation capacity for one unit (MW) | 2.0991 | 2.1253 | 2.1425 | 2.151 |  |  |  |  | K
References
1 | Viegand Maagøe, 2019.
2 | Energistyrelsen, Technological data for energy plants (Compressions Heat Pumps for DH), 2017
3 | EHPA, Large Scale heat pumps in Europe, 2019
4 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
5 | Pieper, H. et al., Allocation of investment costs for large-scale heat pumps supplying district heating, 2018
6 | http://www.planenergi.dk/varmepumper/. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014. [Online]
7 | Danish Energy Agency, Inspirationskatalog for store varmepumper, 2017
Notes
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Manufacturer software calculations
D | Based on lost production during startup/shutdown
E | May vary depending on heat source
F | Very individual, can vary ÷ 20 %
G | Very individual, can vary + 20 %
H | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
I | Going from simple implementation to potential
J | Not relevant to this technology
K | Process cooling

## 302.a High temp. hp Up to 125 C
Technology | High temperature heat pumps, up to 125 °C | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 1.5 | 1.5 | 1.5 | 1.5 | 0.5 | 5 | 0.5 | 5 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 260 | 275 | 285 | 290 | 260 | 302.5 | 260 | 319 |  | 1.5 | High temperature heat pumps, up to 125 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | High temperature heat pumps, up to 125 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 255 | 270 | 280 | 285 | 255 | 297.5 | 255 | 314 | B |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 7 | 1 | 7 |  | 2 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | C | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 23% | 0% | 26% | 0% | 16% | 0% | 17% | 0% | 16% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 5.75% | 0% | 6.5% | 0% | 4% | 0% | 4.25% | 0% | 4%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.4 | 0.8 | D | 2 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 25 | 25 | 25 | 25 |  |  |  |  | E | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 9
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 9
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.8712 | 0.7788 | 0.73 | 0.7 | [5 empty] | 1, 3, 4
- of which equipment (%) | 40 | 40 | 40 | 40 | [5 empty] | 4
- of which installation (%) | 60 | 60 | 60 | 60 | [5 empty] | 4
Fixed O&M (€/MJ/s/year) | 970 | 870 | 800 | 720 | [5 empty] | 5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.22 | 3.12
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | F | 3
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.7 | 1.6 | [5 empty] | 2
Technology specific data
Indirect investments cost (M€ per MW) | 0.17424 | 0.15576 | 0.146 | 0.14 |  |  |  |  | G
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 40 | 40 | 40 | 40 |  |  |  |  | H
Temperature heat source return (°C) | 10 | 10 | 10 | 10 |  |  |  |  | H
Cooling generation capacity for one unit (MW)
References
1 | Viegand Maagøe, 2019
2 | http://www.planenergi.dk/varmepumper/.
3 | Teknologisk instutut, Hybridvarmepumpe til fjernvarme, 2018
4 | Energiforskning, Højtemperatur varmepumper kan bruge lavtemperatur spildvarme, 2013
5 | Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
Notes
A | 0,5-5 MW
B | Calculated from start-up loss
C | May vary depending on heat source availability
D | Slightly higher than large heat pumps [11]
E | Theoretically as low as 10 %. For screw as low as 25 %, lower than that will affect the performance drastically.
F | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
G | Going from current implementation to potential
H | Uses waste heat

## 302.b High temp. hp Up to 150
Technology | High temperature heat pumps, up to 150 °C | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 1.5 | 1.5 | 1.5 | 1.5 | 0.5 | 5 | 0.5 | 5 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 300 | 310 | 320 | 325 | 310 | 341 | 310 | 357.5 |  | 1.5 | High temperature heat pumps, up to 150 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | High temperature heat pumps, up to 150 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 295 | 305 | 315 | 320 | 305 | 336 | 305 | 352.5 | B |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 7 | 1 | 7 |  | 2 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | C | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 9% | 0% | 10% | 0% | 3% | 0% | 5% | 0% | 7% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 2.25% | 0% | 2.5% | 0% | 0.75% | 0% | 1.25% | 0% | 1.75%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.4 | 0.8 | D | 2 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 25 | 25 | 25 | 25 |  |  |  |  | E | 4 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.25 | 0.25 | 0.25 | 0.25 | [5 empty] | 9
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 9 | Notes
Environment | [10 empty] | I | The potential is limited by the available heat source at 80 °C, of which the efficiencies are valied.
SO2 (g per GJ fuel) | Cf. the utilized electricity | [9 empty] | J | The heat pump can potentially cover, 24 %, 32 %, 17 %, 17 %, 18 %, of medium temperature in-direct for the five sectors 1., 2., 3., 4., 5, respectively. But if these potentials are used, the efficiencies needs to be corrected
PM2.5 (g per GJ fuel) | [10 empty] | K | More information on the application potential can be found in the sheet tab "HP APP POT overlap"
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 1.0454 | 0.93456 | 0.876 | 0.84 |  |  |  |  | F | 1, 3, 4
- of which equipment | 40 | 40 | 40 | 40 | [5 empty] | 4
- of which installation | 60 | 60 | 60 | 60 | [5 empty] | 4
Fixed O&M (€/MJ/s/year) | 970 | 870 | 800 | 720 | [5 empty] | 5
Variable O&M (€/MWh) | 3.26 | 3.2 | 3.22 | 3.12
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | G | 3
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.7 | 1.6 | [5 empty] | 2
Technology specific data
Indirect investments cost (M€ per MW) | 0.20909 | 0.18691 | 0.1752 | 0.168 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 80 | 80 | 80 | 80 |  |  |  |  | I
Temperature heat source return (°C) | 50 | 50 | 50 | 50 |  |  |  |  | I
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, 2019
2 | http://www.planenergi.dk/varmepumper/.
3 | Teknologisk instutut, Hybridvarmepumpe til fjernvarme, 2018
4 | Energiforskning, Højtemperatur varmepumper kan bruge lavtemperatur spildvarme, 2013
5 | Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
Notes
A | 0,5-5 MW
B | Calculated from start-up loss
C | May vary depending on heat source availability
D | Slightly higher than large heat pumps [11]
E | Theoretically as low as 10 %. For screw as low as 25 %, lower than that will affect the performance drastically.
F | Corrected to technology readiness level (Not commercially avaiable at the moment)
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Going from current implementation to potential
I | Uses waste heat

## 303 Booster hp 150 C 130 K
Technology | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 4 | 4 | 4 | 4 | 1 | 10 | 1 | 15 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 198 | 203.94 | 208.0188 | 210.099 | 198 | 207.9 | 203.796 | 214.301 | B,C |  | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Booster heat pump, up to 150 °C, Temp lift = 130 K, steam | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 193 | 198.94 | 203.0188 | 205.099 | 193 | 202.9 | 198.796 | 209.301 | D |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 | E |  |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | E |  |  | Medium temperature | 2. Heating/Boiling | x | 0% | 63% | 0% | 36% | 0% | 23% | 0% | 66% | 0% | 47% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 15.75% | 0% | 9% | 0% | 5.75% | 0% | 16.5% | 0% | 11.75%
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | E |  |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 | E |  |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.4 | 0.8 | F |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | [9 empty] | 1 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E
Cold start-up time (hours) | 1 | 1 | 1 | 1 |  |  |  |  | E
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 1.6321 | 1.3231 | 1.037 | 0.93368 |  |  |  |  | G
- of which equipment (%) | 50 | 50 | 50 | 50 |  |  |  |  | H
- of which installation (%) | 50 | 50 | 50 | 50 |  |  |  |  | I
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 |  |  |  |  | E
Variable O&M (€/MWh) | 3.44 | 3.37 | 3.335 | 3.28
- of which is electricity costs (€/MWh) | 1.46 | 1.5 | 1.52 | 1.52 |  |  |  |  | J
- of which is other O&M costs (€/MWh) | 1.98 | 1.87 | 1.815 | 1.76 |  |  |  |  | K
Technology specific data
Indirect investments cost (M€ per MW) | 0.32641 | 0.26462 | 0.2074 | 0.18674 |  |  |  |  | L
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | M
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | 30 | 30 | 30 | 30 |  |  |  |  | N
Temperature heat source return (°C) | 20 | 20 | 20 | 20 |  |  |  |  | N
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | https://www.sciencedirect.com/topics/engineering/partial-load
2 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
3 | Van der Spek, et. Al., Challenges and uncertainties of ex ante techno-economic analysis of low TRL CO2 capture technology: Lessons from a case study of an NGCC with exhaust gas recycle and electric swing adsorption, 2017
Notes
A | 1-15 MW
B | Utilising waste heat above 30 °C will increase COP. Waste heat up to 75 °C can be utilised
C | Calculated from manufacturer software and manufacturer offer.
D | Based on lost production during startup/shutdown
E | Assumed similar to electrical compression heat pump and mechanical vapor recompression technologies
F | Assumed similar to high temperature heat pump technologies
G | From [2], cost correlations and learing curves [3] (Not commercially avaiable at the moment)
H | Very individual, can vary ÷ 10 %
I | Very individual, can vary + 10 %
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
K | Assumed 10 % higher than electrical compression heat pump. The turbo compressors have low O&M
L | Going from simple implementation to potential
M | Not relevant to this technology
N | Uses waste heat

## 304 Heat driven hp 80 C
Technology | Heat driven heat pumps, up to 80 °C | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 12 | 12 | 12 | 12 | 1 | 20 | 1 | 30 | A,B | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 170 | 171 | 172 | 173 | 170 | 180 | 170 | 180 |  | 1 | Heat driven heat pumps, up to 80 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Heat driven heat pumps, up to 80 °C | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 168 | 169 | 170 | 171 | 168 | 178 | 168 | 178 | C |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 3 |  | 1 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 1 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 2% | 0% | 2% | 0% | 1% | 0% | 1% | 0% | 1% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 2% | 0% | 2% | 0% | 1% | 0% | 1% | 0% | 1%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 1 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 20 | 30 | 20 | 30 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7 |  | 1 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | [9 empty] | 1 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 1
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized heat
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.56 | 0.51 | 0.48 | 0.46 | [5 empty] | 1
- of which equipment (%) | 50 | 50 | 50 | 50 | [5 empty] | 2
- of which installation (%) | 50 | 50 | 50 | 50 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1
Variable O&M (€/MWh) | 1.01 | 1 | 1 | 0.99 | [5 empty] | 1
- of which is electricity costs (€/MWh) | 0.73 | 0.75 | 0.76 | 0.76 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.28 | 0.25 | 0.24 | 0.23 | [5 empty] | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | E
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized heat
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | 4.9412 | 4.9825 | 5.0233 | 5.0636 |  |  |  |  | F
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
2 | Viegand Maagøe, 2019.
Notes
A | 1-30 MW
B | A single unit is roughly limited to 6 MW, due to size, but the units are often connected to one unit at the site. Giving the possibility for larger capacities.
C | Based on lost production during startup/shutdown
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology
F | Only relevant if heat source are process cooling

## 305 MVR 5 K
Technology | Mechanical vapor recompression | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 5 | 50 | 5 | 50 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 1260 | 1320 | 1380 | 1430 | 1000 | 1512 | 1056 | 1716 | B | 1 | Mechanical vapor recompression | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Mechanical vapor recompression | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 1210 | 1270 | 1330 | 1380 | 950 | 1462 | 1006 | 1666 |  |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 2 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 31% | 0% | 5% | 0% | 37% | 0% | 41% | 0% | 6% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 31% | 0% | 5% | 0% | 37% | 0% | 41% | 0% | 6%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 15 | 35 | 15 | 35 |  | 1.2 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | 1.3 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 4 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Cold start-up time (hours) | 1 | 1 | 1 | 1 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.35 | 0.33 | 0.32 | 0.31 | [5 empty] | 1.5
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 1.5
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 1.5
Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 200 | 2000 | [5 empty] | 2
Variable O&M (€/MWh) | 2.53 | 2.45 | 2.46 | 2.36 | [5 empty] | 2
- of which is electricity costs (€/MWh) | 0.73 | 0.75 | 0.76 | 0.76 |  |  |  |  | C | 2
- of which is other O&M costs (€/MWh) | 1.8 | 1.7 | 1.7 | 1.6 | [5 empty] | 2
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | D
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | D
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, MVR, 2018
2 | Technological data for energi plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | Viegand Maagøe, 2019
4 | EPCON, EVAPORATION TECHNOLOGY, 2019
5 | EPCON investment cost offer, 2017.
Notes
A | 5-50 MW
B | Assumed temperature lift of 5 K (saturation temperatur)
C | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
D | Not relevant

## 306 Thermal gasification
Technology | Thermal Gasification | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 5 | 5 | 5 | 5 | 2 | 20 | 2 | 20 |  | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 1 | Thermal Gasification | High temperature | 6. Firing /Sintering | x | 0% | 0% | 75% | 0% | 50% | 0% | 20% | 0% | 60% | 0% | Thermal Gasification | High temperature | 6. Firing /Sintering | x | 0% | 0% | 30% | 0% | 0% | 0% | 20% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 1 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.035 | 0.035 | 0.035 | 0.035 | 0.02 | 0.05 | 0.02 | 0.05 |  | 2 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 1 | 0 | 1 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 75% | 0% | 80% | 0% | 60% | 0% | 60% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 30% | 0% | 30% | 0% | 30% | 0% | 30% | 0%
Planned outage (weeks per year) | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 2 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 3 | 3 | 3 | 3 | [5 empty] | 2
Cold start-up time (hours) | 30 | 30 | 30 | 30 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Depends on fuel and operation
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 2 | 1.8 | 1.6 | 1.5 |  |  |  |  | B, E | 1, 2
- of which equipment (%) | 70 | 70 | 70 | 70 | [5 empty] | 2
- of which installation (%) | 30 | 30 | 30 | 30 | [5 empty] | 2
Fixed O&M (€/MJ/s/year) | 13500 | 12375 | 11250 | 10125 |  |  |  |  | B, D | 1, 2
Variable O&M (€/MWh) | 1.0255 | 0.94292 | 0.85993 | 0.7766 | [5 empty] | 1, 2
- of which is electricity costs (€/MWh) | 0.02555 | 0.02625 | 0.0266 | 0.0266 |  |  |  |  | C | 1, 2
- of which is other O&M costs (€/MWh) | 1 | 0.91667 | 0.83333 | 0.75 |  |  |  |  | B | 1, 2
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | F | -
Non energy gains (M€ per MW) | - | - | - | - | [5 empty] | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Viegand Maagøe, Thermal Gasification Direct in Process v01, 2018
2 | Dall Energy, Correspondance 2019
3 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
Notes
A | The efficiency of the thermal gasifier is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Parameter based on current prices, since the technology is still not mature a 25% reduction is expected over the next 30 years. Projections have been carried out by Viegand Maagøe.
C | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
D | If the unit is used at temperatures above 1000 °C additional costs has to be introduced as wear on the insulation will increase.
E | Prices include both gasifier, biomass storage and direct firing unit.
F | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 307 Hotdisc
Technology | Hotdisc | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 50 | 50 | 50 | 50 | 10 | 100 | 10 | 100 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 91 | 92 | 93 | 90 | 98 | 90 | 98 |  | 1 | Hotdisc | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 15% | 0% | 0% | 0% | 0% | 0% | Hotdisc | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 90 | 91 | 92 | 93 | 90 | 98 | 90 | 98 |  | 1 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 1 |  | Medium temperature | 2. Heating/Boiling |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 1 |  |  | 3. Drying | [13 empty] | 3. Drying
Technical lifetime (years) | 20 | 20 | 20 | 20 | 20 | 30 | 20 | 30 |  | 1 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 1 | 0.75 | 1 |  | 1 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | [13 empty] | 8.Other processes <150⁰C,
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 1 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 1
Cold start-up time (hours) | 54 | 54 | 54 | 54 |  |  |  |  | B | 1
Environment
SO2 (g per GJ fuel) | 8.3 | 8.3 | 8.3 | 8.3 |  |  |  |  | C | 2
PM2.5 (g per GJ fuel) | 0.29 | 0.29 | 0.29 | 0.29 |  |  |  |  | C | 2
NOX (g per GJ fuel) | 56 | 45 | 28 | 11 |  |  |  |  | C | 3
CH4 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | C | 3
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 |  |  |  |  | C | 3
Financial data
Nominal investment (M€ per MW) | 0.5 | 0.465 | 0.485 | 0.45 |  |  |  |  | D
- of which equipment (%) | 50 | 50 | 50 | 50
- of which installation (%) | 50 | 50 | 50 | 50
Fixed O&M (€/MJ/s/year) | 400 | 400 | 400 | 400
Variable O&M (€/MWh) | 1.175 | 1.195 | 1.205 | 1.205
- of which is electricity costs (€/MWh) | 0.73 | 0.75 | 0.76 | 0.76
- of which is other O&M costs (€/MWh) | 0.445 | 0.445 | 0.445 | 0.445
Technology specific data
Indirect investments cost (M€ per MW) | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup)
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 |  |  |  |  | F | 4,5
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | FLSmidth, Personal communication, 2019
2 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
3 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
4 | European Commision, The potential for CCS and CCU in Europe, 2019
5 | Sampo Kour, et Al., The potential for CCUS in selected industrial sectors – summary ofconcept evaluations in Finland, 2017
Notes
A | 10-100 MW
B | 36-72 hours
C | Assumed equal to waste used in incineration power plant
D | Includes retrofit to existing system
E | If a rebuillt of the system is necessary, this cost need to be included. E.g. if a cement oven is a separate line and not inline system.
F | Typically engineered to remove 80-90 %, above 95 % is possible
G | The fuel is waste and the waste needs minimum pre-handling. Large pieces of waste can be fired directly in the Hotdisc. Cost of waste will be lower than at an inceration plant

## 308 Dielectric heating
Technology | Dielectric heating | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.2 | 0.01 | 0.2 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 95 | 95 | 95 | 95 | 85 | 100 | 85 | 100 | B | 2 | Dielectric heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Dielectric heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 95 | 95 | 95 | 95 | 85 | 100 | 85 | 100 |  |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 5% | 2% | 3% | 1% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 5% | 2% | 3% | 1% | 0% | 0%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 30 | 30 | 30 | 30 | 20 | 35 | 20 | 35 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.1 | 0.05 | 0.1 |  | 3 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | [13 empty] | 8.Other processes <150⁰C,
Minimum load (% of full load) | 10 | 10 | 10 | 10 |  |  |  |  | C | 5 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 5
Cold start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 5
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 2.7 | 2.619 | 2.538 | 2.43 |  |  |  |  | D | 6,7,8
- of which equipment (%) | 85 | 85 | 85 | 85 | [5 empty] | 9
- of which installation (%) | 15 | 15 | 15 | 15 | [5 empty] | 9
Fixed O&M (€/MJ/s/year) | 0 | 0 | 0 | 0
Variable O&M (€/MWh) | 45.823 | 45.825 | 45.826 | 45.826
- of which is electricity costs (€/MWh) | 0.073 | 0.075 | 0.076 | 0.076 |  |  |  |  | E
- of which is other O&M costs (€/MWh) | 45.75 | 45.75 | 45.75 | 45.75 |  |  |  |  | F | 6
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | G
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | H,I
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Thermex Thermatron, https://thermex-thermatron.com/industrial-microwave-generators/, 2019
2 | Technological Institute, https://www.dti.dk/industrial-microwave-processing/
3 | Viegand Maagøe, 2019
4 | Cellencor, https://www.cellencor.com, 2019
5 | Bi.Elle, http://www.microwaves.it/ing/company.htm, 2019
6 | A.M. Hasna, Microwave Processing Applications in Chemical Engineering: Cost Analysis, 2011
7 | Tony Koral, Considerations for Commercial Success, 2013 in new RF and Microwave Industrial Heating Applications
8 | Bi.Elle, Personal communication, 2019
9 | Beyond Zero Emissions Inc, Zero Carbon Industry Plan Electrifying Industry, 2018
Notes
A | 0,01-0,2 MW
B | Cooling system account for a small loss
C | The capacity is often specifically regulated to product flow
D | Can vary quite significantly, as different applications requires different additional subsystems.
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
F | The magnatron (microwave generator) has a lifetime of around 10.000 hours of operation. Replacement of magnatron are included here.
G | Not relevant
H | Infrared will have non energy gains, but it has not been possible to estimate.
I | Treatment times are up to 20 times faster than traditional systems.

## 309 Infrared (IR)
Technology | Infrared heating | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.2 | 0.01 | 0.2 | A | 1 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 96 | 96 | 96 | 96 | 90 | 100 | 90 | 100 | B,C | 2 | Infrared heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Infrared heating | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 96 | 96 | 96 | 96 | 90 | 100 | 90 | 100 |  |  |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.2 | 0 | 0.2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 3% | 2% | 3% | 1% | 0% | 5% |  | Medium temperature | 2. Heating/Boiling | x | 5% | 4% | 5% | 5% | 3% | 2% | 3% | 1% | 0% | 5%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 30 | 30 | 30 | 30 | 20 | 35 | 20 | 35 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.1 | 0.05 | 0.1 |  | 3 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | [13 empty] | 8.Other processes <150⁰C,
Minimum load (% of full load) | 10 | 10 | 10 | 10 |  |  |  |  | D |  |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 2
Cold start-up time (hours) | 0 | 0 | 0 | 0 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.35 | 0.34 | 0.33 | 0.315 |  |  |  |  | E | 1
- of which equipment (%) | 85 | 85 | 85 | 85 |  |  |  |  | E | 2
- of which installation (%) | 15 | 15 | 15 | 15 |  |  |  |  | E | 2
Fixed O&M (€/MJ/s/year) | 0 | 0 | 0 | 0
Variable O&M (€/MWh) | 117.073 | 117.075 | 117.076 | 117.076
- of which is electricity costs (€/MWh) | 0.073 | 0.075 | 0.076 | 0.076 |  |  |  |  | F
- of which is other O&M costs (€/MWh) | 117 | 117 | 117 | 117 |  |  |  |  | G | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | I,J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Netek IR System A/S, Personal communication, 2019
2 | Beyond Zero Emissions Inc, Zero Carbon Industry Plan Electrifying Industry, 2018
3 | Viegand Maagøe, 2019
4 | IG Infrared, https://www.ig-infrared.com, 2019
5 | American Society of. Heating, Refrigerating and Air-Conditioning Engineers, ASHRAE Handbook – Heating, Ventilating, and Air-Conditioning Systems and Equipment (I-P Edition), 2008
Notes
A | 0,01-0,2 MW
B | The electricity to heat efficiency is 100 %, but not all of the electricity is converted to radiant energy [5]
C | A part of the electricity is conveted to convective heat, and some of it is lost to surrounding.
D | A system often consist of mulitiple emitters, giving the possiblity in turn emitters off individually.
E | Can vary quite significantly, as different applications requires different additional subsystems.
F | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
G | The emitters have a lifetime of 10.000 to 15.000 hours of operation. Replacement of emitters are included here.
H | Not relevant
I | Infrared will have non energy gains, but it has not been possible to estimate.
J | Heating time is 7 to 40 times faster than convective ovens. Uptake much less space which enable possible expansion.

## 310.1 Electric boiler steam
Technology | Electric boiler, 10 kV, steam | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 15 | 15 | 15 | 15 | 10 | 60 | 10 | 60 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 99 | 99 | 99 | 99 | 98 | 100 | 98 | 100 |  | 1,2 | Electric boiler, 10 kV, steam | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Electric boiler, 10 kV, steam | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 |  | 1,2 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1,2 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 |  | 1,2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 2 | 2 | 2 | 2 | [5 empty] | 2 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.03 | 0.03 | 0.03 | 0.03 | [5 empty] | 2
Cold start-up time (hours) | 0.17 | 0.17 | 0.17 | 0.17 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.08 | 0.07 | 0.07 | 0.07 |  |  |  |  | B,C | 1,2
- of which equipment (%) | 85 | 85 | 85 | 85 | [5 empty] | 1
- of which installation (%) | 15 | 15 | 15 | 15 | [5 empty] | 1
Fixed O&M (€/MJ/s/year) | 1070 | 1020 | 970 | 920 | [5 empty] | 1
Variable O&M (€/MWh) | 0.865 | 0.875 | 0.78 | 0.78
- of which is electricity costs (€/MWh) | 0.365 | 0.375 | 0.38 | 0.38 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.5 | 0.5 | 0.4 | 0.4 | [5 empty] | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | E
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
2 | AS:scan, Personal communication, 2019
3 | Tjæreborg Industri, Personal communication, 2019
Notes
A | 10-60 MW
B | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
C | Investment cos is slightly higher than for a hot water boiler.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology

## 310.2 Electric boiler hot water
Technology | Electric boiler, 10 kV, hot water | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 15 | 15 | 15 | 15 | 10 | 60 | 10 | 60 | A | [5 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 99 | 99 | 99 | 99 | 98 | 100 | 98 | 100 |  | 1,2 | Electric boiler, 10 kV, hot water | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Electric boiler, 10 kV, hot water | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 |  | 1,2 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1,2 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.5 | 1 | 0.5 | 1 |  | 1,2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 1 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1 |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 5 | 5 | 5 | 5 | [5 empty] | 1 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.008 | 0.008 | 0.008 | 0.008 | [5 empty] | 1
Cold start-up time (hours) | 0.08 | 0.08 | 0.08 | 0.08 | [5 empty] | 1
Environment
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.07 | 0.06 | 0.06 | 0.06 |  |  |  |  | B,C | 1,2
- of which equipment (%) | 85 | 85 | 85 | 85 | [5 empty] | 1
- of which installation (%) | 15 | 15 | 15 | 15 | [5 empty] | 1
Fixed O&M (€/MJ/s/year) | 1070 | 1020 | 970 | 920 | [5 empty] | 1
Variable O&M (€/MWh) | 0.865 | 0.875 | 0.78 | 0.78
- of which is electricity costs (€/MWh) | 0.365 | 0.375 | 0.38 | 0.38 |  |  |  |  | D
- of which is other O&M costs (€/MWh) | 0.5 | 0.5 | 0.4 | 0.4 | [5 empty] | 1
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | E
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2016
2 | AS:scan, Personal communication, 2019
3 | Tjæreborg Industri, Personal communication, 2019
Notes
A | 10-60 MW
B | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
C | Investment cos is slightly higher than for a hot water boiler.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology

## 311.1a Steam boiler Coal
Technology | Steam boiler, Coal | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 90 | 91 | 92 | 88 | 91.8 | 88 | 93.84 | B | 5,6,7,8 | Steam boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 89 | 89 | 90 | 91 | 87 | 90.8 | 87 | 92.84 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1.5 | 1 | 1.5 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.2 | 1.2 | 1.2 | 1.2 | 0.1 | 2.2 | 0.1 | 2.2 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 1.1 | 0.8 | 1.1 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 8 | 8 | 8 | 8 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 2.1 | 2.1 | 2.1 | 2.1 | [5 empty] | 9
NOX (g per GJ fuel) | 35 | 35 | 35 | 35 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.5 | 0.46576 | 0.446 | 0.44046 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 32600 | 31600 | 30600 | [5 empty] | 3
Variable O&M (€/MWh) | 1.903 | 1.925 | 1.936 | 1.936 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.803 | 0.825 | 0.836 | 0.836 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Nordic Suger operates a 33 MW - which is considered above average
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed slightly higher than gas boiler
D | Estimated based on gas boiler and coal CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Not relevant to this technology

## 311.1b Steam boiler Oil
Technology | Steam boiler, Oil | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 95 | 96 | 97 | 97 | 90 | 98 | 90 | 98 | B | 5,6,7,8 | Steam boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 94 | 95 | 96 | 96 | 89 | 97 | 89 | 97 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.1 | 1.1 | 1.1 | 1.1 | 0.09 | 2.1 | 0.09 | 2.1 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.8 | 0.5 | 0.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 25 | 20 | 18 | 15 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.055 | 0.046576 | 0.0446 | 0.044046 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 1800 | 1700 | 1600 | 1500 | [5 empty] | 3
Variable O&M (€/MWh) | 1 | 0.9 | 0.9 | 0.9 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 0.8978 | 0.81 | 0.8164 | 0.824 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Tjærborg Industri have boiler range up to 50 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed equal to gasboiler
D | Estimated based on gas boiler and coal CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Not relevant to this technology

## 311.1c Steam boiler Gas
Technology | Steam boiler, Natural gas or biogas | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 93 | 94 | 94 | 95 | 90 | 96 | 90 | 97 | B | 5,6,7,8 | Steam boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 92 | 93 | 93 | 94 | 89 | 95 | 89 | 96 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 30 | 25 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | C | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.054545 | 0.045455 | 0.045455 | 0.045455 |  |  |  |  | D | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | E | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | F
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | F
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Will be reduced if carbon capture in installed
D | 20 %-point lower for hot water boiler
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
F | Not relevant to this technology

## 311.1d Steam boiler Gas cond
Technology | Steam boiler, Natural gas or biogas (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 103 | 104 | 104 | 104 | 95 | 106 | 96 | 107 |  | 5,6,7,8,10 | Steam boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Steam boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 101 | 103 | 103 | 103 | 94 | 105 | 95 | 106 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | B | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.06 | 0.05 | 0.05 | 0.05 |  |  |  |  | C | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | D | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | E
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | Will be reduced if carbon capture in installed
C | 20 %-point lower for hot water boiler
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Not relevant to this technology

## 311.1e Steam boiler Wood
Technology | Steam boiler, Wood Chips | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 90 | 90 | 91 | 89 | 92 | 90 | 93 | B | 5,6,7,8 | Steam boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | Steam boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 100%
Total efficiency, net (%), annual average | 89 | 89 | 89 | 90 | 88 | 91 | 89 | 92 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 100% | 0% | 100% | 0% | 97% | 0% | 100% | 0% | 100%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.61818 | 0.59091 | 0.56364 | 0.53636 |  |  |  |  | F,G,H,I | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 35900 | 34800 | 33700 |  |  |  |  | I | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | J | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | K
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | K
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed slightly higher than gas boiler
D | Estimated based on gas boiler and wood CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | 5 % higher for wood pellet
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
K | Not relevant to this technology

## 311.1f Steam boiler Wood cond
Technology | Steam boiler, Wood chips (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 | Steam boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Steam boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | B | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 21% | 0% | 0% | 0% | 0% | 0% | 9% | 0% | 0%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | C | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | x | [12 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation | x
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | D | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.68 | 0.65 | 0.62 | 0.59 |  |  |  |  | E,F,G,H | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 37000 | 35900 | 34800 | 33700 |  |  |  |  | H | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
11 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. Used for estimation of the efficiency for technology "09a Wood Chips HOP" heat only boilers, woodchips 6W in the Technology Data - Energy Plants for Electricity and District heating generation, version 0007 January 2020
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | Assumed slightly higher than gas boiler
C | Estimated based on gas boiler and wood CHP plant
D | Will be reduced if carbon capture in installed
E | Viegand Maagøe A/S experience
F | Future cost prediction is based on average cost development of other similar technologies.
G | 20 %-point lower for hot water boiler
H | 5 % higher for wood pellet
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Not relevant to this technology
L. | Assuming that the system is optimised at a inlet temperature of 40°C.
M. | The efficiency is for a plant using woodchips with a water content of 50% and wetting of the combusting air. If other types of wood- biomass is assumed the efficiency should be reduced accordingly.

## 311.2a Hot water boiler, Coal
Technology | Hot water boiler, Coal | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 90 | 90 | 91 | 92 | 88 | 91.8 | 88 | 92.92 |  | 5,6,7,8 | Hot water boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Coal | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 89 | 89 | 90 | 91 | 87 | 90.8 | 87 | 91.92 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1.5 | 1 | 1.5 | B | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.2 | 1.2 | 1.2 | 1.2 | 0.1 | 2.2 | 0.1 | 2.2 | C | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 1.1 | 0.8 | 1.1 | C | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 8 | 8 | 8 | 8 |  |  |  |  | D | 3, 9
PM2.5 (g per GJ fuel) | 2.1 | 2.1 | 2.1 | 2.1 | [5 empty] | 9
NOX (g per GJ fuel) | 35 | 35 | 35 | 35 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 1.5 | 1.5 | 1.5 | 1.5 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E,F | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 32600 | 31600 | 30600 | [5 empty] | 3
Variable O&M (€/MWh) | 1.903 | 1.925 | 1.936 | 1.936 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.803 | 0.825 | 0.836 | 0.836 |  |  |  |  | G | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | H
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | I
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Nordic Suger operates a 33 MW - which is considered above average
B | Assumed slightly higher than gas boiler
C | Estimated based on gas boiler and coal CHP plant
D | Will be reduced if carbon capture in installed
E | Viegand Maagøe A/S experience
F | Future cost prediction is based on average cost development of other similar technologies.
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
H | Relevant for hot water boiler, going from current potential to full potential
I | Not relevant to this technology

## 311.2b Hot water boiler Oil
Technology | Hot water boiler, Oil | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 96 | 97 | 98 | 98 | 90 | 98 | 90 | 98 | B | 5,6,7,8 | Hot water boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Oil | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 95 | 96 | 97 | 97 | 89 | 97 | 89 | 97 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1.1 | 1.1 | 1.1 | 1.1 | 0.09 | 2.1 | 0.09 | 2.1 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.8 | 0.5 | 0.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 25 | 20 | 18 | 15 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.044 | 0.037261 | 0.03568 | 0.035236 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 1800 | 1700 | 1600 | 1500 | [5 empty] | 3
Variable O&M (€/MWh) | 1 | 0.9 | 0.9 | 0.9 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 0.8978 | 0.81 | 0.8164 | 0.824 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | K
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Only a few plant of this type is in operation in Denmark. Tjærborg Industri have boiler range up to 50 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed equal to gasboiler
D | Estimated based on gas boiler and coal CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 20 %-point lower for hot water boiler
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Relevant for hot water boiler, going from current potential to full potential
K | Not relevant to this technology

## 311.2c Hot water boiler Gas
Technology | Hot water boiler, Natural gas or biogas | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 94 | 95 | 95 | 96 | 90 | 96 | 90 | 98 | B | 5,6,7,8 | Hot water boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Natural gas or biogas | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 93 | 94 | 94 | 95 | 89 | 95 | 89 | 97 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 30 | 25 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | C | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.043636 | 0.036364 | 0.036364 | 0.036364 |  |  |  |  | D | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | E | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | F
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | G
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Will be reduced if carbon capture in installed
D | 20 %-point lower for hot water boiler
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
F | Relevant for hot water boiler, going from current potential to full potential
G | Not relevant to this technology

## 311.d Hot water boiler Gas cond
Technology | Hot water boiler, Natural gas or biogas (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 103 | 104 | 104 | 104 | 95 | 106 | 96 | 107 |  | 5,6,7,8,10 | Hot water boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Natural gas or biogas (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 101 | 103 | 103 | 103 | 94 | 105 | 95 | 106 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 0.14 | 0.12 | 0.11 | 0.1 | 0.1 | 0.14 | 0.08 | 0.12 |  | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 1 | 1 | 1 | 1 | 0.08 | 2 | 0.08 | 2 |  | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 17% | 0% | 0% | 0% | 0% | 0% | 6% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4.25% | 0% | 0% | 0% | 0% | 0% | 1.5% | 0% | 0%
Planned outage (weeks per year) | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 |  | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 3
Cold start-up time (hours) | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | B | 3, 9
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 9
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.048 | 0.04 | 0.04 | 0.04 |  |  |  |  | C | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 2000 | 1900 | 1800 | 1700 | [5 empty] | 3
Variable O&M (€/MWh) | 1.1 | 1 | 1 | 1 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 0.1022 | 0.09 | 0.0836 | 0.076 |  |  |  |  | D | 3
- of which is other O&M costs (€/MWh) | 0.9978 | 0.91 | 0.9164 | 0.924 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | E
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | F
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Ranges from 0,5 to 50. Typical value of 20 MW
B | Will be reduced if carbon capture in installed
C | 20 %-point lower for hot water boiler
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Relevant for hot water boiler, going from current potential to full potential
F | Not relevant to this technology

## 311.2e Hot water boiler Wood
Technology | Hot water boiler, Wood Chips | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 91 | 91 | 91 | 92 | 90 | 93 | 91 | 94 | B | 5,6,7,8 | Hot water boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Wood Chips | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 90 | 90 | 90 | 91 | 89 | 92 | 90 | 93 |  | 5,6,7,8 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | C | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | D | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 67% | 0% | 57% | 0% | 50% | 0% | 51% | 0% | 41% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 16.75% | 0% | 14.25% | 0% | 12.5% | 0% | 12.75% | 0% | 10.25%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | D | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Room heat | 12. spatial heating | x | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | E | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.61818 | 0.59091 | 0.56364 | 0.53636 |  |  |  |  | F,G,H | 3,10
- of which equipment (%) | 60 | 60 | 60 | 60 | [5 empty] | 3
- of which installation (%) | 40 | 40 | 40 | 40 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 33700 | 35900 | 34800 | 33700 |  |  |  |  | H | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | I | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | J
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | K
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
C | Assumed slightly higher than gas boiler
D | Estimated based on gas boiler and wood CHP plant
E | Will be reduced if carbon capture in installed
F | Viegand Maagøe A/S experience
G | Future cost prediction is based on average cost development of other similar technologies.
H | 5 % higher for wood pellet
I | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
J | Relevant for hot water boiler, going from current potential to full potential
K | Not relevant to this technology

## 311.2fHot waterboiler Wood cond
Technology | Hot water boiler, Wood chips (Condensing) | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 20 | 20 | 20 | 20 | 1 | 50 | 1 | 50 | A | 3, 10 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 | Hot water boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Hot water boiler, Wood chips (Condensing) | High temperature | 6. Firing /Sintering |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 116.1896 | 116.1896 | 116.1896 | 116.1896 | 88 | 117 | 88 | 117 | L,M | 11 |  |  | 7. Melting /Casting | [13 empty] | 7. Melting /Casting
Auxiliary electricity consumption (% of heat gen) | 2.3 | 2.3 | 2.3 | 2.3 | 2.2 | 2.5 | 1.8 | 2.5 | B | 3 |  |  | 9. Other processes >150C | [13 empty] | 9. Other processes >150C
Forced outage (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C | 3 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 17% | 0% | 0% | 0% | 0% | 0% | 6% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 4.25% | 0% | 0% | 0% | 0% | 0% | 1.5% | 0% | 0%
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8 | C | 3 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 3,5,8 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering | x
Construction time (years) | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  |  |  |  | 5. Distillation | x | [12 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 3 |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0% |  | Room heat | 12. spatial heating | x | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 0%
Warm start-up time (hours) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 3
Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
SO2 (g per GJ fuel) | 11 | 11 | 11 | 11 |  |  |  |  | D | 3, 9
PM2.5 (g per GJ fuel) | 10 | 10 | 10 | 10 | [5 empty] | 9
NOX (g per GJ fuel) | 63 | 49 | 46 | 41 | [5 empty] | 3, 9
CH4 (g per GJ fuel) | 11 | 8 | 6 | 4 | [5 empty] | 3, 9
N2O (g per GJ fuel) | 3 | 3 | 1 | 1 | [5 empty] | 3, 9
Financial data
Nominal investment (M€ per MW) | 0.68 | 0.65 | 0.62 | 0.59 |  |  |  |  | E,F,G | 3,10
- of which equipment (%) | 65 | 65 | 65 | 65 | [5 empty] | 3
- of which installation (%) | 35 | 35 | 35 | 35 | [5 empty] | 3
Fixed O&M (€/MJ/s/year) | 37000 | 35900 | 34800 | 33700 |  |  |  |  | G | 3
Variable O&M (€/MWh) | 2.779 | 2.825 | 2.848 | 2.848 | [5 empty] | 3
- of which is electricity costs (€/MWh) | 1.679 | 1.725 | 1.748 | 1.748 |  |  |  |  | H | 3
- of which is other O&M costs (€/MWh) | 1.1 | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Technology specific data
Indirect investments cost (M€ per MW) | 0.035 | 0.03 | 0.03 | 0.03 |  |  |  |  | I
Non energy gains (M€ per MW) | - | - | - | - |  |  |  |  | J
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 3
Temperature heat source supply (°C)
Temperature heat source return (°C)
Cooling generation capacity for one unit (MW)
References
1 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
2 | Danish Energy Agency, Heating installations, 2016 (updated 2018).
3 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2019)
4 | Applied Technologies of New York, Steam vs hot water boiler, 2016.
5 | ETSAP, Industrial Combustion Boilers, IEA ETSAP 2010.
6 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., & Swithenbank, J. (2012). Condensing boiler applications in the process industry. Applied Energy, 89(1), 30–36.
7 | Vigants, G., Galindoms, G., Veidenbergs, I., Vigants, E., & Blumberga, D. (2015). Efficiency diagram for district heating system with gas condensing unit. Energy Procedia, 72, 119–126.
8 | EnergyVortex, ENERGY EFFICIENCY & INDUSTRIAL BOILER EFFICIENCY, 2010
9 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
10 | Tjærborg Industri, Olie og gas kedler, 2019
11 | Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. Used for estimation of the efficiency for technology "09a Wood Chips HOP" heat only boilers, woodchips 6W in the Technology Data - Energy Plants for Electricity and District heating generation, version 0007 January 2020
Notes
A | Plants for district heating is around 6 MW, and CHP ranging up to 200-300 MW. 20 MW is considered commom in industry
B | Assumed slightly higher than gas boiler
C | Estimated based on gas boiler and wood CHP plant
D | Will be reduced if carbon capture in installed
E | Viegand Maagøe A/S experience
F | Future cost prediction is based on average cost development of other similar technologies.
G | 5 % higher for wood pellet
H | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
I | Relevant for hot water boiler, going from current potential to full potential
J | Not relevant to this technology
L. | Assuming that the system is optimised at a inlet temperature of 40°C.
M. | The efficiency is for a plant using woodchips with a water content of 50% and wetting of the combusting air. If other types of wood- biomass is assumed the efficiency should be reduced accordingly.

## 312.a Direct firing Natural Gas
Technology | Direct Firing, Natural Gas | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 2.5 | 2.5 | 2.5 | 2.5 | 1 | 10 | 1 | 10 |  | 2 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 | Direct Firing, Natural Gas | High temperature | 6. Firing /Sintering | x | 100% | 0% | 100% | 0% | 100% | 0% | 20% | 0% | 100% | 0% | Direct Firing, Natural Gas | High temperature | 6. Firing /Sintering | x | 75% | 0% | 75% | 0% | 40% | 0% | 20% | 0% | 10% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 1 | 0.1 | 1 |  | 8, 9 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.5 | 0 | 0.5 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 100% | 0% | 100% | 0% | 100% | 0% | 100% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 75% | 0% | 75% | 0% | 30% | 0% | 75% | 0% | 0% | 0%
Planned outage (weeks per year) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2 |  |  | 3. Drying | x | [12 empty] | 3. Drying | x
Technical lifetime (years) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.04 | 0.01 | 0.04 |  | 2 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 6 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 2
Cold start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 2
Environment
SO2 (g per GJ fuel) | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 1 | Potential overlap for the full applcaition potential
PM2.5 (g per GJ fuel) | 0.1 | 0.1 | 0.1 | 0.1 | [5 empty] | 1 | [8 empty] | Nat Gas | 2.425% | 100%
NOX (g per GJ fuel) | 9 | 7 | 6 | 6 | [5 empty] | 1 | [8 empty] | Solid Fuels | 28.63% | 84.15%
CH4 (g per GJ fuel) | 3 | 2 | 2 | 2 | [5 empty] | 1 | [8 empty] | Electricity | 0% | 39.31%
N2O (g per GJ fuel) | 1 | 1 | 1 | 1 | [5 empty] | 1
Financial data
Nominal investment (M€ per MW) | 0.015 | 0.015 | 0.015 | 0.015 |  |  |  |  | B | 4, 7
- of which equipment (%) | 66.6667 | 66.6667 | 66.6667 | 66.6667 | [5 empty] | 7
- of which installation (%) | 33.3333 | 33.3333 | 33.3333 | 33.3333 | [5 empty] | 7
Fixed O&M (€/MJ/s/year) | 181.8182 | 177.2727 | 172.7273 | 154.5455 |  |  |  |  | C | 2, 1
Variable O&M (€/MWh) | 0.2825 | 0.2775 | 0.28 | 0.28 | [5 empty] | 1
- of which is electricity costs (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 |  |  |  |  | D | 7
- of which is other O&M costs (€/MWh) | 0.1 | 0.09 | 0.09 | 0.09 |  |  |  |  | C | 1
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | E | -
Non energy gains (M€ per MW) | - | - | - | - | [5 empty] | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 5
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | Milton Megatherm, Correspondance 2019
5 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
6 | Eclipse, Vortometric Burner Series Datasheet 128-3, 20/2/2015
7 | Viegand Maagøe assessment, 2019
8 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
9 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
Notes
A | The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Unit price is based on Miton Megatherms 2.5 MW burner, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
C | Assumed to be equal to 10% of the boiler O&M from [1].
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 312.b Direct firing Sold Fuels
Technology | Direct Firing Solid Fuels | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [6 empty] | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 | Direct Firing Solid Fuels | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 90% | 0% | 0% | 0% | 0% | 0% | Direct Firing Solid Fuels | High temperature | 6. Firing /Sintering | x | 0% | 0% | 0% | 0% | 60% | 0% | 0% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 1 | 0.1 | 1 | B | 8, 9 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.5 | 0 | 0.5 |  | 2 |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 0% | 0% | 0% | 0% | 70% | 0% | 0% | 0% | 0% | 0%
Planned outage (weeks per year) | 3.5 | 3.5 | 3.5 | 3.5 | 2 | 5 | 2 | 5 |  | 4 |  |  | 3. Drying | x, A | [12 empty] | 3. Drying | x
Technical lifetime (years) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 2, 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.01 | 0.01 | 0.01 | 0.01 | 0.001 | 0.015 | 0.001 | 0.015 | I | 2, 4 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 10 | 10 | 10 | 10 | [5 empty] | 6 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  |  | F | 2
Cold start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  |  | F | 2 | Notes
Environment | [10 empty] | A | Today, direct firing takes place in the sector 2. Commodity production to dry wood in the wood industry. The technology used here differs from the reviewed technology. The reviewed technology is not appliacable, therefore the application potential is set to zero.
SO2 (g per GJ fuel) | Depends on Fuel Mix | [9 empty] | Potential overlap for the full application potential
PM2.5 (g per GJ fuel) | [18 empty] | Nat Gas | 2.425% | 100%
NOX (g per GJ fuel) | [18 empty] | Solid Fuels | 28.63% | 84.15%
CH4 (g per GJ fuel) | [18 empty] | Electricity | 0% | 39.31%
N2O (g per GJ fuel)
Financial data
Nominal investment (M€ per MW) | 0.22 | 0.22 | 0.22 | 0.22 |  |  |  |  | E, G, H | 4, 7
- of which equipment (%) | 66.6667 | 66.6667 | 66.6667 | 66.6667 | [5 empty] | 7
- of which installation (%) | 33.3333 | 33.3333 | 33.3333 | 33.3333 | [5 empty] | 7
Fixed O&M (€/MJ/s/year) | 3400 | 3300 | 3200 | 3100 |  |  |  |  | C | 2, 1
Variable O&M (€/MWh) | 0.3253 | 0.3303 | 0.3328 | 0.3328 | [5 empty] | 2, 7
- of which is electricity costs (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 |  |  |  |  | D | 7
- of which is other O&M costs (€/MWh) | 0.1428 | 0.1428 | 0.1428 | 0.1428 |  |  |  |  | C | 7
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | J | -
Non energy gains (M€ per MW) | - | - | - | - | [5 empty] | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | 90 | 90 | 90 | 90 | [5 empty] | 5
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | FLSmidth - Burner & PLM for HOTDISC, Correspondance 2019
5 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
6 | FCT International Burners, Correspondance 2019.
7 | Viegand Maagøe assessment, 2019
8 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
9 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
Notes
A | The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Auxilliary consumption based on gas burner as the fan power is comparable. Electricity for fuel feed systems are not included.
C | Assumed to be equal to 10% of the coal boiler O&M from [1]. With gaseous or liquid fuels the O&M will be lower.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Unit price from FLSmidth, installed price and auxilliary equipment assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
F | The burner itself can start up quickly. However, in e.g. Cement industry the process equipment will limit the startup time to between 8 (warm) and 72 (cold) hours.
G | Capacity increase in multifuel burners comes with an attractive economy of scale. Going up 10 times in size will correspond toa 150% increase in pricing .
H | Auxilliary systems for solid fuels has been included, these correspond to a large part of the investment and will be a function of the chosen fuel.
I | Corresponds to a burner change, establishing a feed system has a longer construction period.
J | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 312.c Direct firing Electricity
Technology | Direct Firing, Electricity | [9 empty] | Full application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics |  | Current application potential |  |  | "x,n" indicate which end-use, n ref. to note" | 1.Food, beverages and tobacco |  | 2.Commodity production |  | 3.Cement and non-metallic mineral (+Extraction of gravel and stone) |  | 4.Chemical industry |  | 5.Metals, machinery and electronics
Energy/technical data | 2020 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref | Technology | [13 empty] | Technology
[5 empty] | Lower | Upper | Lower | Upper |  |  |  | Energy services | End-use | [12 empty] | Energy services | End-use
Heat generation capacity for one unit (MW) | 5 | 5 | 5 | 5 | 1 | 10 | 1 | 10 |  | 4 |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % |  |  |  |  | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect % | Direct % | Indirect %
Total efficiency, net (%), nominel load | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 | Direct Firing, Electricity | High temperature | 6. Firing /Sintering | x | 100% | 0% | 100% | 0% | 0% | 0% | 20% | 0% | 5% | 0% | Direct Firing, Electricity | High temperature | 6. Firing /Sintering | x | 50% | 0% | 50% | 0% | 0% | 0% | 20% | 0% | 0% | 0%
Total efficiency, net (%), annual average | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A | 2 |  |  | 7. Melting /Casting | x | [12 empty] | 7. Melting /Casting | x
Auxiliary electricity consumption (% of heat gen) | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 1 | 0.1 | 1 | B | 6, 7 |  |  | 9. Other processes >150C | x | [12 empty] | 9. Other processes >150C | x
Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | F | 4 |  | Medium temperature | 2. Heating/Boiling | x | 100% | 0% | 100% | 0% | 50% | 0% | 100% | 0% | 0% | 0% |  | Medium temperature | 2. Heating/Boiling | x | 50% | 0% | 50% | 0% | 25% | 0% | 40% | 0% | 0% | 0%
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | F | 4 |  |  | 3. Drying | x, A | [12 empty] | 3. Drying | x
Technical lifetime (years) | 12.5 | 12.5 | 12.5 | 12.5 | 10 | 15 | 10 | 15 |  | 4 |  |  | 4. Dewatering | [13 empty] | 4. Dewatering
Construction time (years) | 0.04 | 0.04 | 0.04 | 0.04 | 0.02 | 0.06 | 0.02 | 0.06 |  | 5 |  |  | 5. Distillation | [13 empty] | 5. Distillation
Regulation Ability | [12 empty] | 8.Other processes <150⁰C, | x | [12 empty] | 8.Other processes <150⁰C, | x
Minimum load (% of full load) | 15 | 15 | 15 | 15 |  |  |  |  | C | 4 |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | Room heat | 12. spatial heating |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Warm start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 5
Cold start-up time (hours) | 0.01 | 0.01 | 0.01 | 0.01 | [5 empty] | 5 | Notes
Environment | [10 empty] | A | Today the melting and hardening process in the metal industry is almost fully supplied by electricity and the potential noted here is just 5%. The potential denoted here is reduced to that which can be delivered by a heating element in an air flow.
SO2 (g per GJ fuel) | Cf. the utilized electricity
PM2.5 (g per GJ fuel) | [10 empty] | Potential overlap for the full applcaition potential
NOX (g per GJ fuel)
CH4 (g per GJ fuel) | [18 empty] | Nat Gas | 2.425% | 100%
N2O (g per GJ fuel) | [18 empty] | Solid Fuels | 28.63% | 84.15%
Financial data | [18 empty] | Electricity | 0% | 39.31%
Nominal investment (M€ per MW) | 0.06 | 0.06 | 0.06 | 0.06 |  |  |  |  | E | 4, 5
- of which equipment (%) | 66.6667 | 66.6667 | 66.6667 | 66.6667 | [5 empty] | 5
- of which installation (%) | 33.3333 | 33.3333 | 33.3333 | 33.3333 | [5 empty] | 5
Fixed O&M (€/MJ/s/year) | 0 | 0 | 0 | 0 |  |  |  |  | F | 4
Variable O&M (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 | [5 empty] | 2, 5
- of which is electricity costs (€/MWh) | 0.1825 | 0.1875 | 0.19 | 0.19 |  |  |  |  | D | 5
- of which is other O&M costs (€/MWh) | 0 | 0 | 0 | 0 |  |  |  |  | F | 4
Technology specific data
Indirect investments cost (M€ per MW) | - | - | - | - |  |  |  |  | G
Non energy gains (M€ per MW) | - | - | - | -
Startup cost (€/MW/startup) | - | - | - | -
Carbon capture removal of CO2 emissions (% of emission) | Cf. the utilized electricity
Temperature heat source supply (°C) | - | - | - | -
Temperature heat source return (°C) | - | - | - | -
Cooling generation capacity for one unit (MW) | - | - | - | -
References
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | SAN Electro Heat A/S , Correspondance 2019
5 | Viegand Maagøe assessment, 2019
6 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
7 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
Notes
A | Transformer electricity losses are not included, and the efficiency will thus be 100%.
B | Auxilliary consumption based on gas burner as the fan power is comparable. Any pretreatment (grinding, etc.) of the fuel is not included.
C | The regulation is dependant on the flow conditions and the subsequent surface temperature, the chosen value is an average.
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | Unit price from San Electro Heat, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
F | Units are composed of multiple heating elements, each unit is installed with backup elements that can be enabled if some of the elements fail, resulting in minimal downtime and O&M during the lifetime of the equipment.
G | The indirect costs will be too strong a function of the process to put into a single value across all industries.

## 401.a Post comb - small CHP
Technology | Post-combustion carbon capture retrofit - 100 MW(th) WtE or biomass CHP plant
| 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant capacity (t CO2 output / hour) | 32 | 32 | 32 | 34 | 34 | 30 | 34 | 33 | 35 | A
- Inputs at max capacity
A) Mass of Fluegas (t/t CO2 output) | 5.1 | 5.1 | 5.1 | 4.9 | 4.9 | 4.8 | 6 | 4.7 | 6
B1) CO2 share in fluegas input (%-vol, dry) | 15 | 15 | 15 | 15 | 15 | 12 | 15 | 12 | 15
B2) Flue gas temperature (0°C) | 35 | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40 | B
C1) Heat input (MWh/t CO2-output) | 0.833 | 0.833 | 0.72 | 0.66 | 0.66 | 0.66 | 1 | 0.55 | 0.72 | C
C2) Eletricity input (MWh/t CO2-output) | 0.03 | 0.03 | 0.025 | 0.023 | 0.02 | 0.025 | 0.035 | 0.017 | 0.025 | D
C3) Amine make-up (kg/t CO2-output) | 0.3 | 0.3 | 0.2 | 0.15 | 0.1 | 0.15 | 1.5 | 0.05 | 0.3
Y) Auxiliary products inputs (kg/t CO2-output )
- Outputs at max capacity
A2) CO2 purity prior to post cleaning (% vol) | 97 | 97 | 98 | 99 | 99 | 96 | 98 | 98 | 99 | E
A3) Total pressure of CO2 gas (kPa(a)) | 160 | 160 | 300 | 400 | 400 | 120 | 300 | 300 | 600 | F
Ax) CO2 capture rate, net (%) | 90 | 90 | 90 | 95 | 95 | 85 | 95 | 92 | 99 | G
C1) Heat out (MWh/t CO2-output) | 0.833 | 0.833 | 0.72 | 0.66 | 0.66 | 0.66 | 1 | 0.55 | 0.72
C2) Temperature of heat out (°C) | 60 | 60 | 60 | 70 | 70 | 50 | 80 | 50 | 120 | H
X) Other Non-energy outputs (kg/t CO2-output)
- other technical data
Forced outage (%) | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 2 | 2 | 4 | 2 | 3
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 4 | 2 | 3
Financial data
Specific investment (mill € /[t CO2 output/hour]) | 3.3 | 3 | 2.7 | 2.4 | 2 | 2.5 | 5 | 1.6 | 2.8 | I
- hereof capture plant (%) | 50 | 50 | 50 | 50 | 50 |  |  |  |  | J
- hereof CO₂ compression&dehydration (%) | 10 | 10 | 10 | 10 | 10 |  |  |  |  | K
- hereof utilities & flue gas integration (%) | 10 | 10 | 10 | 10 | 10
- hereof heat integration (%) | 15 | 15 | 15 | 15 | 15 |  |  |  |  | L
- hereof Owner's cost (%) | 15 | 15 | 15 | 15 | 15
Fixed O&M (mill € /[t CO2 output/Hour]) | 0.099 | 0.09 | 0.081 | 0.072 | 0.06 | 0.075 | 0.15 | 0.048 | 0.084 | M
Variable O&M (€ per t CO2 output) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5 | 3.5 | 1.5 | 3.5
Startup cost (€ per startup/[t CO2/hour]) | 25 | 25 | 25 | 25 | 25
Technology specific data
CO₂ compression and dehydration - Electricity input (MWh/t CO₂ output) | 0.1 | 0.1 | 0.085 | 0.075 | 0.075 | 0.09 | 0.11 | 0.07 | 0.09 | N
CO₂ compression and dehydration - Heat out (MWh/t CO₂ output) | 0.16 | 0.16 | 0.14 | 0.13 | 0.13 | 0.14 | 0.18 | 0.12 | 0.15 | N
References
1
2
3
Notes
A | CC capacity is chosen to match flue gas flow and CO₂ emission from a 100 MWth biomass boiler. Larger capacites available today if required.
B | The biomass CHP is assumed to be equipped with flue gas condensation, hence flue gas is available at 35 deg. C
C | Heat is supplied as low pressure steam 3-5 bara and (130-150 deg. C)
D | Electricity consumption includes additional CC plant, flue gas fan work and cooling water pumps, but no ID cooling tower, other utilities. CO₂ compression and drying not included.
E | Purity given on wet basis. On dry basis purity is >99.95%vol
F | CO₂ pressure at outlet flange. Future processes is expected to deliver CO₂ at higher pressure (save compression work)
G | The CO₂ capture percentage from the flue gas is expected to increase from today's 90% to 95% in 2050.
H | 20% of heat is available at 80 deg. C, 80% is available at 50 deg C. The reported 60 deg C is an weighed average.
I | Total cost including site integration and CO₂ compression. CAPEX is expected to decrease by 40% in 2050 as the market develops. Total capital investment is calculated as plant capacity (t CO₂ output/h) multiplied by the specific investment cost
J | If the CHP is euipped with flue gas condensation to <40 deg C the precooler of the CC plant may be omitted. The CC plant cost can in that case be reduced with 5% and the utility cost with 20% (because of less cooling requirement)
K | If CO₂ should be delivered liquefied for truck or road transport, a liquefaction plant must be added hence increase this post with 50% + interim storage (specified in chapter on CO₂ transport of Technology Catalogue)
L | Substantial cost have been included for heat integration which covers steam turbine modification, coupling to district heating net. Heat pump technology for upgrade of low temp waste heat not included.
M | Fixed O&M is taken as 3% of CAPEX
N | Assume compression from CC plant outlet pressure to 150 bar and drying to < 50 ppmv H₂O. Specific power consumption decrease with time as CO₂ is delivered at increasingly higher pressure from the CC plant

## 401.b Post comb - Large biomass
Technology | Post-combustion carbon capture retrofit - 500 MW(th) biomass-fired boiler
| 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant capacity (t CO2 output / hour) | 164 | 164 | 164 | 173 | 173 | 155 | 173 | 167 | 180
- Inputs at max capacity
A) Mass of Fluegas (t/t CO2 output) | 5.1 | 5.1 | 5.1 | 4.8 | 4.8 | 5.4 | 4.8 | 5 | 4.7
B1) CO2 share in fluegas input (%-vol, dry) | 17 | 17 | 17 | 17 | 17 | 15 | 17 | 15 | 17
B2) Flue gas temperature (°C) | 35 | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40 | B
C1) Heat input (MWh/t CO2-output) | 0.833 | 0.833 | 0.72 | 0.66 | 0.66 | 0.66 | 1 | 0.55 | 0.72 | C
C2) Eletricity input (MWh/t CO2-output) | 0.03 | 0.03 | 0.025 | 0.023 | 0.02 | 0.025 | 0.035 | 0.017 | 0.025 | D
C3) Amine make-up (kg/t CO2-output) | 0.3 | 0.3 | 0.2 | 0.15 | 0.1 | 0.15 | 1.5 | 0.05 | 0.3
Y) Auxiliary products inputs (kg/t CO2-output )
- Outputs at max capacity
A1) CO2 purity prior to post cleaning (% vol) | 97 | 97 | 98 | 99 | 99 | 96 | 98 | 98 | 99 | E
A2) Total pressure of CO2 gas (kPa(a)) | 160 | 160 | 300 | 400 | 400 | 120 | 300 | 300 | 600 | F
A3) CO2 capture rate, net (%) | 90 | 90 | 90 | 95 | 95 | 85 | 95 | 92 | 99
C1) Heat out (MWh/t CO2-output) | 0.833 | 0.833 | 0.72 | 0.66 | 0.66 | 0.66 | 1 | 0.55 | 0.72
C2) Temperature of heat out (°C) | 60 | 60 | 60 | 70 | 70 | 50 | 80 | 50 | 120 | H
X) Other Non-energy outputs (kg/t CO2-output)
- other technical data
Forced outage (%) | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 2 | 2 | 4 | 2 | 3
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Construction time (years) | 3 | 3 | 2.5 | 2 | 2 | 2 | 4 | 2 | 3
Financial data
Specific investment (mill € /[t CO2 output/hour]) | 2.7 | 2.5 | 2.3 | 2 | 1.6 | 2.2 | 3.7 | 1.2 | 2.2 | I
- hereof capture plant (%) | 50 | 50 | 50 | 50 | 50 |  |  |  |  | J
- hereof CO₂ compression&dehydration (%) | 10 | 10 | 10 | 10 | 10 |  |  |  |  | K
- hereof utilities & flue gas integration (%) | 10 | 10 | 10 | 10 | 10
- hereof heat integration (%) | 15 | 15 | 15 | 15 | 15 |  |  |  |  | L
- hereof Owner's cost (%) | 15 | 15 | 15 | 15 | 15
Fixed O&M (mill € /[t CO2 output/Hour]) | 0.081 | 0.075 | 0.069 | 0.06 | 0.048 | 0.066 | 0.111 | 0.036 | 0.066 | M
Variable O&M (€ per t CO2 output) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5 | 3.5 | 1.5 | 3.5
Startup cost (€ per startup/[t CO2/hour]) | 25 | 25 | 25 | 25 | 25
Technology specific data
CO₂ compression and dehydration - Electricity input (MWh/t CO₂ output) | 0.1 | 0.1 | 0.085 | 0.075 | 0.075 | 0.09 | 0.11 | 0.07 | 0.09 | N
CO₂ compression and dehydration - Heat out (MWh/t CO₂ output) | 0.16 | 0.16 | 0.14 | 0.13 | 0.13 | 0.14 | 0.18 | 0.12 | 0.15 | N
References
1
2
3
Notes
A | CC capacity is chosen to match flue gas flow and CO₂ emission from a 500 MWth biomass boiler
B | The biomass CHP is assumed to be equipped with flue gas condensation, hence flue gas is available at 35 deg. C
C | Heat is supplied as low pressure steam 3-5 bara and (130-150 deg. C)
D | Electricity consumption includes additional CC plant, flue gas fan work and cooling water pumps, but no ID cooling tower, other utilities. CO₂ compression and drying not included.
E | Purity given on wet basis. On dry basis purity is >99.95%vol
F | CO₂ pressure at outlet flange. Future processes is expected to deliver CO₂ at higher pressure (save compression work)
G | The CO₂ capture percentage from the flue gas is expected to increase from today's 90% to 95% in 2050.
H | 20% of heat is available at 80 deg. C, 80% is available at 50 deg C. The reported 60 deg C is an weighed average.
I | Total cost including CO₂ compression & drying, heat and site integration. CAPEX is expected to decrease by 40% in 2050 as the market develops. Total capital investment is calculated as plant capacity (t CO₂ output/h) multiplied by the specific investment cost.
J | If the CHP is euipped with flue gas condensation to <40 deg C the precooler of the CC plant may be omitted. The CC plant cost can in that case be reduced with 5% and the utility cost with 20% (because of less cooling requirement)
K | If CO₂ should be delivered liquefied for truck or road transport, a liquefaction plant must be added hence increase this post with 50% + interim storage (specified in chapter on CO₂ transport of Technology Catalogue)
L | Substantial cost have been included for heat integration which covers steam turbine modification, coupling to district heating net. Heat pump technology for upgrade of low temp waste heat not included.
M | Fixed O&M is taken as 3% of CAPEX
N | Assume compression from CC plant outlet pressure to 150 bar and drying to < 50 ppmv H₂O. Specific power consumption decrease with time as CO₂ is delivered at increasingly higher pressure from the CC plant

## 401.c Post comb - Cement kiln
Technology | Post-combustion carbon capture - Retrofit 4500 ton clinker per day cement kiln
| 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant capacity (t CO2 output / hour) | 152 | 152 | 152 | 160 | 160 | 144 | 160 | 155 | 167 | A
- Inputs at max capacity
A) Mass of Fluegas (t/t CO2 output) | 5.1 | 5.1 | 5.1 | 4.8 | 4.8 | 4 | 6.5 | 4 | 6.5
B1) CO2 share in fluegas input (%-vol, dry) | 20 | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30
B2) Flue gas temperature (°C) | 125 | 125 | 125 | 125 | 125 | 80 | 200 | 80 | 200 | B
C1) Heat input (MWh/t CO2-output) | 0.833 | 0.833 | 0.72 | 0.66 | 0.66 | 0.66 | 1 | 0.55 | 0.72 | C
C2) Eletricity input (MWh/t CO2-output) | 0.025 | 0.025 | 0.022 | 0.02 | 0.018 | 0.02 | 0.03 | 0.015 | 0.021 | D
C3) Amine make-up (kg/t CO2-output) | 0.3 | 0.3 | 0.2 | 0.15 | 0.1 | 0.15 | 1.5 | 0.05 | 0.3
Y) Auxiliary products inputs (kg/t CO2-output )
- Outputs at max capacity
A2) CO2 purity prior to post cleaning (% vol) | 97 | 97 | 98 | 99 | 99 | 96 | 98 | 98 | 99 | E
A3) Total pressure of CO2 gas (kPa(a)) | 160 | 160 | 300 | 400 | 400 | 120 | 300 | 300 | 600 | F
Ax) CO2 capture rate, net (%) | 90 | 90 | 90 | 95 | 95 | 85 | 95 | 92 | 99
C1) Heat out (MWh/t CO2-output) | 1.65 | 1.65 | 1.54 | 1.48 | 1.48 | 1.48 | 1.8 | 1.3 | 1.55
C2) Temperature of heat out (°C) | 60 | 60 | 60 | 70 | 70 | 50 | 80 | 50 | 120 | H
D) Flue gas condensate (t/t CO2-output) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | I
- other technical data
Forced outage (%) | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 2 | 2 | 4 | 2 | 3
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Construction time (years) | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 4 | 2 | 3.5
Financial data
Specific investment (mill € /[t CO2 output/hour]) | 3 | 2.8 | 2.6 | 2.2 | 1.8 | 2.8 | 5.2 | 1.4 | 2.4 | J
- hereof capture plant (%) | 45 | 45 | 45 | 45 | 45 |  |  |  |  | K
- hereof CO₂ compression&dehydration (%) | 10 | 10 | 10 | 10 | 10 |  |  |  |  | L
- hereof utilities & flue gas integration (%) | 10 | 10 | 10 | 10 | 10
- hereof heat integration and steam plant (%) | 20 | 20 | 20 | 20 | 20 |  |  |  |  | M
- hereof Owner's cost (%) | 15 | 15 | 15 | 15 | 15
Fixed O&M (mill € /[t CO2 output/Hour]) | 0.09 | 0.084 | 0.078 | 0.066 | 0.054 | 0.084 | 0.156 | 0.042 | 0.072 | N
Variable O&M (€ per t CO2 output) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5 | 3.5 | 1.5 | 3.5
Startup cost (€ per startup/[t CO2/hour]) | 25 | 25 | 25 | 25 | 25
Technology specific data
CO₂ compression and dehydration - Electricity input (MWh/t CO₂ output) | 0.1 | 0.1 | 0.085 | 0.075 | 0.075 | 0.09 | 0.11 | 0.07 | 0.09 | O
CO₂ compression and dehydration - Heat out (MWh/t CO₂ output) | 0.16 | 0.16 | 0.14 | 0.13 | 0.13 | 0.14 | 0.18 | 0.12 | 0.15 | O
References
1
2
3
Notes
A | CC capacity is chosen to match a cement kiln with production of 4500 tonne clinker per day. CO₂ generated from combusiton of additional fuel to provide heat to CC plant is not captured. Part of the heat demand may be recovered from the cement kiln
B | Cement kiln exhaust gas is assumed to be 125 deg C
C | Heat is supplied as low pressure steam 3-5 bara and 130-150 deg C
D | Electricity consumption includes additional CC plant, flue gas fan work and cooling water pumps, but no ID cooling tower, other utilities. CO₂ compression and drying not included.
E | Purity given on wet basis. On dry basis purity is >99.95%vol
F | CO₂ pressure at outlet flange. Future processes is expected to deliver CO₂ at higher pressure (save compression work)
G | This is the water vapour contained in the CO₂ product. This is recovered during compression and may be returned to the CC process
H | 20% of heat is available at 80 deg. C, 80% is available at 50 deg C. The reported 60 deg C is an weighed average.
I | Flue gas condensate is produced from pre-cooling of flue gas
J | Total retrofit cost including CC plant, steam plant/waste heat recovery units, utilities, cooling water, CO₂ compression and drying to pipeline specifications (150 bar) and integration costs. CAPEX is expected to decrease by 40% in 2050 as the market develops.
K | If the CHP is euipped with flue gas condensation to <40 deg C the precooler of the CC plant may be omitted. The CC plant cost can in that case be reduced with 5% and the utility cost with 20% (because of less cooling requirement)
L | If CO₂ should be delivered liquefied for truck or road transport, a liquefaction plant must be added hence increase this post with 50% + interim storage (specified in chapter on CO₂ transport of Technology Catalogue)
M | Cement plants typically don't have steam available for CC. Investment cost of steam plant and/or waste heat recovery boilers are included
N | Fixed O&M is taken as 3% of CAPEX
O | Assume compression from CC plant outlet pressure to 150 bar and drying to < 50 ppmv H₂O. Specific power consumption decrease with time as CO₂ is delivered at increasingly higher pressure from the CC plant

## 402.a Oxy-fuel- Large Biomass
Technology | Oxy-fuel carbon capture - Retrofit 500 MW biomass boiler excluding ASU
| 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant capacity (t CO2 output / hour) | 175 | 175 | 175 | 175 | 175 | 170 | 180 | 175 | 180 | A | 1
- Inputs at max capacity
A) Mass of Fluegas (t,/t CO2 output) | 2 | 1.9 | 1.85 | 1.8 | 1.8 | 2 | 1.8 | 2 | 1.8 |  | 1
B1) CO2 share in fluegas input (% vol) | 30% | 31% | 31% | 32% | 32% | 30% | 35% | 30% | 35% | B | 1
B2) H2O share in fluegas Input (% vol) | 58% | 60% | 60% | 62% | 62% | 58% | 62% | 58% | 62% |  | 1
C1) Heat input (MWh/t CO2-output) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1
C2) Eletricity input (MWh/t CO2-output) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C | 1
D) mass of O₂ input (ton O₂/ton CO₂ output) | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
- Outputs at max capacity
A2) CO2 purity prior to post cleaning (% vol) | 70% | 75% | 80% | 80% | 85% | 70% | 80% | 70% | 90% |  | 1
A3) Total pressure of CO2 gas (kPa(a)) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 1
Ax) CO2 capture rate, net (%) | 96.15% | 96.15% | 96.15% | 96.15% | 96.15% | 93.41% | 98.9% | 96.15% | 98.9% | D | 1
B1) Mass of H2O (t/t CO2-output) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.9 | 0.7 | 0.9 | E | 1
C1) Heat out (MW/t CO2-output/hour) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.55 | 0.4 | 0.55 | F
C2) Temperature of heat out (C) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
- other technical data
Forced outage (%) | 5% | 5% | 4% | 3% | 3% | 3% | 5% | 3% | 5%
Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 2 | 2 | 4 | 2 | 3
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Financial data
Specific investment (mill € /[t CO2 output/hour]) | 1.45 | 1.45 | 1.3775 | 1.3 | 1.15 | 1.2 | 2.6 | 0.95 | 2.1 | G
- hereof equipment (%)
- hereof installation (%)
Fixed O&M (mill € /[t CO2 output/Hour]) | 0.0435 | 0.0435 | 0.041325 | 0.039 | 0.0345 | 0.036 | 0.078 | 0.0285 | 0.063 | H
Variable O&M (€ per t CO2 output) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | I
Startup cost (€ per startup/[t CO2/hour]) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | J
Technology specific data
Specific investment optional O₂ plant (ASU) (mill € /[t CO2 output/ hour]) | 0.8 | 0.8 | 0.75 | 0.7 | 0.6 | 0.7 | 0.9 | 0.5 | 0.8 | K
Electricity input for optional O₂ plant (ASU) (MW/ton CO₂/h) | 0.19 | 0.18 | 0.16 | 0.15 | 0.15 | 0.18 | 0.2 | 0.125 | 0.175
Electricity input CO₂ post treatment (CPU) (MWh/t CO2-output) | 0.18 | 0.18 | 0.17 | 0.16 | 0.15 | 0.16 | 0.2 | 0.12 | 0.18
Heat output CO₂ post treatment (MWh/t CO₂ output) | 0.3 | 0.3 | 0.29 | 0.27 | 0.25 | 0.25 | 0.35 | 0.2 | 0.3
References
1 | Chris Spero, Toshihiko Yamada. Callide Oxyfuel Project, Final Results, March 2018. https://www.globalccsinstitute.com/archive/hub/publications/202090/cop-finalresults-publicreport-march2018.pdf
2
3
Notes
A | CC capacity is chosen to match flue gas flow and CO₂ emission from a 500 MWth biomass boiler
B | On wet basis, before flue gas condensation
C | Electricity for oxy-fuel retrofit plant is assumed unchanged when excluding ASU and CPU.
D | Some CO₂ is vented from CPU during purification. The capture rate provides the fraction of the CO₂ from the boiler which is captured
E | The amount of flue gas condensate produced is depending on fuel composition (moisture). This value is based on wood chips (wet fuel)
F | Cooling water for flue gas condensation. As mentioned in D) this depends on fuel composition.
G | Cost includes boiler modification and CO₂ purification unit (CPU) and compression to 150 bar for pipeline transport, but excludes O₂ production plant (ASU). Cost assumed to decrease by 20% up to 2050 as market develops
H | Fixed O&M is estimated as 3% of CAPEX.
I | Cost for make-up chemicals to CPU and disposal of acid waste. Power consumption for new flue gas recirculations fans assumed to equal reduced power at existing fans
J | Estimated value excluding ASU for O₂ production
K | An large O₂ source is required for an oxy-fuel plant. An ASU is therefore likely to be required.

## 402.b Oxy-fuel Cement
Technology | Oxy-fuel carbon caputre - Retrofit 3000 ton clinker per day cement kiln excluding ASU
| 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant capacity (t CO2 output / hour) | 94.5 | 94.5 | 94.5 | 100 | 100 | 90 | 100 | 95 | 104 | A | 1
- Inputs at max capacity
A) Mass of Fluegas (t/t CO2 output) | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.5 | 1.2 | 1.4 | 1.2 | B
B1) CO2 share in fluegas input (% vol) | 74 | 74 | 74 | 74 | 74 | 65 | 80 | 74 | 80 |  | 1
B2) H2O share in fluegas Input (% vol) | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.5 | 6 | 2.5 | 6 |  | 1
C1) Heat input (MWh/t CO2-output) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C2) Eletricity input (MWh/t CO2-output) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
D) mass of O₂ input (ton O₂/ton CO₂ output) | 0.38 | 0.38 | 0.38 | 0.36 | 0.36 | 0.41 | 0.36 | 0.38 | 0.35
- Outputs at max capacity
A2) CO2 purity prior to post cleaning (% vol) | 74 | 74 | 74 | 74 | 74 | 65 | 80 | 74 | 85
A3) Total pressure of CO2 gas (kPa(a)) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Ax) CO2 capture rate, net (%) | 90 | 90 | 90 | 95 | 95 | 85 | 95 | 90 | 99 | D | 1
B1) Mass of H2O (t/t CO2-output) | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.1 | 0.05 | 0.1 | E
C1) Heat out (MW/t CO2-output/hour)
C2) Temperature of heat out (C)
- other technical data
Forced outage (%) | 5% | 5% | 4% | 3% | 3% | 3% | 5% | 3% | 5%
Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 2 | 2 | 4 | 2 | 3
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Financial data
Specific investment (mill € /[t CO2 output/hour]) | 1.2 | 1.2 | 1.15 | 1.05 | 1 | 1 | 1.8 | 0.8 | 1.4 | F
- hereof equipment (%)
- hereof installation (%)
Fixed O&M (mill € /[t CO2 output/Hour]) | 0.036 | 0.036 | 0.0345 | 0.0315 | 0.03 | 0.03 | 0.054 | 0.024 | 0.042 | G
Variable O&M (€ per t CO2 output) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H
Startup cost (€ per startup/t CO2/hour) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | I
Technology specific data
Specific investment optional O₂ plant (ASU) (mill € /[t CO2 output/ hour]) | 0.3 | 0.3 | 0.28 | 0.26 | 0.24 | 0.25 | 0.35 | 0.22 | 0.3 | J
Electricity input for optional O₂ plant (ASU) (MW/ton CO₂/h) | 0.086 | 0.086 | 0.08 | 0.075 | 0.7 | 0.08 | 0.09 | 0.6 | 0.08
Electricity input CO₂ post treatment (CPU) (MWh/t CO2-output) | 0.18 | 0.18 | 0.17 | 0.16 | 0.15 | 0.16 | 0.2 | 0.12 | 0.18
Heat output CO₂ post treatment (MWh/t CO₂ output) | 0.3 | 0.3 | 0.29 | 0.27 | 0.25 | 0.25 | 0.35 | 0.2 | 0.3
References
1 | ECRA CCS Project – Report on Phase III. European Cement Research Academy. Technical Report TR-ECRA-119/2012.
2
3
Notes
A | CC capacity is chosen to match a cement kiln with production of 3000 tonne clinker per day.
B | On wet basis, after flue gas condensation unit
C | Electricity for oxy-fuel retrofit plant is assumed unchanged when excluding ASU and CPU.
D | Some CO₂ is vented from CPU during purification. The capture rate provides the fraction of the CO₂ from the klin exhaust gases which is captured
E | The amount of flue gas condensate produced is depending on fuel composition (moisture) and is based on dry cement process. For wet process 1.1 t condensate/t CO₂ and 0.8 MWh/tonc CO₂ heat out can be used
F | Cost includes cement kiln modifications and CO₂ purification unit (CPU) and compression to 150 bar for pipeline transport, but excludes O₂ production plant (ASU). Cost assumed to decrease by 20% up to 2050 as market develops
G | Fixed O&M is estimated as 3% of CAPEX.
H | Cost for make-up chemicals to CPU and disposal of acid waste. Power at flue gas recirculations fans equals reduced power at other fans
I | Estimated value excluding ASU for O₂ generation.
J | An large O₂ source is required for an oxy-fuel plant. An ASU is therefore likely to be required. For cement kilns significantly less O₂ required pr. t CO₂ compared to energy plants

## 403.a Direct air capture
Technology | Direct Air Capture Plant
| 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant capacity (t CO2 output / hour) | 0.1 | 0.2 | 2 | 50 | 125 | 0.1 | 0.4 | 50 | 200 | A | 1
- Inputs at max capacity
A) Air flow rate (t/t CO2 output) | 3300 | 3300 | 2800 | 2400 | 2100 | 3000 | 3600 | 2000 | 3000 | B
C1) Heat input (MWh/t CO2-output) | 2.5 | 2.5 | 2 | 1.5 | 1.5 | 1.5 | 2.5 | 1.4 | 2 | C | 1,2,3,4
C2) Eletricity input (MWh/t CO2-output) | 0.35 | 0.35 | 0.32 | 0.3 | 0.28 | 0.2 | 0.5 | 0.25 | 0.35 | D | 1,2,3,4
Y) Auxiliary products inputs (kg/t CO2-output )
- Outputs at max capacity
A2) CO2 purity prior to post cleaning (% vol) | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 |  |  |  |  | E | 2.4
A3) Total pressure of CO2 gas (kPa(a)) | 20 | 20 | 20 | 20 | 20 | [5 empty] | 2
B1) Mass of H2O (t/t CO2-output) | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | F | 1
C1) Heat out (MWh/t CO2-output) | 1.25 | 1.25 | 1 | 0.75 | 0.75 | 0.75 | 1.25 | 0.7 | 1 | G
C2) Temperature of heat out (°C) | 50 | 50 | 50 | 50 | 50 | 20 | 70 | 20 | 70 | H
- other technical data
Forced outage (%) | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | I
Planned outage (weeks per year) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | I
Technical lifetime (years) | 20 | 20 | 20 | 20 | 20 |  |  |  |  | J | 4
Construction time (years) | 1 | 1 | 2 | 2.5 | 2.5 | 0.75 | 1.5 | 1.5 | 3 | K
Financial data
Specific investment (mill € /[t CO2 output/hour]) | 7 | 7 | 6 | 5 | 4 | 6 | 10 | 3 | 7 | L | 2
- hereof equipment (%)
- hereof installation (%)
Fixed O&M (mill € /[t CO2 output/hour]) | 0.3465 | 0.3465 | 0.297 | 0.2475 | 0.198 | 0.297 | 0.495 | 0.1485 | 0.3465 | M | 2
Variable O&M (€ per Mt CO2 output) | [9 empty] | N
Startup cost (€ per startup/t CO2/hour)
Technology specific data
Land use for DAC unit (km^2/(Mt CO₂ output/year) | 0.1 | 0.1 | 0.1 | 0.05 | 0.02 | 0.02 | 0.1 | 0.05 | 0.002 |  | 1
CO₂ compression and dehydration - Electricity input (MWh/t CO₂ output) | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  |  |  |  | O
CO₂ compression and dehydration - Heat out (MWh/t CO₂ output) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
References
1 | P. Viebahn, A. Scholz and O. Zelt. The potential Role of Direct Air capture in the German energy research program. Energies 2019, 12, 3443
2 | M. Fasihi, O. Efimova, C. Breyer. Techno-economic assessment of CO₂ direct air capture plants. J. of Cleaner Prod. 224 (2019) 957-980.
3 | Evans, S. The Swiss Company Hoping to Capture 1% of Global CO2 Emissions by 2025; CarbonBrief. 22 June 2017.
4 | A.B. Vogel. CO2 – the Raw Material that Comes from AIR. Swiss Federal Office of Energy. 8643 Gasbefeurte kraftwerke. 05.05.2017.
Notes
A | Largest facility in operation today is approx. 0.1 t/h by Climeworks consisting of 18 modules. The 2050 value is based on technology vendors expectations of +1 MTPA plant.
B | Air flow to DAC unit up to year 2025 assumes 50% capture rate of 400 ppmv CO₂ in air. It is expected that capture rate may increase to 80% in 2050.
C | Based on solid adsorption by Climeworks. Heat is required around 100 deg C to desorb CO₂. Inconsistency in reported heat requirement, 2.5 MWh/ton CO₂ is regarded as more realistic value. The 2050 value is Climeworks' target (undocumented)!
D | Electrical consumption between 0.2 and 0.5 MWh/t CO₂ reported. The average value (0.35 MWh/t CO₂) is selected with 20% improvement to 2050.
E | CO₂ purity is claimed to 99.9%, however this is undocumented. It is expected that this is on dry basis as the CO₂ will contain moisture as well.
F | Moisture from the air is co-adsorbed on the filter and desorbed during regeneration. 1 m³/t CO₂ is reported but this will presumably vary with air humidity.
G | Modules must be cooled to 15 deg C after regeneration. No data, hence it is assumed that 50% of heat input must be removed, rest is heat of desorption.
H | Filter module to be cooled from approx. 100 to 15 deg C, hence 50 deg C is taken as an average. Heat only available intermittently as it is a batch process. Details unkonwn.
I | Values assumed, no data available.
J | The life expectancy of one module is reported to be 4 years according to Vogel et al. [4]. Overall plant is assumed to have 20 years lifetime Fashi et al. [2].
K | Climeworks have currently capacity to produce 150 CO₂ collector modules per year, hence today's small scale plants can be produced in short time. The installation time is expected to increase with size of facility.
L | No CAPEX value reported by Climeworks, however based on CAPEX estimate for 360 ktpa plant from Antecy (which has become part of Climeworks). 0.5 mill €/(t CO₂) added for CO₂ compression to 150 bar CAPEX assumed to decrease by 40% in 2050.
M | Total O&M is taken as 3.7% of CAPEX as in Fashi et al. [2]. CO₂ filter is reported to need replacement every 4 years [4]. The filter is assumed to make up 5% of CAPEX, hence additonal 1.25% of CAPEX is added to fixed O&M
N | O&M is not split in fixed and variable. It is expected that O&M is mainly fixed for the solid adsorption technology.
O | Compression of CO₂ from 0,2 to 150 bara inkl. dehydration to 50 ppmv