## Index
INDEX | Technology Data for Heating Installations
201 Oil boiler, ex single | All cost data is in | 2020 | EURO
201 Oil boiler, ex apart
201 Oil boiler, new single
201 Oil boiler, new apart
202 Gas boiler, ex single
202 Gas boiler, ex apart | License:
202 Gas boiler, new single | This work is licensed under Attribution 4.0 International
202 Gas boiler, new apart
203 DH indirect,new single
203 DH indirect,ex single | Date | Sheet | Change | Notes
203 DH indirect,ex apart | 2021-01-20 | all | major update of all datasheets | Note that guideline is updated in 2020 as well
203 DH indirect,new apart | 2021-01-20 | alldata_flat | added a sheet with all data on flat format
203 DH direct,new single | 2021-06-24 | 208 | added new sheets for hybrid headpumps
203 DH direct,ex single | 2021-06-24 | 207 HP air-water,ex single | capacity adjusted | To represent capacity at specified temperature set (-7/55 degrees)
203 DH direct,ex apart | 2021-06-24 | alldata_flat | added columns to flat data table
203 DH direct,new apart | 2023-08-31 | all | Update to 2020 prices
204 Biomass auto,ex single
204 Biomass auto,new single
204 Biomass auto,ex apart
204 Biomass auto,new apart
205 Biomass manual,ex single
206 Wood stove,single, ex tank
206 Wood stove, single n w tank
207 HP air-water,ex single
207 HP air-water,ex apart
207 HP air-water LPP,ex single
207 HP air-water,new single
207 HP air-water,new apart
207 HP ground-water,ex single
207 HP ground-water,ex apart
207 HP ground-water,new single
207 HP ground-water,new apart
207 HP air-air,ex single
207 HP air-air,new single
207 HP ventilation,new single
207 HP ventilation,new apart
208 HP hybrid,ex apart
208 HP hybrid,ex single
208 HP hybrid,new single
208 HP hybrid,new apart
215 Solar heating,ex single
215 Solar heating,ex apart
215 Solar heating,new single
215 Solar heating,new apart
216 Electric heating,new single
216 Electric heating,new apart
This file contains the technology data sheets related to heating installatoins. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. Dates and descriptions of updates are listed in the ammendment sheet below.

## alldata_flat
ws | Technology | cat | par | unit | priceyear | note | ref | est | year | val
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2020 | 140
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2025 | 130
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2030 | 120
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2040 | 115
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2050 | 110
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2025 | 100
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2050 | 90
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2025 | 160
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2050 | 150
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | ctrl | 2020 | 0.92
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | ctrl | 2025 | 0.92
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | ctrl | 2030 | 0.93
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | ctrl | 2040 | 0.94
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | ctrl | 2050 | 0.95
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | lower | 2025 | 0.92
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | lower | 2050 | 0.92
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | upper | 2025 | 0.95
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N | 1,2,3,4,14 | upper | 2050 | 0.98
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 13
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 13
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 30
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 30
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | D |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | ctrl | 2020 | 52
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | ctrl | 2025 | 52
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | ctrl | 2030 | 52
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | ctrl | 2040 | 52
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | ctrl | 2050 | 52
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | upper | 2025 | 100
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E | 5 | upper | 2050 | 100
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 5
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 5
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 5
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 5
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 5
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 10
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 10
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2020 | 6.7
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2025 | 6.7
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2030 | 6.7
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2040 | 6.7
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2050 | 6.7
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | upper | 2025 | 10
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | upper | 2050 | 10
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 184.5808
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 181.3466
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 178.7321
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 169.6216
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 160.4311
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 154.2782
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 136.2891
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 217.5651
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 192.9151
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2020 | 9.66
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2025 | 11.05
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2030 | 12.12
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2040 | 12.535
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2050 | 12.87
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | lower | 2025 | 8.5
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | lower | 2050 | 10.53
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | upper | 2025 | 13.6
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | upper | 2050 | 17.55
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 174.9208
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 170.2966
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 166.6121
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 157.0866
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 147.5611
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 145.7782
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 125.7591
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 203.9651
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 175.3651
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2020 | 5.6
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2025 | 5.4936
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2030 | 5.3898
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2040 | 5.1898
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2050 | 4.9997
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | lower | 2025 | 4.6695
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | lower | 2050 | 4.2497
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | upper | 2025 | 6.8137
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | upper | 2050 | 6.2496
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2020 | 4.3
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2025 | 4.1936
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2030 | 4.0898
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2040 | 3.8898
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2050 | 3.6997
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | lower | 2025 | 3.5645
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | lower | 2050 | 3.1447
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | upper | 2025 | 5.2013
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | upper | 2050 | 4.6246
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2020 | 1.3
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2025 | 1.3
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2030 | 1.3
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2040 | 1.3
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2050 | 1.3
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | lower | 2025 | 1.105
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | lower | 2050 | 1.105
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | upper | 2025 | 1.6124
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | upper | 2050 | 1.625
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, ex single | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2020 | 1400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2025 | 1350
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2030 | 1300
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2040 | 1250
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2050 | 1200
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2025 | 1000
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2050 | 500
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2025 | 1800
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2050 | 1500
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2020 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2025 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2030 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2040 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2050 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2025 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2050 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2025 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2050 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2020 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2025 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2030 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2040 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2050 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2025 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2050 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2025 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2050 | 1
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2020 | 0.92
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2025 | 0.92
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2030 | 0.93
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2040 | 0.94
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2050 | 0.95
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | lower | 2025 | 0.92
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | lower | 2050 | 0.92
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | upper | 2025 | 0.95
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | upper | 2050 | 0.98
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2020 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2025 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2030 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2040 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2050 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | lower | 2025 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | lower | 2050 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | upper | 2025 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | upper | 2050 | 400
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | ctrl | 2020 | 52
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | ctrl | 2025 | 52
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | ctrl | 2030 | 52
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | ctrl | 2040 | 52
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | ctrl | 2050 | 52
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | upper | 2025 | 100
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | C,E |  | upper | 2050 | 100
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 10
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 10
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2020 | 6.7
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2025 | 6.7
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2030 | 6.7
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2040 | 6.7
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | ctrl | 2050 | 6.7
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | upper | 2025 | 10
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B,E |  | upper | 2050 | 10
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 1038.8081
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 1042.8305
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 1057.9309
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 1067.6258
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 1076.5208
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 888.2819
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 903.5503
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 1249.1074
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 1293.151
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 96.6
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 114.75
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 131.3
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 136.25
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 140.4
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 85
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 58.5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 153
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 175.5
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 942.2081
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 928.0805
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 926.6309
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 931.3758
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 936.1208
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 803.2819
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 845.0503
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 1096.1074
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 1117.651
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2020 | 32.6025
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2025 | 31.7955
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2030 | 31.0086
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2040 | 29.4926
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | ctrl | 2050 | 28.0507
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | lower | 2025 | 27.0262
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | lower | 2050 | 23.8431
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | upper | 2025 | 38.1547
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J |  | upper | 2050 | 33.6608
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 26.082
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 25.4364
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 24.8069
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 23.5941
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 22.4405
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 21.621
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 19.0745
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 30.5237
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 26.9286
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 6.5205
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 6.3591
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 6.2017
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 5.8985
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 5.6101
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 5.4052
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 4.7686
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 7.6309
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 6.7322
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, ex apart | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2020 | 100
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2025 | 95
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2030 | 90
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2040 | 82
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2050 | 75
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2025 | 75
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2050 | 60
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2025 | 125
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2050 | 100
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2020 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2030 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2040 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2020 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2030 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2040 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | ctrl | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | lower | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | I |  | upper | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2020 | 0.88
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2025 | 0.9
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2030 | 0.92
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2040 | 0.93
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | ctrl | 2050 | 0.94
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | lower | 2025 | 0.85
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | lower | 2050 | 0.9
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | upper | 2025 | 0.95
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, N | 1, 2, 3, 4, 14 | upper | 2050 | 0.98
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2020 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2025 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2030 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2040 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | ctrl | 2050 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | lower | 2025 | 15
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | lower | 2050 | 15
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | upper | 2025 | 25
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I |  | upper | 2050 | 25
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 52
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 52
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 52
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 52
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 52
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 100
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 100
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 5
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 5
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 5
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 5
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 5
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 10
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 10
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 0.3
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 0.3
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 0.3
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 0.3
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 0.3
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 185.5577
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 181.7918
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 178.5491
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 169.1563
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 159.6576
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 154.5961
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 135.626
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 218.0102
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 191.8101
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 6.9
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 8.075
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 9.09
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 8.938
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 8.775
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 6.375
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 7.02
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 10.625
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 11.7
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 178.6577
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 173.7168
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 169.4591
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 160.2183
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 150.8826
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 148.2211
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 128.606
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 207.3852
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 180.1101
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | ctrl | 2020 | 7
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | ctrl | 2025 | 6.8267
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | ctrl | 2030 | 6.6578
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | ctrl | 2040 | 6.3323
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | ctrl | 2050 | 6.0227
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | lower | 2025 | 5.8027
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | lower | 2050 | 5.1193
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | upper | 2025 | 8.1921
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, J, |  | upper | 2050 | 7.2272
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 4.9
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 4.7787
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 4.6604
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 4.4326
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 4.2159
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 4.0619
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 3.5835
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 5.7345
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 5.0591
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 2.1
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 2.048
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.9973
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.8997
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.8068
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.7408
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.5358
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 2.4576
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2.1682
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, new single | Oil boiler (bio oil) - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2020 | 900
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2025 | 750
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2030 | 520
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2040 | 500
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | ctrl | 2050 | 480
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2025 | 400
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | lower | 2050 | 200
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2025 | 900
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | M | 11 | upper | 2050 | 600
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | ctrl | 2020 | 0.88
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | ctrl | 2025 | 0.9
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | ctrl | 2030 | 0.92
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | ctrl | 2040 | 0.93
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | ctrl | 2050 | 0.94
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | lower | 2025 | 0.85
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | lower | 2050 | 0.9
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | upper | 2025 | 0.95
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, G | 1,2,3,4,14 | upper | 2050 | 0.98
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2020 | 160
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2025 | 160
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2030 | 160
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2040 | 160
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2050 | 160
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2025 | 100
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2050 | 100
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2025 | 1000
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2050 | 1000
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 52
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 52
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 52
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 52
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 52
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 100
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 100
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 10
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 10
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2020 | 0.3
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2025 | 0.3
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2030 | 0.3
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2040 | 0.3
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | ctrl | 2050 | 0.3
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2025 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | E |  | upper | 2050 | 1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2020 | 751.0195
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2025 | 740.4614
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2030 | 733.1723
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2040 | 737.0503
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | ctrl | 2050 | 740.6083
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | lower | 2025 | 632.4128
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | lower | 2050 | 624.9201
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | upper | 2025 | 906.143
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | M |  | upper | 2050 | 889.2604
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 62.1
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 63.75
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 52.52
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 54.5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 56.16
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 34
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 23.4
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 76.5
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 70.2
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 688.9195
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 676.7114
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 680.6523
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 682.5503
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 684.4483
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 598.4128
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 601.5201
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 829.643
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 819.0604
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | ctrl | 2020 | 26.082
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | ctrl | 2025 | 25.4364
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | ctrl | 2030 | 24.8069
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | ctrl | 2040 | 23.5941
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | ctrl | 2050 | 22.4405
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | lower | 2025 | 21.621
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | lower | 2050 | 19.0745
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | upper | 2025 | 30.5237
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F, H, K, J, O |  | upper | 2050 | 26.9286
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 18.2574
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 17.8055
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 17.3648
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 16.5158
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 15.7084
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 15.1347
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 13.3521
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 21.3666
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 18.8501
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 7.8246
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 7.6309
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 7.4421
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 7.0782
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 6.7322
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 6.4863
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 5.7223
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 9.1571
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 8.0786
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
201 Oil boiler, new apart | Oil boiler (bio oil) - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2020 | 140
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2025 | 130
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2030 | 120
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2040 | 110
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2050 | 100
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | lower | 2025 | 100
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | lower | 2050 | 90
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | upper | 2025 | 160
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | upper | 2050 | 150
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | ctrl | 2020 | 0.97
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | ctrl | 2025 | 0.97
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | ctrl | 2030 | 0.98
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | ctrl | 2040 | 0.99
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | ctrl | 2050 | 0.99
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | lower | 2025 | 0.95
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | lower | 2050 | 0.98
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | upper | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B, M | 1,4, 28 | upper | 2050 | 1.02
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2020 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2025 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2030 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2040 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2050 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | lower | 2025 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | lower | 2050 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | upper | 2025 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | upper | 2050 | 14
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2020 | 20
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2025 | 20
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2030 | 20
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2040 | 20
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2050 | 20
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | lower | 2025 | 18
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | lower | 2050 | 18
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | upper | 2025 | 22
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | upper | 2050 | 22
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2040 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2040 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2020 | 20.4
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2025 | 20.4
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2030 | 20.4
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2040 | 20.4
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2050 | 20.4
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | lower | 2025 | 15
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | lower | 2050 | 15
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | upper | 2025 | 25
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | upper | 2050 | 25
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | ctrl | 2020 | 0.1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | ctrl | 2025 | 0.1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | ctrl | 2030 | 0.1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | ctrl | 2040 | 0.1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | ctrl | 2050 | 0.1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | lower | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | lower | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | upper | 2025 | 0.5
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3.7 | upper | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | ctrl | 2020 | 0.43
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | ctrl | 2025 | 0.43
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | ctrl | 2030 | 0.43
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | ctrl | 2040 | 0.43
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | ctrl | 2050 | 0.43
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | lower | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | lower | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | upper | 2025 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, | 5 | upper | 2050 | 1
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2020 | 191.5808
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2025 | 188.3466
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2030 | 186.7321
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2040 | 176.5511
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2050 | 170.2101
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | lower | 2025 | 160.2282
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | lower | 2050 | 144.7891
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | upper | 2025 | 225.9651
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | upper | 2050 | 204.9151
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | ctrl | 2020 | 9.66
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | ctrl | 2025 | 11.05
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | ctrl | 2030 | 12.12
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | ctrl | 2040 | 11.99
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | ctrl | 2050 | 11.7
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | lower | 2025 | 8.5
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | lower | 2050 | 10.53
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | upper | 2025 | 13.6
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | T |  | upper | 2050 | 17.55
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 181.9208
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 177.2966
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 174.6121
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 164.5611
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 158.5101
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 151.7282
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 134.2591
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 212.3651
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 187.3651
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2020 | 3.9
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2025 | 3.8035
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2030 | 3.7093
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2040 | 3.528
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2050 | 3.3555
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | lower | 2025 | 3.2329
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | lower | 2050 | 2.8522
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | upper | 2025 | 4.5642
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | upper | 2050 | 4.0266
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 2
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 2.73
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 2.6624
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 2.5965
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 2.4696
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 2.3488
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 2.2631
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.9965
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 3.1949
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2.8186
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.17
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.141
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.1128
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.0584
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.0066
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.96988
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.85565
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.3692
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.208
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
202 Gas boiler, ex single | Natural gas boiler - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | ctrl | 2020 | 700
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | ctrl | 2025 | 650
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | ctrl | 2030 | 600
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | ctrl | 2040 | 550
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | ctrl | 2050 | 500
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | lower | 2025 | 500
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | lower | 2050 | 250
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | upper | 2025 | 1000
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M | 30 | upper | 2050 | 750
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | ctrl | 2020 | 1.01
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | ctrl | 2025 | 1.01
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | ctrl | 2030 | 1.02
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | ctrl | 2040 | 1.02
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | ctrl | 2050 | 1.02
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | lower | 2025 | 0.99
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | lower | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | upper | 2025 | 1.03
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31 | upper | 2050 | 1.04
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2020 | 400
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2025 | 400
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2030 | 400
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2040 | 400
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2050 | 400
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2025 | 300
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2050 | 300
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2025 | 500
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2050 | 500
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2020 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2025 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2030 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2040 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2050 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | lower | 2025 | 20
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | lower | 2050 | 20
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | upper | 2025 | 30
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | upper | 2050 | 30
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2020 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2030 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2040 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | lower | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | lower | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | upper | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N, G |  | upper | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2020 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2030 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2040 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | lower | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | lower | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | upper | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N, G |  | upper | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | ctrl | 2020 | 20.4
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | ctrl | 2025 | 20.4
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | ctrl | 2030 | 20.4
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | ctrl | 2040 | 20.4
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | ctrl | 2050 | 20.4
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | lower | 2025 | 15
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | lower | 2050 | 15
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | upper | 2025 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N,G,D |  | upper | 2050 | 25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | ctrl | 2020 | 0.1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | ctrl | 2025 | 0.1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | ctrl | 2030 | 0.1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | ctrl | 2040 | 0.1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | ctrl | 2050 | 0.1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | lower | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | lower | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | upper | 2025 | 0.5
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N, G | 3.7 | upper | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2020 | 0.43
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2025 | 0.43
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2030 | 0.43
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2040 | 0.43
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | ctrl | 2050 | 0.43
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | lower | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | lower | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | upper | 2025 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N, G |  | upper | 2050 | 1
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2020 | 665.904
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2025 | 660.7332
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2030 | 654.6604
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2040 | 627.7554
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2050 | 179.0503
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | lower | 2025 | 562.2909
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | lower | 2050 | 148.3252
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | upper | 2025 | 790.0819
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | upper | 2050 | 218.1755
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 48.3
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 55.25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 60.6
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 59.95
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 58.5
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 42.5
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 29.25
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 85
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 87.75
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 617.604
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 605.4832
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 594.0604
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 567.8054
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 120.5503
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 519.7909
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 119.0752
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 705.0819
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 130.4255
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | ctrl | 2020 | 27.4738
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | ctrl | 2025 | 26.8928
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | ctrl | 2030 | 26.3262
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | ctrl | 2040 | 25.2346
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | ctrl | 2050 | 24.1965
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | lower | 2025 | 19.5942
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | lower | 2050 | 17.8753
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | upper | 2025 | 38.3392
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C |  | upper | 2050 | 34.2947
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2020 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2025 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2030 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2040 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2050 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | lower | 2025 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | lower | 2050 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | upper | 2025 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | upper | 2050 | 2
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 21.979
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 21.5142
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 21.0609
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 20.1877
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 19.3572
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 15.6753
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 14.3002
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 30.6714
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 27.4358
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 5.4948
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 5.3786
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 5.2652
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 5.0469
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 4.8393
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 3.9188
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 3.5751
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 7.6678
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 6.8589
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
202 Gas boiler, ex apart | Natural gas boiler - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2020 | 140
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2025 | 130
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2030 | 120
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2040 | 110
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | ctrl | 2050 | 100
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | lower | 2025 | 100
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | lower | 2050 | 90
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | upper | 2025 | 160
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T | 28 | upper | 2050 | 150
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | ctrl | 2020 | 0.97
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | ctrl | 2025 | 0.97
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | ctrl | 2030 | 0.98
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | ctrl | 2040 | 0.99
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | ctrl | 2050 | 0.99
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | lower | 2025 | 0.95
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | lower | 2050 | 0.98
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | upper | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A, B | 1.28 | upper | 2050 | 1.02
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2020 | 14
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2025 | 14
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2030 | 14
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2040 | 14
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | ctrl | 2050 | 14
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | lower | 2025 | 10
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | lower | 2050 | 10
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | upper | 2025 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U |  | upper | 2050 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2020 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2025 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2030 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2040 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | ctrl | 2050 | 20
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | lower | 2025 | 18
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | lower | 2050 | 18
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | upper | 2025 | 22
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2, 29 | upper | 2050 | 22
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2040 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2040 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2020 | 20.4
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2025 | 20.4
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2030 | 20.4
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2040 | 20.4
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | ctrl | 2050 | 20.4
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | lower | 2025 | 15
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | lower | 2050 | 15
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | upper | 2025 | 25
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F, G | 5 | upper | 2050 | 25
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | ctrl | 2020 | 0.1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | ctrl | 2025 | 0.1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | ctrl | 2030 | 0.1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | ctrl | 2040 | 0.1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | ctrl | 2050 | 0.1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | lower | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | lower | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | upper | 2025 | 0.5
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | D, E, G | 3 | upper | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | ctrl | 2020 | 0.43
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | ctrl | 2025 | 0.43
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | ctrl | 2030 | 0.43
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | ctrl | 2040 | 0.43
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | ctrl | 2050 | 0.43
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | lower | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | lower | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | upper | 2025 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G, |  | upper | 2050 | 1
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2020 | 191.5808
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2025 | 188.3466
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2030 | 186.7321
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2040 | 176.5511
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | ctrl | 2050 | 170.2101
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | lower | 2025 | 160.2282
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | lower | 2050 | 144.7891
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | upper | 2025 | 225.9651
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J | 33 | upper | 2050 | 204.9151
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 9.66
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 11.05
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 12.12
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 11.99
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 11.7
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 8.5
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 10.53
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 13.6
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 17.55
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 181.9208
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 177.2966
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 174.6121
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 164.5611
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 158.5101
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 151.7282
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 134.2591
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 212.3651
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 187.3651
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2020 | 3.9
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2025 | 3.8035
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2030 | 3.7093
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2040 | 3.528
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | ctrl | 2050 | 3.3555
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | lower | 2025 | 2.3092
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | lower | 2050 | 2.0373
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | upper | 2025 | 6.5202
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | V, C |  | upper | 2050 | 5.7523
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2020 | 2
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2025 | 2
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2030 | 2
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2040 | 2
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | ctrl | 2050 | 2
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | lower | 2025 | 1.4286
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | lower | 2050 | 1.4286
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | upper | 2025 | 2.8571
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 6 | upper | 2050 | 2.8571
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 2.73
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 2.6624
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 2.5965
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 2.4696
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 2.3488
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.6165
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.4261
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 4.5642
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2.8186
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.17
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.141
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.1128
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.0584
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.0066
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.69277
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.61118
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.9561
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.208
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
202 Gas boiler, new single | Natural gas boiler - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | ctrl | 2020 | 700
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | ctrl | 2025 | 650
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | ctrl | 2030 | 600
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | ctrl | 2040 | 550
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | ctrl | 2050 | 500
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | lower | 2025 | 500
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | lower | 2050 | 250
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | upper | 2025 | 1000
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | T,M |  | upper | 2050 | 750
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | ctrl | 2020 | 1.01
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | ctrl | 2025 | 1.01
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | ctrl | 2030 | 1.02
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | ctrl | 2040 | 1.02
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | ctrl | 2050 | 1.02
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | lower | 2025 | 0.99
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | lower | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | upper | 2025 | 1.03
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A,B,L,O,P,M | 30, 31, 1 | upper | 2050 | 1.04
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2020 | 160
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2025 | 160
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2030 | 160
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2040 | 160
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2050 | 160
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2025 | 100
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2050 | 100
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2025 | 200
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2050 | 200
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2020 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2025 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2030 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2040 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | ctrl | 2050 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | lower | 2025 | 20
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | lower | 2050 | 20
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | upper | 2025 | 30
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | M | 31 | upper | 2050 | 30
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2020 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2030 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2040 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | lower | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | lower | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | upper | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | N |  | upper | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2020 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2030 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2040 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | lower | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | lower | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | upper | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | N |  | upper | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | ctrl | 2020 | 20.4
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | ctrl | 2025 | 20.4
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | ctrl | 2030 | 20.4
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | ctrl | 2040 | 20.4
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | ctrl | 2050 | 20.4
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | lower | 2025 | 15
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | lower | 2050 | 15
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | upper | 2025 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | F,N |  | upper | 2050 | 25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2020 | 0.1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2025 | 0.1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2030 | 0.1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2040 | 0.1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2050 | 0.1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | lower | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | lower | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | upper | 2025 | 0.5
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | N |  | upper | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2020 | 0.43
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2025 | 0.43
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2030 | 0.43
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2040 | 0.43
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | ctrl | 2050 | 0.43
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | lower | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | lower | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | upper | 2025 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | N |  | upper | 2050 | 1
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2020 | 665.904
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2025 | 660.7332
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2030 | 654.6604
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2040 | 627.7554
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | ctrl | 2050 | 179.0503
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | lower | 2025 | 562.2909
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | lower | 2050 | 148.3252
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | upper | 2025 | 790.0819
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, O, P, S |  | upper | 2050 | 218.1755
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 48.3
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 55.25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 60.6
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 59.95
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 58.5
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 42.5
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 29.25
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 85
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 87.75
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 617.604
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 605.4832
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 594.0604
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 567.8054
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 120.5503
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 519.7909
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 119.0752
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 705.0819
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 130.4255
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | ctrl | 2020 | 22.68
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | ctrl | 2025 | 22.1186
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | ctrl | 2030 | 21.5712
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | ctrl | 2040 | 20.5166
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | ctrl | 2050 | 19.5135
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | lower | 2025 | 18.8008
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | lower | 2050 | 16.5865
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | upper | 2025 | 26.5424
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | C, O, P |  | upper | 2050 | 23.4162
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | ctrl | 2020 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | ctrl | 2025 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | ctrl | 2030 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | ctrl | 2040 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | ctrl | 2050 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | lower | 2025 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | lower | 2050 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | upper | 2025 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 33 | upper | 2050 | 2
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 15.876
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 15.483
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 15.0998
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 14.3616
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 13.6595
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 13.1606
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 11.6105
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 18.5797
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 16.3914
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 6.804
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 6.6356
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 6.4714
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 6.155
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 5.8541
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 5.6403
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 4.9759
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 7.9627
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 7.0249
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
202 Gas boiler, new apart | Natural gas boiler - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 60
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 55
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 50
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 40
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 35
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 40
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 80
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 75
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2020 | 0.96
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2025 | 0.96
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2030 | 0.97
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2040 | 0.97
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2050 | 0.98
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | lower | 2025 | 0.95
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | lower | 2050 | 0.95
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | upper | 2025 | 0.99
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | upper | 2050 | 0.99
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2020 | 12
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2025 | 12
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2030 | 12
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2040 | 12
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2050 | 12
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | lower | 2025 | 5
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | lower | 2050 | 5
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | upper | 2025 | 15
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | upper | 2050 | 15
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2020 | 53.14
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2025 | 52.175
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2030 | 51.05
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2040 | 48.36
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2050 | 46.095
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | lower | 2025 | 40.4
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | lower | 2050 | 32.925
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | upper | 2025 | 69.8
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | upper | 2050 | 68.775
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 4.14
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 4.675
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 5.05
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 4.36
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 4.095
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 3.4
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 2.925
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 6.8
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 8.775
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 49
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 47.5
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 46
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 44
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 42
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 37
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 30
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 63
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 60
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2020 | 2.41
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2025 | 2.34
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2030 | 2.28
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2040 | 2.15
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2050 | 2.03
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2025 | 2.0485
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2050 | 1.7255
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2025 | 3.5
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2050 | 3.25
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2020 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2025 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2030 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2040 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2050 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2025 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2050 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2025 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2050 | 3
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.687
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.638
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.596
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.505
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.421
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.434
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.2079
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 2.45
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2.275
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0.723
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0.702
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.684
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.645
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.609
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.61455
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.51765
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.05
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0.975
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH indirect,new single | Indirect district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 120
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 110
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 100
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 80
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 75
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 50
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 50
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 125
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 100
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2020 | 0.96
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2025 | 0.96
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2030 | 0.97
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2040 | 0.97
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2050 | 0.98
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | lower | 2025 | 0.95
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | lower | 2050 | 0.95
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | upper | 2025 | 0.99
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | upper | 2050 | 0.99
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2020 | 12
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2025 | 12
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2030 | 12
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2040 | 12
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2050 | 12
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | lower | 2025 | 5
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | lower | 2050 | 5
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | upper | 2025 | 30
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | upper | 2050 | 30
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 46.0693
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 45.601
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 46.6101
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 45.1281
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 43.6576
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 39.3141
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 36.805
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 54.8102
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 52.6101
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 8.28
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 9.35
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 10.1
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 8.72
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 8.775
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 4.25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 5.85
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 10.625
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 11.7
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | ctrl | 2020 | 37.7893
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | ctrl | 2025 | 36.251
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | ctrl | 2030 | 36.5101
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | ctrl | 2040 | 36.4081
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | ctrl | 2050 | 34.8826
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | lower | 2025 | 35.0641
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | lower | 2050 | 30.955
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | upper | 2025 | 44.1852
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, F |  | upper | 2050 | 40.9101
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2020 | 2.41
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2025 | 2.34
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2030 | 2.28
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2040 | 2.15
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2050 | 2.03
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2025 | 2.0485
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2050 | 1.7255
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2025 | 3.5
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2050 | 3.25
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2020 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2025 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2030 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2040 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2050 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2025 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2050 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2025 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2050 | 3
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.2773
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.2402
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.2084
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.1395
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.0759
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.0857
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.91451
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.855
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.7225
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.1327
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0998
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.0716
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.0105
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.9541
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.9628
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.81098
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.645
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.5275
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH indirect,ex single | Indirect district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 600
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 550
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 500
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 450
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 250
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 1000
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 800
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2020 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2030 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2040 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | lower | 2025 | 0.98
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | lower | 2050 | 0.98
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | upper | 2025 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | upper | 2050 | 1
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | ctrl | 2020 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | ctrl | 2025 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | ctrl | 2030 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | ctrl | 2040 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | ctrl | 2050 | 400
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | lower | 2025 | 150
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | lower | 2050 | 150
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | upper | 2025 | 500
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, H |  | upper | 2050 | 500
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | ctrl | 2020 | 140.4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | ctrl | 2025 | 143.25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | ctrl | 2030 | 144.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | ctrl | 2040 | 138.55
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | ctrl | 2050 | 131.8
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | lower | 2025 | 110.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | lower | 2050 | 94.25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | upper | 2025 | 201.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D |  | upper | 2050 | 198.6
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 41.4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 46.75
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 50.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 49.05
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 46.8
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 34
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 29.25
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 85
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 93.6
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 99
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 96.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 94
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 89.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 85
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 76.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 65
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 116.5
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 105
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2020 | 16.56
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2025 | 16.1501
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2030 | 15.7504
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2040 | 14.9803
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2050 | 14.248
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | lower | 2025 | 13.7276
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | lower | 2050 | 12.1108
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | upper | 2025 | 19.3801
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | upper | 2050 | 17.0976
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2020 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2025 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2030 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2040 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2050 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2025 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2050 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2025 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2050 | 4
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 11.592
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 11.3051
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 11.0253
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 10.4862
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 9.9736
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 9.6093
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 8.4775
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 13.5661
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 11.9683
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 4.968
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 4.845
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 4.7251
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 4.4941
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 4.2744
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 4.1183
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 3.6332
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 5.814
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 5.1293
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH indirect,ex apart | Indirect district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 350
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 325
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 300
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 250
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 250
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 250
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 200
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 500
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 400
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2020 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2030 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2040 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | ctrl | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | lower | 2025 | 0.98
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | lower | 2050 | 0.98
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | upper | 2025 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I |  | upper | 2050 | 1
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 160
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 160
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 160
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 160
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 160
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 150
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 150
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 500
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 500
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | ctrl | 2020 | 107.15
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | ctrl | 2025 | 109.125
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | ctrl | 2030 | 109.3
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | ctrl | 2040 | 102.25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | ctrl | 2050 | 100.25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | lower | 2025 | 89.25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | lower | 2050 | 79.4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | upper | 2025 | 140.5
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 8 | upper | 2050 | 132.8
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 24.15
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 27.625
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 30.3
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 27.25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 29.25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 21.25
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 23.4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 42.5
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 46.8
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 83
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 81.5
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 79
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 75
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 71
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 68
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 56
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 98
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 86
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2020 | 11.592
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2025 | 11.3051
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2030 | 11.0253
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2040 | 10.4862
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | ctrl | 2050 | 9.9736
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | lower | 2025 | 9.6093
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | lower | 2050 | 8.4775
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | upper | 2025 | 13.5661
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 2, 4, 7, 10 | upper | 2050 | 11.9683
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2020 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2025 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2030 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2040 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2050 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2025 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2050 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2025 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2050 | 4
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 8.1144
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 7.9136
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 7.7177
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 7.3404
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 6.9815
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 6.7265
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 5.9343
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 9.4963
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 8.3778
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | ctrl | 2020 | 3.4776
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | ctrl | 2025 | 3.3915
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | ctrl | 2030 | 3.3076
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | ctrl | 2040 | 3.1459
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | ctrl | 2050 | 2.9921
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | lower | 2025 | 2.8828
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | lower | 2050 | 2.5433
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | upper | 2025 | 4.0698
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | C,E |  | upper | 2050 | 3.5905
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH indirect,new apart | Indirect district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 40
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 40
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 35
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 32
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 30
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 30
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 22.5
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 50
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 37.5
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2020 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2030 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2040 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | ctrl | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | lower | 2025 | 0.98
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | lower | 2050 | 0.99
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | upper | 2025 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, I | 9 | upper | 2050 | 1
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2020 | 12
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2025 | 12
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2030 | 12
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2040 | 12
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | ctrl | 2050 | 12
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | lower | 2025 | 5
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | lower | 2050 | 5
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | upper | 2025 | 15
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H |  | upper | 2050 | 15
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH direct,new single | Direct district heating substation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 48.76
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 48.4
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 47.535
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 45.488
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 42.51
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 37.55
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 26.6325
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 64.25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 58.3875
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2020 | 2.76
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2025 | 3.4
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2030 | 3.535
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2040 | 3.488
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2050 | 3.51
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2025 | 2.55
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2050 | 2.6325
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2025 | 4.25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2050 | 4.3875
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2020 | 46
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2025 | 45
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2030 | 44
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2040 | 42
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2050 | 39
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2025 | 35
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2050 | 24
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2025 | 60
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2050 | 54
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2020 | 2.17
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2025 | 2.11
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2030 | 2.06
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2040 | 1.97
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2050 | 1.87
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2025 | 1.8445
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2050 | 1.5895
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2025 | 3.5
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2050 | 3.25
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2020 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2025 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2030 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2040 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2050 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2025 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2050 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2025 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2050 | 3
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.0416
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0128
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.9888
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.9456
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.8976
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.88536
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.76296
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.68
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.56
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.1284
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0972
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.0712
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.0244
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.9724
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.95914
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.82654
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.82
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.69
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH direct,new single | Direct district heating substation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 40
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 40
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 35
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 32
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 30
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 30
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 22.5
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 50
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 37.5
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2020 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2030 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2040 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | lower | 2025 | 0.98
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | lower | 2050 | 0.99
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | upper | 2025 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | upper | 2050 | 1
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | ctrl | 2020 | 12
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | ctrl | 2025 | 12
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | ctrl | 2030 | 12
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | ctrl | 2040 | 12
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | ctrl | 2050 | 12
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | lower | 2025 | 5
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | lower | 2050 | 5
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | upper | 2025 | 15
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | H, J |  | upper | 2050 | 15
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2020 | 48.76
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2025 | 48.4
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2030 | 47.535
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2040 | 45.488
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | ctrl | 2050 | 42.51
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | lower | 2025 | 37.55
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | lower | 2050 | 26.6325
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | upper | 2025 | 64.25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D, F | 8 | upper | 2050 | 58.3875
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 2.76
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 3.4
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 3.535
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 3.488
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 3.51
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 2.55
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 2.6325
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 4.25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 4.3875
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 46
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 45
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 44
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 42
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 39
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 35
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 24
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 60
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 54
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | ctrl | 2020 | 2.17
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | ctrl | 2025 | 2.11
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | ctrl | 2030 | 2.06
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | ctrl | 2040 | 1.97
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | ctrl | 2050 | 1.87
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | lower | 2025 | 1.8445
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | lower | 2050 | 1.5895
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | upper | 2025 | 3.5
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 10 | upper | 2050 | 3.25
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2020 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2025 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2030 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2040 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2050 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2025 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2050 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2025 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2050 | 3
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.0416
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0128
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.9888
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.9456
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.8976
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.88536
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.76296
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.68
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.56
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.1284
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0972
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.0712
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.0244
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.9724
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.95914
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.82654
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.82
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.69
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH direct,ex single | Direct district heating substation - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 200
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 200
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 175
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 165
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 150
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 150
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 125
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 300
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 250
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2020 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2030 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2040 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | lower | 2025 | 0.98
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | lower | 2050 | 0.99
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | upper | 2025 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | upper | 2050 | 1
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 400
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 400
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 400
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 400
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 400
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 150
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 150
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 500
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 500
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | ctrl | 2020 | 88.8
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | ctrl | 2025 | 90
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | ctrl | 2030 | 88.675
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | ctrl | 2040 | 85.985
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | ctrl | 2050 | 82.55
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | lower | 2025 | 75.75
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | lower | 2050 | 74.625
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | upper | 2025 | 113.5
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 8 | upper | 2050 | 109.25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 13.8
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 17
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 17.675
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 17.985
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 17.55
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 12.75
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 14.625
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 25.5
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 29.25
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 75
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 73
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 71
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 68
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 65
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 63
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 60
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 88
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 80
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | ctrl | 2020 | 12.3165
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | ctrl | 2025 | 12.0117
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | ctrl | 2030 | 11.7143
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | ctrl | 2040 | 11.1416
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | ctrl | 2050 | 10.5969
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | lower | 2025 | 10.2099
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | lower | 2050 | 9.0074
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | upper | 2025 | 14.414
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, F | 10 | upper | 2050 | 12.7163
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2020 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2025 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2030 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2040 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2050 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2025 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2050 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2025 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2050 | 4
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 8.6215
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 8.4082
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 8.2
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 7.7991
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 7.4178
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 7.1469
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 6.3052
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 10.0898
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 8.9014
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2020 | 3.6949
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2025 | 3.6035
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2030 | 3.5143
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2040 | 3.3425
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2050 | 3.1791
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2025 | 3.063
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2050 | 2.7022
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2025 | 4.3242
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2050 | 3.8149
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH direct,ex apart | Direct district heating substation - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2020 | 200
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2025 | 195
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2030 | 180
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2040 | 175
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | ctrl | 2050 | 150
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2025 | 150
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | lower | 2050 | 125
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2025 | 300
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | G |  | upper | 2050 | 250
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2020 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2030 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2040 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | ctrl | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | lower | 2025 | 0.98
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | lower | 2050 | 0.99
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | upper | 2025 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | I | 9 | upper | 2050 | 1
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 160
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 160
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 160
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 160
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 160
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 150
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 150
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 500
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 500
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2020 | 25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2025 | 25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2030 | 25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2040 | 25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | ctrl | 2050 | 25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2025 | 20
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | lower | 2050 | 20
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2025 | 30
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 8 | upper | 2050 | 30
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | ctrl | 2020 | 76.8
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | ctrl | 2025 | 78.075
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | ctrl | 2030 | 78.18
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | ctrl | 2040 | 76.575
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | ctrl | 2050 | 72.55
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | lower | 2025 | 59.75
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | lower | 2050 | 64.625
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | upper | 2025 | 101.5
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J, D | 8 | upper | 2050 | 99.25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 13.8
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 16.575
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 18.18
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 19.075
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 17.55
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 12.75
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 14.625
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 25.5
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 29.25
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 63
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 61.5
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 60
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 57.5
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 55
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 47
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 50
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 76
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 70
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2020 | 8.5
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2025 | 8.2896
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2030 | 8.0844
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2040 | 7.6892
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | ctrl | 2050 | 7.3133
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2025 | 7.0462
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | lower | 2050 | 6.2163
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2025 | 9.9475
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 10 | upper | 2050 | 8.7759
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2020 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2025 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2030 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2040 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | ctrl | 2050 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2025 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | lower | 2050 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2025 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | C, E |  | upper | 2050 | 4
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 5.95
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 5.8027
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 5.6591
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 5.3824
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 5.1193
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 4.9323
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 4.3514
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 6.9633
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 6.1431
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 2.55
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 2.4869
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 2.4253
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 2.3068
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 2.194
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 2.1139
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.8649
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 2.9843
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2.6328
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
203 DH direct,new apart | Direct district heating substation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2020 | 240
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2025 | 230
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2030 | 220
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2040 | 210
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2050 | 200
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | lower | 2025 | 180
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | lower | 2050 | 150
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | upper | 2025 | 280
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | upper | 2050 | 250
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2020 | 0.82
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2025 | 0.84
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2030 | 0.86
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2040 | 0.88
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2050 | 0.9
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | lower | 2025 | 0.76
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | lower | 2050 | 0.85
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | upper | 2025 | 0.92
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | upper | 2050 | 0.96
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2020 | 10
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2025 | 10
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2030 | 10
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2040 | 10
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2050 | 8
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2025 | 8
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2050 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2025 | 15
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2050 | 12
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | ctrl | 2020 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | ctrl | 2025 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | ctrl | 2030 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | ctrl | 2040 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | ctrl | 2050 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | lower | 2025 | 15
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | lower | 2050 | 15
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | upper | 2025 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3, 10 | upper | 2050 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 2
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 2
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 2
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2020 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2025 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2030 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2040 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2050 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2025 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2050 | 1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2025 | 7
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2050 | 7
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 70
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 60
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 50
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 45
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 40
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 40
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 32
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 80
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 48
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | ctrl | 2020 | 14
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | ctrl | 2025 | 14
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | ctrl | 2030 | 11
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | ctrl | 2040 | 9
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | ctrl | 2050 | 9
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | lower | 2025 | 8
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | lower | 2050 | 4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | upper | 2025 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1, 7 | upper | 2050 | 14
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2020 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2025 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2030 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2040 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2050 | 25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | lower | 2025 | 18
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | lower | 2050 | 18
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | upper | 2025 | 32
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | upper | 2050 | 32
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2020 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2025 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2030 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2040 | 20
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2050 | 16
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | lower | 2025 | 8
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | lower | 2050 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | upper | 2025 | 45
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | upper | 2050 | 36
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2020 | 374.1385
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2025 | 367.6694
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2030 | 362.764
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2040 | 346.7131
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2050 | 331.3661
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | lower | 2025 | 311.2015
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | lower | 2050 | 279.3212
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | upper | 2025 | 441.5432
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | upper | 2050 | 383.411
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 16.56
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 19.55
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 22.22
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 22.89
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 23.4
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 15.3
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 17.55
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 23.8
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 29.25
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 357.5785
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 348.1194
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 340.544
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 323.8231
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 307.9661
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 295.9015
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 261.7712
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 417.7432
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 354.161
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2020 | 4.8645
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2025 | 4.7441
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2030 | 4.6267
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2040 | 4.4005
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2050 | 4.1853
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2025 | 3.3209
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2050 | 2.9297
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2025 | 6.6417
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2050 | 5.8595
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 6
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 5.1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 5.1
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 7.2
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 7.2
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 3.7943
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 3.7004
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 3.6088
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 3.4324
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 3.2646
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 2.5903
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 2.7749
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 5.1806
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 3.9175
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.0702
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0437
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.0179
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.96811
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.92077
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.73059
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.78266
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.4612
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.1049
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
204 Biomass auto,ex single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2020 | 190
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2025 | 185
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2030 | 180
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2040 | 170
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | ctrl | 2050 | 160
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | lower | 2025 | 175
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | lower | 2050 | 150
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | upper | 2025 | 250
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 4 | upper | 2050 | 200
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2020 | 0.78
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2025 | 0.79
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2030 | 0.8
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2040 | 0.82
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | ctrl | 2050 | 0.85
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | lower | 2025 | 0.7
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | lower | 2050 | 0.80485
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | upper | 2025 | 0.85
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B, G | 2 | upper | 2050 | 0.95515
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2020 | 10
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2025 | 8
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2030 | 8
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2040 | 8
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2050 | 8
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2025 | 6
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2050 | 6
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2025 | 12
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2050 | 10
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | ctrl | 2020 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | ctrl | 2025 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | ctrl | 2030 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | ctrl | 2040 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | ctrl | 2050 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | lower | 2025 | 15
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | lower | 2050 | 15
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | upper | 2025 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+10 | upper | 2050 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 2
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 2
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 2
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2020 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2025 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2030 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2040 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2050 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2025 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2050 | 1
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2025 | 7
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2050 | 7
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 70
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 60
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 50
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 45
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 40
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 40
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 32
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 80
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 48
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | ctrl | 2020 | 14
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | ctrl | 2025 | 14
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | ctrl | 2030 | 11
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | ctrl | 2040 | 9
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | ctrl | 2050 | 9
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | lower | 2025 | 8
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | lower | 2050 | 4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | upper | 2025 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, M | 1+7 | upper | 2050 | 14
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2020 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2025 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2030 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2040 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | ctrl | 2050 | 25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | lower | 2025 | 18
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | lower | 2050 | 18
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | upper | 2025 | 32
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 5 | upper | 2050 | 32
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2020 | 20
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2025 | 16
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2030 | 16
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2040 | 16
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | ctrl | 2050 | 16
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | lower | 2025 | 6
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | lower | 2050 | 6
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | upper | 2025 | 36
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  | N | 9 | upper | 2050 | 30
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2020 | 375.3597
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2025 | 368.2417
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2030 | 362.52
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2040 | 346.1491
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | ctrl | 2050 | 330.4821
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | lower | 2025 | 314.5142
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | lower | 2050 | 282.5478
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | upper | 2025 | 444.27
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | I | 6 | upper | 2050 | 381.9264
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 13.11
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 15.725
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 18.18
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 18.53
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 18.72
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 14.875
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 17.55
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 21.25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 23.4
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 362.2497
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 352.5167
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 344.34
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 327.6191
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 311.7621
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 299.6392
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 264.9978
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 423.02
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 358.5264
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2020 | 4.7
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2025 | 4.5837
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2030 | 4.4702
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2040 | 4.2517
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2050 | 4.0438
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2025 | 3.2086
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2050 | 2.8307
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2025 | 6.4171
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2050 | 5.6613
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2020 | 5
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2025 | 5
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2030 | 5
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2040 | 5
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | ctrl | 2050 | 5
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | lower | 2025 | 4.25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | lower | 2050 | 4.25
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | upper | 2025 | 6
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | H |  | upper | 2050 | 6
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 3.666
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 3.5753
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 3.4868
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 3.3163
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 3.1542
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 2.5027
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 2.681
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 5.0054
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 3.785
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.034
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.0084
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.98345
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.93537
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.88964
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.70589
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.75619
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.4118
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.0676
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
204 Biomass auto,new single | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 2400
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 2300
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 2200
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 2100
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 2000
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 2200
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 1800
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 3000
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 2500
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2020 | 0.85
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2025 | 0.87
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2030 | 0.9
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2040 | 0.9
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2050 | 0.9
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | lower | 2025 | 0.79144
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | lower | 2050 | 0.8508
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | upper | 2025 | 0.90856
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | upper | 2050 | 0.9492
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 400
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 400
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 400
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 400
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 400
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 200
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 200
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 600
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 600
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2020 | 20
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2025 | 20
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2030 | 20
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2040 | 20
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2050 | 20
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | lower | 2025 | 15
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | lower | 2050 | 15
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | upper | 2025 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | upper | 2050 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2020 | 2
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2025 | 2
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2030 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2040 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2050 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | lower | 2025 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | lower | 2050 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | upper | 2025 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | upper | 2050 | 2
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2025 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2040 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2025 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 1
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2025 | 7
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 7
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 70
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2025 | 60
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 50
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2040 | 45
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2025 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 32
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2025 | 80
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 48
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2020 | 14
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2025 | 14
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2030 | 11
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2040 | 9
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2050 | 9
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | lower | 2025 | 8
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | lower | 2050 | 4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | upper | 2025 | 20
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | upper | 2050 | 14
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2025 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2040 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 25
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2025 | 18
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 18
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2025 | 32
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 32
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2020 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2025 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2030 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2040 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2050 | 40
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | lower | 2025 | 10
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | lower | 2050 | 10
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | upper | 2025 | 90
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | upper | 2050 | 90
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2020 | 1501.3852
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2025 | 1490.7483
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2030 | 1497.4215
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2040 | 1449.6114
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2050 | 1387.2013
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | lower | 2025 | 1264.0201
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | lower | 2050 | 1181.3312
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | upper | 2025 | 1785.8456
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | upper | 2050 | 1666.8517
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 165.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 195.5
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 222.2
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 228.9
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 234
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 187
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 210.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 255
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 292.5
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 1335.7852
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 1295.2483
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 1275.2215
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 1220.7114
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 1153.2013
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 1077.0201
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 970.7312
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 1530.8456
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 1374.3517
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2020 | 88
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2025 | 85.8219
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2030 | 83.6977
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2040 | 79.6057
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2050 | 75.7138
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2025 | 72.9486
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2050 | 64.3567
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2025 | 102.9863
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2050 | 90.8566
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2020 | 14.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2025 | 14.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2030 | 14.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2040 | 14.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2050 | 14.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2025 | 12.41
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2050 | 12.41
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2025 | 17.52
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2050 | 17.52
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 70.4
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 68.6575
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 66.9582
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 63.6846
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 60.571
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 58.3589
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 51.4854
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 82.389
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 72.6853
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 17.6
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 17.1644
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 16.7395
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 15.9211
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 15.1428
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 14.5897
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 12.8713
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 20.5973
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 18.1713
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
204 Biomass auto,ex apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 1400
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 1360
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 1320
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 1280
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 1250
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 1200
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 1000
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 2000
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 1800
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2020 | 0.85
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2025 | 0.87
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2030 | 0.9
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2040 | 0.9
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | ctrl | 2050 | 0.9
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | lower | 2025 | 0.79144
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | lower | 2050 | 0.8508
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | upper | 2025 | 0.90856
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | B | 2 | upper | 2050 | 0.9492
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 160
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 160
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 160
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 160
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 160
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 80
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 80
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 400
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 400
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2020 | 20
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2025 | 20
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2030 | 20
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2040 | 20
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | ctrl | 2050 | 20
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | lower | 2025 | 15
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | lower | 2050 | 15
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | upper | 2025 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 3+7 | upper | 2050 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2020 | 2
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2025 | 2
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2030 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2040 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | ctrl | 2050 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | lower | 2025 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | lower | 2050 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | upper | 2025 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+2 | upper | 2050 | 2
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2025 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2040 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2025 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2025 | 7
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 7
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 70
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2025 | 60
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 50
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2040 | 45
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 40
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2025 | 40
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2025 | 80
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 48
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2020 | 14
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2025 | 14
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2030 | 11
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2040 | 9
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | ctrl | 2050 | 9
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | lower | 2025 | 8
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | lower | 2050 | 4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | upper | 2025 | 20
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | C, K, L | 6 | upper | 2050 | 14
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2025 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2040 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2025 | 18
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 18
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2025 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2020 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2025 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2030 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2040 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2050 | 32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | lower | 2025 | 12
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | lower | 2050 | 12
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | upper | 2025 | 100
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | upper | 2050 | 100
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2020 | 999.8081
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2025 | 991.2034
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2030 | 991.0529
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2040 | 954.0489
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | ctrl | 2050 | 916.6258
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | lower | 2025 | 841.9633
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | lower | 2050 | 777.7507
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | upper | 2025 | 1184.7638
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F, I | 5 | upper | 2050 | 1106.5812
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 96.6
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 115.6
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 133.32
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 139.52
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 146.25
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 102
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 117
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 170
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 210.6
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 903.2081
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 875.6034
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 857.7329
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 814.5289
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 770.3758
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 739.9633
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 660.7507
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 1014.7638
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 895.9812
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | ctrl | 2020 | 53
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | ctrl | 2025 | 51.6882
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | ctrl | 2030 | 50.4088
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | ctrl | 2040 | 47.9444
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | ctrl | 2050 | 45.6
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | lower | 2025 | 43.935
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | lower | 2050 | 38.7603
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | upper | 2025 | 62.0258
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | H | 8 | upper | 2050 | 54.7204
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2020 | 8.8
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2025 | 8.8
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2030 | 8.8
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2040 | 8.8
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | ctrl | 2050 | 8.8
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2025 | 7.48
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | lower | 2050 | 7.48
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2025 | 10.56
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | E |  | upper | 2050 | 10.56
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 42.4
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 41.3505
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 40.3271
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 38.3555
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 36.5
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 35.148
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 31.0252
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 49.6207
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 43.7763
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 10.6
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 10.3376
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 10.0818
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 9.5889
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 9.1
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 8.787
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 7.7351
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 12.4052
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 10.9441
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
204 Biomass auto,new apart | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | ctrl | 2020 | 200
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | ctrl | 2025 | 190
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | ctrl | 2030 | 180
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | ctrl | 2040 | 160
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | ctrl | 2050 | 150
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | lower | 2025 | 150
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | lower | 2050 | 100
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | upper | 2025 | 250
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  | 5+8 | upper | 2050 | 200
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | ctrl | 2020 | 0.82
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | ctrl | 2025 | 0.83
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | ctrl | 2030 | 0.86
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | ctrl | 2040 | 0.87
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | ctrl | 2050 | 0.88
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | lower | 2025 | 0.7
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | lower | 2050 | 0.80485
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | upper | 2025 | 0.89515
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  | 3 | upper | 2050 | 0.95515
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2020 | 30
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2025 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2030 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2040 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2050 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2025 | 15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2050 | 15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2025 | 50
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2050 | 50
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | ctrl | 2020 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | ctrl | 2025 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | ctrl | 2030 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | ctrl | 2040 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | ctrl | 2050 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | lower | 2025 | 15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | lower | 2050 | 15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | upper | 2025 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 4+8 | upper | 2050 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 2
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 2
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 2
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2020 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2025 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2030 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2040 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2050 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | lower | 2025 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | lower | 2050 | 1
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | upper | 2025 | 7
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 6 | upper | 2050 | 7
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | ctrl | 2020 | 70
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | ctrl | 2025 | 60
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | ctrl | 2030 | 50
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | ctrl | 2040 | 45
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | ctrl | 2050 | 40
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | lower | 2025 | 40
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | lower | 2050 | 32
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | upper | 2025 | 80
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 2+3 | upper | 2050 | 48
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | ctrl | 2020 | 14
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | ctrl | 2025 | 14
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | ctrl | 2030 | 11
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | ctrl | 2040 | 9
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | ctrl | 2050 | 9
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | lower | 2025 | 8
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | lower | 2050 | 4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | upper | 2025 | 20
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | B, H | 4+8 | upper | 2050 | 14
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2020 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2025 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2030 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2040 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | ctrl | 2050 | 25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | lower | 2025 | 18
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | lower | 2050 | 18
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | upper | 2025 | 32
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 6 | upper | 2050 | 32
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2020 | 60
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2025 | 50
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2030 | 40
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2040 | 40
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | ctrl | 2050 | 40
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | lower | 2025 | 15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | lower | 2050 | 15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | upper | 2025 | 200
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 7 | upper | 2050 | 200
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | ctrl | 2020 | 434.1154
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | ctrl | 2025 | 425.5836
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | ctrl | 2030 | 418.0981
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | ctrl | 2040 | 399.7561
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | ctrl | 2050 | 381.3151
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | lower | 2025 | 360.7685
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | lower | 2050 | 320.9003
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | upper | 2025 | 512.5703
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F | 7 | upper | 2050 | 441.7299
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | ctrl | 2020 | 13.8
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | ctrl | 2025 | 16.15
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | ctrl | 2030 | 18.18
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | ctrl | 2040 | 17.44
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | ctrl | 2050 | 17.55
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | lower | 2025 | 12.75
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | lower | 2050 | 11.7
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | upper | 2025 | 21.25
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | G |  | upper | 2050 | 23.4
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 420.3154
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 409.4336
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 399.9181
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 382.3161
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 363.7651
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 348.0185
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 309.2003
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 491.3203
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 418.3299
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | ctrl | 2020 | 6.42
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | ctrl | 2025 | 5.2176
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | ctrl | 2030 | 4.0708
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | ctrl | 2040 | 3.8717
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | ctrl | 2050 | 3.6824
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | lower | 2025 | 4.4349
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | lower | 2050 | 3.1301
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | upper | 2025 | 6.2611
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 9 | upper | 2050 | 4.4189
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 4.494
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 3.6523
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 2.8495
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 2.7102
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 2.5777
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 3.1045
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 2.1911
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 4.3828
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 3.0933
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.926
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.5653
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.2212
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.1615
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.1047
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.3305
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.93902
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.8783
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.3257
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
205 Biomass manual,ex single | Biomass boiler, manual stoking, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2020 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2030 | 30
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2040 | 30
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2050 | 30
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | lower | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | lower | 2050 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | upper | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | upper | 2050 | 40
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2020 | 0.3
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2025 | 0.3
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2030 | 0.3
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2040 | 0.3
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2050 | 0.3
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | lower | 2025 | 0.2
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | lower | 2050 | 0.2
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | upper | 2025 | 0.6
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | upper | 2050 | 0.6
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0.7
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0.72
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0.75
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0.75
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0.75
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | lower | 2025 | 0.62485
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | lower | 2050 | 0.67485
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | upper | 2025 | 0.77515
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | upper | 2050 | 0.82515
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | ctrl | 2020 | 5
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | ctrl | 2025 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | ctrl | 2030 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | ctrl | 2040 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | ctrl | 2050 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | lower | 2025 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | lower | 2050 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | upper | 2025 | 8
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | E |  | upper | 2050 | 8
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2020 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2025 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2030 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2040 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2050 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | lower | 2025 | 15
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | lower | 2050 | 15
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | upper | 2025 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | upper | 2050 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2020 | 125
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2025 | 100
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2030 | 100
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2040 | 100
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2050 | 100
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | lower | 2025 | 75
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | lower | 2050 | 50
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | upper | 2025 | 200
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | upper | 2050 | 175
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2025 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2040 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 4
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2025 | 0.78627
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0.78627
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2025 | 7.2137
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 7.2137
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 90
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 90
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 90
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 90
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 90
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 85.08
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 85.08
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 120
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 120
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2020 | 28.8
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2025 | 25.2
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2030 | 21.6
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2040 | 18
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2050 | 18
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | lower | 2025 | 18
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | lower | 2050 | 10.8
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | upper | 2025 | 180
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | upper | 2050 | 144
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2025 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2040 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 25
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2025 | 17.8986
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 17.8986
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2025 | 32.1014
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 32.1014
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2020 | 50
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2025 | 40
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2030 | 40
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2040 | 40
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2050 | 40
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | lower | 2025 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | lower | 2050 | 20
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | upper | 2025 | 120
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | upper | 2050 | 120
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2020 | 145
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2025 | 141.4111
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2030 | 200.183
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2040 | 195.423
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2050 | 190.663
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | lower | 2025 | 120.1994
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | lower | 2050 | 162.0051
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | upper | 2025 | 169.6933
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | upper | 2050 | 219.906
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | ctrl | 2020 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | ctrl | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | ctrl | 2030 | 3.03
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | ctrl | 2040 | 3.27
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | ctrl | 2050 | 3.51
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | lower | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | lower | 2050 | 2.925
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | upper | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | K |  | upper | 2050 | 4.68
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 145
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 141.4111
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 197.153
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 192.153
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 187.153
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 120.1994
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 159.0801
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 169.6933
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 215.226
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | ctrl | 2020 | 2.52
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | ctrl | 2025 | 1.9661
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | ctrl | 2030 | 3.5
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | ctrl | 2040 | 3.3289
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | ctrl | 2050 | 3.1661
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | lower | 2025 | 1.6712
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | lower | 2050 | 2.6912
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | upper | 2025 | 2.3593
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | F | 8 | upper | 2050 | 3.7994
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.6
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.2483
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.2174
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.1579
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.1013
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.2
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.08
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 2
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 2.13
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.5961
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 3.15
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 2.996
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 2.8495
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.3567
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 2.6912
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.9153
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 3.4194
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0.39
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0.37
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.35
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.33289
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.31661
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.3145
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.26912
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0.444
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0.37994
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
206 Wood stove,single, ex tank | Wood stove without water tank, wood logs - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2020 | 140
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2025 | 135
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2030 | 160
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2040 | 150
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | ctrl | 2050 | 130
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | lower | 2025 | 110
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | lower | 2050 | 100
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | upper | 2025 | 180
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | J |  | upper | 2050 | 160
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 0.1
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 0.1
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 0.4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 0.4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2020 | 0.45
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2025 | 0.45
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2030 | 0.45
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2040 | 0.45
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | ctrl | 2050 | 0.45
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | lower | 2025 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | lower | 2050 | 0.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | upper | 2025 | 0.7
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | C |  | upper | 2050 | 0.7
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0.7
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0.72
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0.75
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0.75
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0.75
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | lower | 2025 | 0.62485
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | lower | 2050 | 0.67485
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | upper | 2025 | 0.77515
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  |  |  | upper | 2050 | 0.82515
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2020 | 12
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2025 | 10
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2030 | 10
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2040 | 10
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2050 | 10
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2025 | 8
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2050 | 8
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2025 | 12
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2050 | 12
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2020 | 20
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2025 | 20
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2030 | 20
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2040 | 20
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | ctrl | 2050 | 20
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | lower | 2025 | 15
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | lower | 2050 | 15
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | upper | 2025 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 2+5 | upper | 2050 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2020 | 125
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2025 | 100
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2030 | 100
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2040 | 100
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | ctrl | 2050 | 100
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | lower | 2025 | 75
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | lower | 2050 | 50
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | upper | 2025 | 200
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 1+3 | upper | 2050 | 175
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2025 | 4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2040 | 4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2025 | 0.78627
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0.78627
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2025 | 7.2137
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 7.2137
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 90
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2025 | 90
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 90
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2040 | 90
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 90
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2025 | 85.08
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 85.08
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2025 | 120
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 120
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2020 | 28.8
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2025 | 25.2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2030 | 21.6
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2040 | 18
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | ctrl | 2050 | 18
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | lower | 2025 | 18
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | lower | 2050 | 10.8
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | upper | 2025 | 108
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | A, G, H, I | 1+6+7 | upper | 2050 | 72
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2025 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2040 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 25
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2025 | 17.8986
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 17.8986
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2025 | 32.1014
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 32.1014
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2020 | 48
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2025 | 40
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2030 | 40
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2040 | 40
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | ctrl | 2050 | 40
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | lower | 2025 | 24
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | lower | 2050 | 24
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | upper | 2025 | 120
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  | 5 | upper | 2050 | 120
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2020 | 191.5808
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2025 | 220.7831
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2030 | 250.9761
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2040 | 247.1151
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | ctrl | 2050 | 242.8731
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | lower | 2025 | 187.726
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | lower | 2050 | 206.2101
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | upper | 2025 | 264.7107
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 4 | upper | 2050 | 291.5361
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2020 | 9.66
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2025 | 11.475
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2030 | 16.16
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2040 | 16.35
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2050 | 15.21
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2025 | 9.35
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2050 | 11.7
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2025 | 15.3
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2050 | 18.72
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 181.9208
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 209.3081
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 234.8161
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 230.7651
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 227.6631
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 178.376
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 194.5101
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 249.4107
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 272.8161
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2020 | 4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2025 | 3.2508
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2030 | 4.5
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2040 | 4.28
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | ctrl | 2050 | 4.0707
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2025 | 2.7632
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | lower | 2050 | 3.4601
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2025 | 3.901
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 8 | upper | 2050 | 4.8849
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.6
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.3003
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.2681
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.2061
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.1472
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 2
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.7
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 3.4
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 2.7632
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 3.825
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 3.638
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 3.4601
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 2.3487
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 2.9411
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 3.3158
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 4.1522
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0.6
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0.48762
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.675
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.642
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.61061
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.41448
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.51902
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0.58515
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0.73273
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
206 Wood stove, single n w tank | Wood stove with water tank - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2020 | 0.25
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2025 | 0.25
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2030 | 0.25
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2040 | 0.25
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2050 | 0.25
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2025 | 0.2
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2050 | 0.2
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2025 | 0.3
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2050 | 0.3
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2020 | 3.15
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2025 | 3.3
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2030 | 3.45
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2040 | 3.6
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2050 | 3.7
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | lower | 2025 | 2.85
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | lower | 2050 | 3.3
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | upper | 2025 | 3.75
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | upper | 2050 | 4.35
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2020 | 7
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2025 | 7
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2030 | 7
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2040 | 7
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2050 | 7
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2025 | 5
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2050 | 5
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2025 | 15
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2050 | 15
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 16
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 16
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 16
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 16
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 16
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 14
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 14
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 20
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 20
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 311.4094
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 227.5913
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 224.3101
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 218.2211
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 212.1321
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 175.2125
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 194.8089
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 273.4227
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 229.4553
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2020 | 311.4094
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2025 | 227.5913
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2030 | 224.3101
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2040 | 218.2211
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2050 | 212.1321
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2025 | 175.2125
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2050 | 194.8089
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2025 | 273.4227
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2050 | 229.4553
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 10.953
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 10.103
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 9.2529
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 8.5634
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 7.874
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 7.4497
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 5.9055
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 12.9396
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 9.8425
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2020 | 6.9208
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2025 | 6.5748
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2030 | 6.2287
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2040 | 5.9173
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2050 | 5.6059
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | lower | 2025 | 5.1007
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | lower | 2050 | 4.2044
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | upper | 2025 | 9.1812
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | upper | 2050 | 7.0073
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 4.0322
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 3.5282
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 3.0242
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 2.6461
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 2.2681
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 2.349
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 1.7011
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 3.7584
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 2.8352
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2020 | 4.05
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2025 | 4.25
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2030 | 4.4
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2040 | 4.55
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2050 | 4.65
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | lower | 2025 | 3.35
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | lower | 2050 | 3.85
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | upper | 2025 | 4.65
207 HP air-water,ex single | Heat pump, Air-to-water - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | upper | 2050 | 5.15
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2020 | 0.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2025 | 0.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2030 | 0.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2040 | 0.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2050 | 0.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2025 | 0.2
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2050 | 0.2
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2025 | 0.3
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2050 | 0.3
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2020 | 600
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2025 | 550
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2030 | 500
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2040 | 450
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2050 | 400
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2025 | 400
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2050 | 250
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2025 | 1000
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2050 | 800
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2020 | 2.9
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2025 | 3.05
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2030 | 3.2
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2040 | 3.35
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2050 | 3.5
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | lower | 2025 | 2.65
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | lower | 2050 | 3.1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | upper | 2025 | 3.4
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | upper | 2050 | 4
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2020 | 320
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2025 | 320
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2030 | 320
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2040 | 320
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2050 | 320
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | lower | 2025 | 300
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | lower | 2050 | 300
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | upper | 2025 | 500
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | upper | 2050 | 500
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 3465.8537
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 3448.8915
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 3430.3294
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 3387.4743
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 3343.8191
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 3302.5756
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 3208.4716
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 3620.7075
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 3508.4167
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 41.4
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 46.75
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 50.5
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 49.05
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 46.8
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 34
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 29.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 85
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 93.6
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2020 | 3424.4537
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2025 | 3402.1415
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2030 | 3379.8294
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2040 | 3338.4243
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2050 | 3297.0191
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | lower | 2025 | 3268.5756
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | lower | 2050 | 3179.2216
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | upper | 2025 | 3535.7075
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | upper | 2050 | 3414.8167
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 220.1342
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 197.1141
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 174.094
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 155.9295
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 137.7651
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 167.547
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 103.3238
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 236.5369
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 172.2064
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2020 | 179.8658
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2025 | 161.8792
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2030 | 143.8926
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2040 | 129.5034
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2050 | 115.1141
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | lower | 2025 | 137.5973
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | lower | 2050 | 86.3356
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | upper | 2025 | 194.255
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | upper | 2050 | 143.8926
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 40.2685
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 35.2349
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 30.2013
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 26.4262
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 22.651
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 29.9497
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 16.9883
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 42.2819
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 28.3138
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2020 | 3.7
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2025 | 3.85
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2030 | 3.95
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2040 | 4.1
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2050 | 4.25
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | lower | 2025 | 3.15
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | lower | 2050 | 3.6
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | upper | 2025 | 4.3
207 HP air-water,ex apart | Heat pump, Air-to-water - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | upper | 2050 | 4.7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2020 | 0.25
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2025 | 0.25
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2030 | 0.25
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2040 | 0.25
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2050 | 0.25
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2025 | 0.2
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2050 | 0.2
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2025 | 0.3
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2050 | 0.3
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | ctrl | 2020 | 3
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | ctrl | 2025 | 3.15
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | ctrl | 2030 | 3.3
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | ctrl | 2040 | 3.45
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | ctrl | 2050 | 3.55
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | lower | 2025 | 2.7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | lower | 2050 | 3.15
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | upper | 2025 | 3.55
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | M,O | 29 | upper | 2050 | 4.15
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2020 | 7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2025 | 7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2030 | 7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2040 | 7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2050 | 7
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2025 | 5
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2050 | 5
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2025 | 15
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2050 | 15
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | ctrl | 2020 | 12
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | ctrl | 2025 | 12
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | ctrl | 2030 | 12
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | ctrl | 2040 | 12
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | ctrl | 2050 | 12
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | lower | 2025 | 10
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | lower | 2050 | 10
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | upper | 2025 | 20
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | O,N |  | upper | 2050 | 20
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 359.7315
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 275.9134
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 272.6322
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 266.5432
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 260.4543
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 223.5346
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 243.1311
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 321.7449
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 277.7774
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | ctrl | 2020 | 359.7315
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | ctrl | 2025 | 275.9134
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | ctrl | 2030 | 272.6322
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | ctrl | 2040 | 266.5432
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | ctrl | 2050 | 260.4543
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | lower | 2025 | 223.5346
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | lower | 2050 | 243.1311
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | upper | 2025 | 321.7449
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E | 1 | upper | 2050 | 277.7774
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 8.596
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 7.8638
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 7.1315
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 6.5482
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 5.9648
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 6.2255
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 4.4736
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 9.1651
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 7.456
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2020 | 4.5638
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2025 | 4.3356
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2030 | 4.1074
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2040 | 3.902
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2050 | 3.6966
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | lower | 2025 | 3.8765
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | lower | 2050 | 2.7725
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | upper | 2025 | 5.4067
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | upper | 2050 | 4.6208
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 4.0322
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 3.5282
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 3.0242
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 2.6461
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 2.2681
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 2.349
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 1.7011
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 3.7584
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 2.8352
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | ctrl | 2020 | 4
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | ctrl | 2025 | 4.2
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | ctrl | 2030 | 4.35
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | ctrl | 2040 | 4.5
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | ctrl | 2050 | 4.6
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | lower | 2025 | 3.3
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | lower | 2050 | 3.8
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | upper | 2025 | 4.6
207 HP air-water LPP,ex single | Heat pump, Air-to-water, low-price product - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | M,O |  | upper | 2050 | 5.05
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2020 | 0.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2025 | 0.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2030 | 0.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2040 | 0.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2050 | 0.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2025 | 0.2
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2050 | 0.2
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2025 | 0.3
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2050 | 0.3
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | ctrl | 2020 | 2.95
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | ctrl | 2025 | 3.1
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | ctrl | 2030 | 3.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | ctrl | 2040 | 3.4
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | ctrl | 2050 | 3.5
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | lower | 2025 | 2.65
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | lower | 2050 | 3.15
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | upper | 2025 | 3.45
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4,5,6,7,8,9,10 | upper | 2050 | 4.05
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2020 | 5
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2025 | 5
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2030 | 5
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2040 | 5
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | ctrl | 2050 | 5
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2025 | 3
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | lower | 2050 | 3
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2025 | 8
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A | 1 | upper | 2050 | 6
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 16
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 16
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 16
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 16
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 16
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 14
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 14
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 20
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 20
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 277.0516
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 193.2334
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 189.9523
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 183.8633
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 177.7743
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 140.8547
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 160.4511
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 239.0649
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 195.0974
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2020 | 277.0516
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2025 | 193.2334
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2030 | 189.9523
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2040 | 183.8633
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2050 | 177.7743
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2025 | 140.8547
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2050 | 160.4511
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2025 | 239.0649
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2050 | 195.0974
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 6.0711
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 5.7273
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 5.3835
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 5.0801
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 4.7767
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 5.3188
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 3.8213
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 9.1275
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 5.9709
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2020 | 4.4604
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2025 | 4.2374
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2030 | 4.0144
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2040 | 3.8136
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | ctrl | 2050 | 3.6129
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | lower | 2025 | 3.953
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | lower | 2050 | 2.8903
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | upper | 2025 | 7.1409
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | B | 1 | upper | 2050 | 4.5162
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 1.6107
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 1.4899
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 1.3691
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 1.2664
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 1.1638
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 1.3658
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 0.93101
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 1.9866
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 1.4547
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | ctrl | 2020 | 3.75
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | ctrl | 2025 | 3.95
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | ctrl | 2030 | 4.15
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | ctrl | 2040 | 4.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | ctrl | 2050 | 4.35
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | lower | 2025 | 3.25
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | lower | 2050 | 3.75
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | upper | 2025 | 4.2
207 HP air-water,new single | Heat pump, Air-to-water - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4,5,6,7,8,9,10 | upper | 2050 | 4.95
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2020 | 0.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2025 | 0.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2030 | 0.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2040 | 0.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | ctrl | 2050 | 0.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2025 | 0.2
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | lower | 2050 | 0.2
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2025 | 0.3
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H | 3 | upper | 2050 | 0.3
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2020 | 350
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2025 | 325
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2030 | 300
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2040 | 250
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2050 | 250
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2025 | 250
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2050 | 200
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2025 | 500
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2050 | 400
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2020 | 2.75
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2025 | 2.9
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2030 | 3
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2040 | 3.15
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | ctrl | 2050 | 3.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | lower | 2025 | 2.5
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | lower | 2050 | 2.9
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | upper | 2025 | 3.15
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L,Z | 4, 5, 11, 12 | upper | 2050 | 3.8
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2020 | 160
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2025 | 160
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2030 | 160
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2040 | 160
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | ctrl | 2050 | 160
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | lower | 2025 | 140
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | lower | 2050 | 140
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | upper | 2025 | 200
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A,C | 1 | upper | 2050 | 200
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 2233.9896
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 2215.1524
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 2195.5153
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 2151.0601
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 2111.655
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 2075.2115
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 1988.0075
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 2363.5934
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 2247.0026
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 24.15
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 27.625
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 30.3
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 27.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 29.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 21.25
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 23.4
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 42.5
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 46.8
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2020 | 2209.8396
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2025 | 2187.5274
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2030 | 2165.2153
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2040 | 2123.8101
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | ctrl | 2050 | 2082.405
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | lower | 2025 | 2053.9615
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | lower | 2050 | 1964.6075
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | upper | 2025 | 2321.0934
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D | 1 | upper | 2050 | 2200.2026
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 123.4899
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 110.3758
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 97.2617
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 86.9617
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 76.6617
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 93.8195
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 57.4963
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 132.451
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 95.8272
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2020 | 92.8859
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2025 | 83.5973
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2030 | 74.3087
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2040 | 66.8779
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | ctrl | 2050 | 59.447
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | lower | 2025 | 71.0577
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | lower | 2050 | 44.5852
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | upper | 2025 | 100.3168
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | AC | 1 | upper | 2050 | 74.3087
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 30.604
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 26.7785
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 22.953
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 20.0839
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 17.2148
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 22.7617
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 12.9111
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 32.1342
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 21.5185
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2020 | 3.45
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2025 | 3.6
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2030 | 3.75
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2040 | 3.85
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | ctrl | 2050 | 3.95
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | lower | 2025 | 3
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | lower | 2050 | 3.4
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | upper | 2025 | 3.85
207 HP air-water,new apart | Heat pump, Air-to-water - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G I,L | 4, 5, 11, 12 | upper | 2050 | 4.5
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2020 | 3.45
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2025 | 3.55
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2030 | 3.65
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2040 | 3.8
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2050 | 3.85
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | lower | 2025 | 3.05
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | lower | 2050 | 3.45
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | upper | 2025 | 3.75
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | upper | 2050 | 4.35
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 7
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 7
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 7
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 7
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 7
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 5
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 5
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 15
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 15
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2020 | 20
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2025 | 20
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2030 | 20
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2040 | 20
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2050 | 20
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2025 | 18
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2050 | 18
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2025 | 40
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2050 | 40
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 287.2483
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 203.4302
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 200.149
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 194.06
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 187.971
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 151.0514
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 170.6479
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 249.2617
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 205.2942
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2020 | 287.2483
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2025 | 203.4302
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2030 | 200.149
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2040 | 194.06
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2050 | 187.971
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | lower | 2025 | 151.0514
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | lower | 2050 | 170.6479
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | upper | 2025 | 249.2617
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | upper | 2050 | 205.2942
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2020 | 14.5056
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2025 | 13.7803
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2030 | 13.055
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2040 | 12.4023
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2050 | 11.7495
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | lower | 2025 | 11.2215
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | lower | 2050 | 8.8121
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | upper | 2025 | 16.3221
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | upper | 2050 | 14.6869
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2020 | 7.0604
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2025 | 6.7074
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2030 | 6.3544
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2040 | 6.0366
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2050 | 5.7189
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | lower | 2025 | 6.1208
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | lower | 2050 | 4.2892
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | upper | 2025 | 8.903
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | upper | 2050 | 7.1487
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2020 | 7.4452
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2025 | 7.0729
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2030 | 6.7007
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2040 | 6.3656
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2050 | 6.0306
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | lower | 2025 | 5.1007
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | lower | 2050 | 4.523
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | upper | 2025 | 7.4192
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | upper | 2050 | 7.5383
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2020 | 4.35
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2025 | 4.45
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2030 | 4.55
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2040 | 4.65
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2050 | 4.7
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | lower | 2025 | 3.85
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | lower | 2050 | 4.15
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | upper | 2025 | 4.95
207 HP ground-water,ex single | Heat pump, Ground source - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | upper | 2050 | 5.35
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 600
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 550
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 500
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 450
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 400
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 400
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 250
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 1000
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 800
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | ctrl | 2020 | 3.2
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | ctrl | 2025 | 3.3
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | ctrl | 2030 | 3.4
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | ctrl | 2040 | 3.55
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | ctrl | 2050 | 3.6
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | lower | 2025 | 2.85
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | lower | 2050 | 3.15
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | upper | 2025 | 3.45
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4, 5, 11, 12 | upper | 2050 | 4
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 320
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 320
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 320
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 320
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 320
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 300
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 300
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 500
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 500
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2020 | 20
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2025 | 20
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2030 | 20
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2040 | 20
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2050 | 20
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2025 | 18
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2050 | 18
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2025 | 40
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2050 | 40
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 2144.7506
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 2127.7884
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 2109.2263
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 2066.3712
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 2022.716
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 1981.4725
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 1887.3685
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 2299.6044
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 2187.3136
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 41.4
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 46.75
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 50.5
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 49.05
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 46.8
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 34
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 29.25
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 85
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 93.6
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2020 | 2103.3506
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2025 | 2081.0384
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2030 | 2058.7263
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2040 | 2017.3212
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2050 | 1975.916
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | lower | 2025 | 1947.4725
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | lower | 2050 | 1858.1185
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | upper | 2025 | 2214.6044
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | upper | 2050 | 2093.7136
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2020 | 205.1007
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2025 | 189.7181
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2030 | 174.3356
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2040 | 161.2604
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2050 | 148.1852
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | lower | 2025 | 161.2604
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | lower | 2050 | 111.1389
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | upper | 2025 | 227.6617
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | upper | 2050 | 185.2315
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2020 | 115.9732
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2025 | 107.2752
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2030 | 98.5772
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2040 | 91.1839
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2050 | 83.7906
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | lower | 2025 | 91.1839
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | lower | 2050 | 62.843
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | upper | 2025 | 128.7302
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | upper | 2050 | 104.7383
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2020 | 89.1275
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2025 | 82.443
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2030 | 75.7584
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2040 | 70.0765
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2050 | 64.3946
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | lower | 2025 | 70.0765
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | lower | 2050 | 48.296
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | upper | 2025 | 98.9315
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | upper | 2050 | 80.4933
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2020 | 4.1
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2025 | 4.2
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2030 | 4.3
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2040 | 4.4
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2050 | 4.45
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | lower | 2025 | 3.65
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | lower | 2050 | 3.9
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | upper | 2025 | 4.6
207 HP ground-water,ex apart | Heat pump, Ground source - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | upper | 2050 | 4.9
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2020 | 3.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2025 | 3.35
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2030 | 3.45
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2040 | 3.6
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | ctrl | 2050 | 3.75
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | lower | 2025 | 2.85
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | lower | 2050 | 3.35
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | upper | 2025 | 3.95
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, K, L, Z | 4,5,6,7,8,9,10 | upper | 2050 | 4.45
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 5
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 5
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 5
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 5
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 5
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 3
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 3
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 8
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 6
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2020 | 20
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2025 | 20
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2030 | 20
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2040 | 20
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2050 | 20
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2025 | 18
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2050 | 18
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2025 | 40
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2050 | 40
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 274.7084
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 190.8903
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 187.6091
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 181.5201
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 175.4312
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 138.5115
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 158.108
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 236.7218
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 192.7543
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2020 | 274.7084
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2025 | 190.8903
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2030 | 187.6091
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2040 | 181.5201
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | ctrl | 2050 | 175.4312
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | lower | 2025 | 138.5115
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | lower | 2050 | 158.108
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | upper | 2025 | 236.7218
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F,S |  | upper | 2050 | 192.7543
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2020 | 9.6644
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2025 | 9.1812
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2030 | 8.698
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2040 | 8.2631
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | ctrl | 2050 | 7.8282
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | lower | 2025 | 7.804
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | lower | 2050 | 5.8711
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | upper | 2025 | 11.0174
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | Q |  | upper | 2050 | 9.7852
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2020 | 5.8389
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2025 | 5.547
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2030 | 5.255
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2040 | 4.9923
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | ctrl | 2050 | 4.7295
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | lower | 2025 | 4.7149
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | lower | 2050 | 3.5471
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | upper | 2025 | 6.6564
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, B |  | upper | 2050 | 5.9119
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2020 | 3.8255
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2025 | 3.6342
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2030 | 3.443
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2040 | 3.2708
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | ctrl | 2050 | 3.0987
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | lower | 2025 | 3.0891
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | lower | 2050 | 2.324
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | upper | 2025 | 4.3611
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | Q, R, AB |  | upper | 2050 | 3.8733
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2020 | 4.05
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2025 | 4.15
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2030 | 4.25
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2040 | 4.4
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | ctrl | 2050 | 4.55
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | lower | 2025 | 3.45
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | lower | 2050 | 3.75
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | upper | 2025 | 4.55
207 HP ground-water,new single | Heat pump, Ground source - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G, I, L | 4,5,6,7,8,9,10 | upper | 2050 | 5.05
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2020 | 350
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2025 | 325
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2030 | 300
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2040 | 250
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | ctrl | 2050 | 250
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2025 | 250
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | lower | 2050 | 200
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2025 | 500
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 2 | upper | 2050 | 400
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | ctrl | 2020 | 2.9
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | ctrl | 2025 | 3
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | ctrl | 2030 | 3.1
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | ctrl | 2040 | 3.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | ctrl | 2050 | 3.4
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | lower | 2025 | 2.65
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | lower | 2050 | 3.05
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | upper | 2025 | 3.6
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G,I,K,L, Z | 4, 5, 11, 12 | upper | 2050 | 4.05
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2020 | 160
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2025 | 160
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2030 | 160
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2040 | 160
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | ctrl | 2050 | 160
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2025 | 140
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | lower | 2050 | 140
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2025 | 200
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A |  | upper | 2050 | 200
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2020 | 20
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2025 | 20
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2030 | 20
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2040 | 20
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | ctrl | 2050 | 20
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2025 | 18
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | lower | 2050 | 18
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2025 | 40
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P | 1 | upper | 2050 | 40
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 1543.2252
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 1524.388
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 1504.7509
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 1460.2958
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 1420.8906
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 1384.4471
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 1297.2431
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 1672.829
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 1556.2382
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 24.15
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 27.625
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 30.3
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 27.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 29.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 21.25
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 23.4
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 42.5
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 46.8
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2020 | 1519.0752
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2025 | 1496.763
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2030 | 1474.4509
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2040 | 1433.0458
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | ctrl | 2050 | 1391.6406
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | lower | 2025 | 1363.1971
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | lower | 2050 | 1273.8431
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | upper | 2025 | 1630.329
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | D,F,S |  | upper | 2050 | 1509.4382
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2020 | 117.047
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2025 | 108.2685
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2030 | 99.4899
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2040 | 92.0282
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | ctrl | 2050 | 84.5664
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | lower | 2025 | 92.0282
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | lower | 2050 | 63.4248
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | upper | 2025 | 129.9221
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | T |  | upper | 2050 | 105.7081
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2020 | 59.0604
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2025 | 54.6309
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2030 | 50.2013
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2040 | 46.4362
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | ctrl | 2050 | 42.6711
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | lower | 2025 | 46.4362
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | lower | 2050 | 32.0034
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | upper | 2025 | 65.557
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AC |  | upper | 2050 | 53.3389
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2020 | 57.9866
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2025 | 53.6376
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2030 | 49.2886
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2040 | 45.5919
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | ctrl | 2050 | 41.8953
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | lower | 2025 | 45.5919
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | lower | 2050 | 31.4215
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | upper | 2025 | 64.3651
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | T, R, AB |  | upper | 2050 | 52.3691
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2020 | 3.7
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2025 | 3.8
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2030 | 3.9
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2040 | 4.05
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | ctrl | 2050 | 4.15
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | lower | 2025 | 3.15
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | lower | 2050 | 3.5
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | upper | 2025 | 4.2
207 HP ground-water,new apart | Heat pump, Ground source - apartment complex - new building | Technology specific data | Heat efficiency (annual average, net, floor heating) [p.u.] | p.u. |  | G,I,L | 4, 5, 11, 12 | upper | 2050 | 4.6
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | upper | 2050 | 100
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2020 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2025 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2030 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2040 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2050 | 0.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2025 | 0.2
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2050 | 0.2
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2025 | 0.7
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2050 | 0.7
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2020 | 4.85
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2025 | 5.1
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2030 | 5.3
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2040 | 5.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2050 | 5.6
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | lower | 2025 | 4
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | lower | 2050 | 4.8
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | upper | 2025 | 6
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | upper | 2050 | 6.8
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2020 | 6.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2025 | 6.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2030 | 6.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2040 | 6.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2050 | 6.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | lower | 2025 | 2.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | lower | 2050 | 2.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | upper | 2025 | 8.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | upper | 2050 | 8.5
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 12
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 12
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 12
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 12
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 12
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 10
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 10
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 15
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 15
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 150.3356
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 102.1402
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 100.2535
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 96.7523
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 93.2511
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 79.2244
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 83.2903
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 125.0559
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 106.5322
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2020 | 150.3356
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2025 | 102.1402
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2030 | 100.2535
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2040 | 96.7523
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2050 | 93.2511
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2025 | 79.2244
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2050 | 83.2903
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2025 | 125.0559
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2050 | 106.5322
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 1.698
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 1.6565
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 1.615
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 1.5379
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 1.4609
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 1.2571
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 0.9496
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 2.1999
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 3.3601
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 1.204
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 1.1746
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 1.1452
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 1.0905
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 1.0359
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 0.87996
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 0.67335
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 1.5714
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 2.3826
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 0.49396
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 0.48188
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 0.46981
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 0.4474
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 0.425
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 0.37713
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 0.27625
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 0.62855
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 0.97749
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-air,ex single | Heat pump, Air-to-air - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | W |  | upper | 2050 | 1
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2020 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2025 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2030 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2040 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2050 | 0.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2025 | 0.2
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2050 | 0.2
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2025 | 0.7
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2050 | 0.7
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2020 | 4.6
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2025 | 4.85
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2030 | 5.05
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2040 | 5.25
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | ctrl | 2050 | 5.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | lower | 2025 | 4
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | lower | 2050 | 4.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | upper | 2025 | 5.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | G, I, L,Y, Z | 4, 14, 6, 13 | upper | 2050 | 6.3
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2020 | 2.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2025 | 2.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2030 | 2.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2040 | 2.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | ctrl | 2050 | 2.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | lower | 2025 | 2
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | lower | 2050 | 2
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | upper | 2025 | 6.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | U | 1,15 | upper | 2050 | 6.5
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 12
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 12
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 12
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 12
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 12
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 10
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 10
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 15
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 15
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 150.3356
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 102.1402
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 100.2535
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 96.7523
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 93.2511
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 79.2244
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 83.2903
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 125.0559
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 106.5322
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2020 | 150.3356
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2025 | 102.1402
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2030 | 100.2535
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2040 | 96.7523
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | ctrl | 2050 | 93.2511
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2025 | 79.2244
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | lower | 2050 | 83.2903
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2025 | 125.0559
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E,F | 1 | upper | 2050 | 106.5322
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 1.114
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 1.0868
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 1.0596
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 1.009
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 0.95851
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 0.83806
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 0.62303
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 1.5714
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 2.2046
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2020 | 0.62009
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2025 | 0.60493
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2030 | 0.58977
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2040 | 0.56164
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | ctrl | 2050 | 0.53351
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2025 | 0.46093
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | lower | 2050 | 0.34678
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2025 | 0.94282
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 1 | upper | 2050 | 1.2271
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2020 | 0.49396
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2025 | 0.48188
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2030 | 0.46981
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2040 | 0.4474
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | ctrl | 2050 | 0.425
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2025 | 0.37713
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | lower | 2050 | 0.27625
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2025 | 0.62855
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 1 | upper | 2050 | 0.97749
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP air-air,new single | Heat pump, Air-to-air - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 16,17,20 | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | ctrl | 2020 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | ctrl | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | ctrl | 2030 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | ctrl | 2040 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | ctrl | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | lower | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | lower | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | upper | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 16,17,20 | upper | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 16,17,20 | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 20 | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | ctrl | 2020 | 0.9
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | ctrl | 2025 | 0.9
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | ctrl | 2030 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | ctrl | 2040 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | ctrl | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | upper | 2025 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V | 16,20 | upper | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | ctrl | 2020 | 3.3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | ctrl | 2025 | 3.4
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | ctrl | 2030 | 3.5
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | ctrl | 2040 | 3.6
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | ctrl | 2050 | 3.7
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | lower | 2025 | 3.2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | lower | 2050 | 3.2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | upper | 2025 | 3.5
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 16,17,20 | upper | 2050 | 4
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | ctrl | 2020 | 2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | ctrl | 2025 | 2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | ctrl | 2030 | 3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | ctrl | 2040 | 3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | ctrl | 2050 | 3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | lower | 2025 | 2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | lower | 2050 | 2
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | upper | 2025 | 3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 16,17,19 | upper | 2050 | 3
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | ctrl | 2020 | 15
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | ctrl | 2025 | 15
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | ctrl | 2030 | 15
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | ctrl | 2040 | 15
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | ctrl | 2050 | 15
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | lower | 2025 | 10
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | lower | 2050 | 10
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | upper | 2025 | 20
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 16,17,20 | upper | 2050 | 20
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 202.0589
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 191.8485
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 181.6381
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 172.5024
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 163.3668
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 153.0706
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 161.2172
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 255.1177
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 268.6954
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | ctrl | 2020 | 202.0589
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | ctrl | 2025 | 191.8485
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | ctrl | 2030 | 181.6381
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | ctrl | 2040 | 172.5024
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | ctrl | 2050 | 163.3668
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | lower | 2025 | 153.0706
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | lower | 2050 | 161.2172
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | upper | 2025 | 255.1177
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 16,17,20 | upper | 2050 | 268.6954
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | ctrl | 2020 | 2.307
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | ctrl | 2025 | 2.2126
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | ctrl | 2030 | 2.122
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | ctrl | 2040 | 2.0436
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | ctrl | 2050 | 1.9719
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | lower | 2025 | 1.77
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | lower | 2050 | 1.5775
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | upper | 2025 | 2.5444
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 18,21,22,23 | upper | 2050 | 2.2677
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | ctrl | 2020 | 2.1059
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | ctrl | 2025 | 2.0191
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | ctrl | 2030 | 1.9393
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | ctrl | 2040 | 1.8717
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | ctrl | 2050 | 1.8107
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | lower | 2025 | 1.6153
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | lower | 2050 | 1.47
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | upper | 2025 | 2.3408
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 16,17,20 | upper | 2050 | 1.8378
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | ctrl | 2020 | 0.20112
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | ctrl | 2025 | 0.19346
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | ctrl | 2030 | 0.18271
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | ctrl | 2040 | 0.17197
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | ctrl | 2050 | 0.16122
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | lower | 2025 | 0.15477
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | lower | 2050 | 0.10748
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | upper | 2025 | 0.20364
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 16,17,20 | upper | 2050 | 0.42991
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP ventilation,new single | Heat pump, ventilation - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | ctrl | 2020 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | ctrl | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | ctrl | 2030 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | ctrl | 2040 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | ctrl | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | lower | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | lower | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | upper | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  | 20,26 | upper | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2020 | 0.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2025 | 0.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2030 | 0.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2040 | 0.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | ctrl | 2050 | 0.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2025 | 0.2
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | lower | 2050 | 0.2
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2025 | 0.3
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | H |  | upper | 2050 | 0.3
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | ctrl | 2020 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | ctrl | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | ctrl | 2030 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | ctrl | 2040 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | ctrl | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | lower | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | lower | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | upper | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  | 20,26 | upper | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | ctrl | 2020 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | ctrl | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | ctrl | 2030 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | ctrl | 2040 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | ctrl | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | lower | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | lower | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | upper | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  | 20,26 | upper | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | ctrl | 2020 | 350
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | ctrl | 2025 | 325
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | ctrl | 2030 | 300
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | ctrl | 2040 | 250
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | ctrl | 2050 | 250
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | lower | 2025 | 250
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | lower | 2050 | 200
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | upper | 2025 | 500
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | AA | 24,20 | upper | 2050 | 400
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2020 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2030 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2040 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2025 | 0.7
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2050 | 0.7
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2020 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2030 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2040 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | ctrl | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2025 | 0.7
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | lower | 2050 | 0.7
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2025 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | V |  | upper | 2050 | 1
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | ctrl | 2020 | 5.4
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | ctrl | 2025 | 5.45
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | ctrl | 2030 | 5.5
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | ctrl | 2040 | 5.6
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | ctrl | 2050 | 5.7
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | lower | 2025 | 5.3
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | lower | 2050 | 5.3
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | upper | 2025 | 5.6
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | X, I | 24,26,27,28 | upper | 2050 | 6.2
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | ctrl | 2020 | 160
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | ctrl | 2025 | 160
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | ctrl | 2030 | 160
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | ctrl | 2040 | 160
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | ctrl | 2050 | 160
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | lower | 2025 | 140
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | lower | 2050 | 140
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | upper | 2025 | 200
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  | 19,25 | upper | 2050 | 200
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | ctrl | 2020 | 15
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | ctrl | 2025 | 15
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | ctrl | 2030 | 15
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | ctrl | 2040 | 15
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | ctrl | 2050 | 15
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | lower | 2025 | 12
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | lower | 2050 | 12
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | upper | 2025 | 20
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  | 20,27 | upper | 2050 | 20
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 1034.4447
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 987.405
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 939.5652
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 890.837
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 847.1588
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 531.7713
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 560.7908
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 2084.585
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 2196.3632
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 24.15
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 27.625
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 30.3
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 27.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 29.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 21.25
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 23.4
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 42.5
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 46.8
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | ctrl | 2020 | 1010.2947
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | ctrl | 2025 | 959.78
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | ctrl | 2030 | 909.2652
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | ctrl | 2040 | 863.587
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | ctrl | 2050 | 817.9088
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | lower | 2025 | 510.5213
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | lower | 2050 | 537.3908
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | upper | 2025 | 2042.085
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  | 27 | upper | 2050 | 2149.5632
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | ctrl | 2020 | 76.3095
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | ctrl | 2025 | 72.0104
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | ctrl | 2030 | 67.7112
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | ctrl | 2040 | 64.4869
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | ctrl | 2050 | 61.2626
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | lower | 2025 | 60.8538
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | lower | 2050 | 53.7391
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | upper | 2025 | 101.4231
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  | 27,28 | upper | 2050 | 107.4782
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | ctrl | 2020 | 53.4166
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | ctrl | 2025 | 50.4073
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | ctrl | 2030 | 47.3979
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | ctrl | 2040 | 45.1408
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | ctrl | 2050 | 42.8838
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | lower | 2025 | 42.5977
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | lower | 2050 | 26.8695
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | upper | 2025 | 70.9961
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | J | 27 | upper | 2050 | 91.3564
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | ctrl | 2020 | 22.8928
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | ctrl | 2025 | 21.6031
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | ctrl | 2030 | 20.3134
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | ctrl | 2040 | 19.3461
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | ctrl | 2050 | 18.3788
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | lower | 2025 | 18.2561
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | lower | 2050 | 8.0609
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | upper | 2025 | 30.4269
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | AB | 27 | upper | 2050 | 53.7391
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
207 HP ventilation,new apart | Heat pump, ventilation - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2020 | 0.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2025 | 0.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2030 | 0.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2040 | 0.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2050 | 0.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2025 | 0.2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2050 | 0.2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2025 | 0.3
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2050 | 0.3
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2020 | 2.15
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2025 | 2.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2030 | 2.3
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2040 | 2.35
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2050 | 2.4
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2025 | 2.05
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2050 | 2.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2025 | 2.45
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2050 | 2.65
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2020 | 5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2025 | 5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2030 | 5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2040 | 5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2050 | 5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | lower | 2025 | 3
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | lower | 2050 | 3
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | upper | 2025 | 9
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | upper | 2050 | 9
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | ctrl | 2020 | 18
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | ctrl | 2025 | 18
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | ctrl | 2030 | 18
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | ctrl | 2040 | 18
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | ctrl | 2050 | 18
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | lower | 2025 | 14
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | lower | 2050 | 14
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | upper | 2025 | 20
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | F |  | upper | 2050 | 20
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 20.4
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 20.4
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 20.4
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 20.4
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 20.4
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 15
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 15
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 0.5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.43
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.43
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.43
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.43
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.43
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 375.8389
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 271.0663
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 266.9648
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 259.3536
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 251.7423
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 205.5928
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 230.0883
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 328.3556
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 273.3963
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2020 | 375.8389
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2025 | 271.0663
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2030 | 266.9648
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2040 | 259.3536
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2050 | 251.7423
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | lower | 2025 | 205.5928
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | lower | 2050 | 230.0883
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | upper | 2025 | 328.3556
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | upper | 2050 | 273.3963
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2020 | 11.2752
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2025 | 10.4385
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2030 | 9.6018
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2040 | 8.871
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2050 | 8.1402
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2025 | 8.3508
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2050 | 6.5122
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2025 | 13.57
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2050 | 10.5822
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 2
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2020 | 6.706
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2025 | 6.4405
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2030 | 6.175
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2040 | 5.8725
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2050 | 5.5701
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2025 | 5.1524
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2050 | 4.456
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2025 | 8.3727
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2050 | 7.2411
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2020 | 4.5691
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2025 | 3.998
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2030 | 3.4268
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2040 | 2.9985
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2050 | 2.5701
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2025 | 3.1984
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2050 | 2.0561
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2025 | 5.1974
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2050 | 3.3412
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2020 | 0.913
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2025 | 0.913
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2030 | 0.92241
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2040 | 0.93182
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2050 | 0.93182
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2025 | 0.89418
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2050 | 0.92241
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2025 | 0.94124
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2050 | 0.96006
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2020 | 4.5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2025 | 4.75
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2030 | 4.9
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2040 | 5.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2050 | 5.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | lower | 2025 | 3.6
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | lower | 2050 | 4.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | upper | 2025 | 5.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | upper | 2050 | 5.85
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2020 | 3.35
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2025 | 3.55
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2030 | 3.75
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2040 | 3.95
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2050 | 4.05
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | lower | 2025 | 3
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | lower | 2050 | 3.55
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | upper | 2025 | 4.1
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | upper | 2050 | 4.85
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2020 | 2.5
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2025 | 2.55
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2030 | 2.65
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2040 | 2.7
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2050 | 2.7
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2025 | 2.25
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2050 | 2.45
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2025 | 2.75
208 HP hybrid,ex single | Heat pump, gas-hybrid - single-family house - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2050 | 2.9
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2020 | 0.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2025 | 0.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2030 | 0.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2040 | 0.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2050 | 0.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2025 | 0.2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2050 | 0.2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2025 | 0.3
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2050 | 0.3
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2020 | 600
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2025 | 550
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2030 | 500
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2040 | 450
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2050 | 400
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2025 | 400
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2050 | 250
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2025 | 1000
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2050 | 800
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2020 | 2.15
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2025 | 2.2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2030 | 2.3
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2040 | 2.35
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2050 | 2.45
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2025 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2050 | 2.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2025 | 2.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2050 | 2.65
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2020 | 160
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2025 | 160
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2030 | 160
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2040 | 160
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2050 | 160
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | lower | 2025 | 150
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | lower | 2050 | 150
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | upper | 2025 | 250
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | upper | 2050 | 250
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 20.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 20.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 20.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 20.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 20.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 15
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 15
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 0.5
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.43
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.43
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.43
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.43
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.43
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 3743.0723
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 3720.5821
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 3696.3919
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 3643.2355
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 3589.1791
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 3540.8247
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 3424.4321
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 3925.7395
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 3783.2261
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 41.4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 46.8
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 50.5
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 49.1
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 46.8
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 34
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 29.3
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 85
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 93.6
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 3701.6723
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 3673.7821
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 3645.8919
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 3594.1355
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 3542.3791
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 3506.8247
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 3395.1321
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 3840.7395
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 3689.6261
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2020 | 193.2886
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2025 | 177.1347
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2030 | 160.9807
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2040 | 147.5275
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2050 | 134.0743
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2025 | 141.7077
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2050 | 107.2594
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2025 | 230.2751
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2050 | 174.2965
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 2
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2020 | 147.1141
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2025 | 136.732
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2030 | 126.3499
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2040 | 117.2255
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2050 | 108.1011
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2025 | 109.3856
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2050 | 86.4809
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2025 | 177.7516
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2050 | 140.5314
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2020 | 46.1745
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2025 | 40.4027
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2030 | 34.6309
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2040 | 30.302
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2050 | 25.9732
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2025 | 32.3221
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2050 | 20.7785
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2025 | 52.5235
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2050 | 33.7651
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2020 | 0.913
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2025 | 0.913
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2030 | 0.92204
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2040 | 0.92204
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2050 | 0.92204
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2025 | 0.89492
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2050 | 0.90396
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2025 | 0.93108
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2050 | 0.94012
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2020 | 4.45
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2025 | 4.65
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2030 | 4.8
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2040 | 5.05
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2050 | 5.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | lower | 2025 | 3.6
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | lower | 2050 | 4.3
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | upper | 2025 | 5.35
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | upper | 2050 | 5.95
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2020 | 3.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2025 | 3.45
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2030 | 3.7
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2040 | 3.9
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2050 | 4.15
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | lower | 2025 | 2.85
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | lower | 2050 | 3.55
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | upper | 2025 | 4
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | upper | 2050 | 4.9
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2020 | 2.5
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2025 | 2.55
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2030 | 2.6
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2040 | 2.65
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2050 | 2.7
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2025 | 2.25
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2050 | 2.45
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2025 | 2.75
208 HP hybrid,ex apart | Heat pump, gas-hybrid - apartment complex - existing building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2050 | 2.85
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2020 | 0.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2025 | 0.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2030 | 0.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2040 | 0.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2050 | 0.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2025 | 0.2
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2050 | 0.2
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2025 | 0.3
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2050 | 0.3
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2020 | 2.15
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2025 | 2.2
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2030 | 2.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2040 | 2.35
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2050 | 2.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2025 | 1.95
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2050 | 2.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2025 | 2.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2050 | 2.65
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2020 | 4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2025 | 4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2030 | 4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2040 | 4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | ctrl | 2050 | 4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | lower | 2025 | 3
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | lower | 2050 | 3
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | upper | 2025 | 8
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I | 1 | upper | 2050 | 6
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | ctrl | 2020 | 18
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | ctrl | 2025 | 18
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | ctrl | 2030 | 18
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | ctrl | 2040 | 18
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | ctrl | 2050 | 18
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | lower | 2025 | 14
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | lower | 2050 | 14
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | upper | 2025 | 20
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | P |  | upper | 2050 | 20
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 20.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 20.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 20.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 20.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 20.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 15
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 15
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 0.5
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.43
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.43
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.43
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.43
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.43
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 358.1755
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 253.4028
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 249.3013
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 241.6901
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 234.0789
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 187.9293
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 212.4249
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 310.6921
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 255.7328
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2020 | 358.1755
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2025 | 253.4028
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2030 | 249.3013
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2040 | 241.6901
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | ctrl | 2050 | 234.0789
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | lower | 2025 | 187.9293
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | lower | 2050 | 212.4249
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | upper | 2025 | 310.6921
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | B, C, E | 1 | upper | 2050 | 255.7328
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2020 | 7.302
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2025 | 6.953
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2030 | 6.604
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2040 | 6.2344
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2050 | 5.8649
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2025 | 5.551
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2050 | 4.6919
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2025 | 9.043
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2050 | 7.6243
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2020 | 5.1544
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2025 | 4.9664
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2030 | 4.7785
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2040 | 4.5458
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2050 | 4.3132
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2025 | 3.6886
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2050 | 3.4506
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2025 | 6.5598
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2050 | 5.6072
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2020 | 2.1477
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2025 | 1.9866
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2030 | 1.8255
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2040 | 1.6886
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2050 | 1.5517
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2025 | 1.8624
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2050 | 1.2413
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2025 | 2.4832
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2050 | 2.0172
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2020 | 0.913
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2025 | 0.913
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2030 | 0.92241
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2040 | 0.93182
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2050 | 0.93182
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2025 | 0.89418
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2050 | 0.92241
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2025 | 0.94124
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2050 | 0.96006
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2020 | 4.3
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2025 | 4.55
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2030 | 4.8
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2040 | 4.95
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2050 | 5.1
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | lower | 2025 | 3.6
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | lower | 2050 | 4.3
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | upper | 2025 | 4.9
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5,6,7,8,9,10,11 | upper | 2050 | 5.9
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2020 | 3.2
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2025 | 3.4
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2030 | 3.6
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2040 | 3.8
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | ctrl | 2050 | 3.95
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | lower | 2025 | 2.81
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | lower | 2050 | 3.45
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | upper | 2025 | 3.85
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5,6,7,8,9,10,11 | upper | 2050 | 4.7
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2020 | 2.45
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2025 | 2.5
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2030 | 2.6
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2040 | 2.65
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2050 | 2.7
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2025 | 2.25
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2050 | 2.45
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2025 | 2.65
208 HP hybrid,new single | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2050 | 2.9
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2020 | 0.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2025 | 0.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2030 | 0.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2040 | 0.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | ctrl | 2050 | 0.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2025 | 0.2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | lower | 2050 | 0.2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2025 | 0.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  | W |  | upper | 2050 | 0.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2020 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2030 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2040 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | ctrl | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | lower | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  | M |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2020 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2030 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2040 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | ctrl | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  | M |  | upper | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2020 | 350
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2025 | 325
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2030 | 300
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2040 | 250
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | ctrl | 2050 | 250
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2025 | 250
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | lower | 2050 | 200
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2025 | 500
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  | V | 2 | upper | 2050 | 400
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | lower | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | A |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2020 | 2.15
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2025 | 2.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2030 | 2.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2040 | 2.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | ctrl | 2050 | 2.45
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2025 | 1.95
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | lower | 2050 | 2.2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2025 | 2.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | N, O |  | upper | 2050 | 2.75
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2020 | 160
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2025 | 160
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2030 | 160
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2040 | 160
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | ctrl | 2050 | 160
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | lower | 2025 | 140
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | lower | 2050 | 140
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | upper | 2025 | 200
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | I, L | 1 | upper | 2050 | 200
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 20
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 20
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 20
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 20
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 20
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 15
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 15
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | N2O [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 20.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 20.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 20.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 20.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 20.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 15
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 15
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | NOX [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 0.5
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | PM2.5 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2020 | 0.43
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2025 | 0.43
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2030 | 0.43
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2040 | 0.43
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | ctrl | 2050 | 0.43
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2025 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Environment | SO2 [g/GJ_i] | g/GJ_i |  | G,H |  | upper | 2050 | 1
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 2371.8311
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 2348.4566
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 2324.382
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 2271.6958
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 2224.0097
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 2181.8774
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 2076.7526
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 2523.6357
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 2382.8668
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2020 | 24.2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2025 | 27.6
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2030 | 30.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2040 | 27.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | ctrl | 2050 | 29.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2025 | 21.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | lower | 2050 | 23.4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2025 | 42.5
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | J |  | upper | 2050 | 46.8
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 2347.6311
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 2320.8566
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 2294.082
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 2244.3958
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 2194.7097
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 2160.5774
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 2053.3526
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 2481.1357
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 2336.0668
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2020 | 107.3826
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2025 | 98.2085
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2030 | 89.0344
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2040 | 81.3799
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | ctrl | 2050 | 73.7253
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2025 | 68.7459
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | lower | 2050 | 58.9802
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2025 | 127.671
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D | 1 | upper | 2050 | 95.8428
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2020 | 71.9463
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2025 | 67.2018
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2030 | 62.4573
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2040 | 58.1248
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | ctrl | 2050 | 53.7924
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2025 | 47.0412
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | lower | 2050 | 43.0339
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2025 | 87.3623
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 | D, Y | 1 | upper | 2050 | 69.9301
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2020 | 35.4362
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2025 | 31.0067
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2030 | 26.5772
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2040 | 23.255
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | ctrl | 2050 | 19.9329
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2025 | 21.7047
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | lower | 2050 | 15.9463
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2025 | 40.3087
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D, X | 1 | upper | 2050 | 25.9128
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/MWh_h, 2020] | EUR/MWh_h, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2020 | 0.913
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2025 | 0.913
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2030 | 0.92204
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2040 | 0.92204
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | ctrl | 2050 | 0.92204
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2025 | 0.89492
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | lower | 2050 | 0.90396
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2025 | 0.93108
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, gas boiler heating) [p.u.] | p.u. |  | R | 4 | upper | 2050 | 0.94012
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2020 | 4.55
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2025 | 4.85
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2030 | 5.15
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2040 | 5.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | ctrl | 2050 | 5.5
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | lower | 2025 | 3.7
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | lower | 2050 | 4.45
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | upper | 2025 | 5.3
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | p.u. |  | Q, P, U, S, T | 5, 6, 12, 13 | upper | 2050 | 6.55
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2020 | 3.35
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2025 | 3.5
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2030 | 3.7
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2040 | 4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | ctrl | 2050 | 4.2
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | lower | 2025 | 2.75
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | lower | 2050 | 3.5
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | upper | 2025 | 4
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | p.u. |  | Q, U, S, T | 5, 6, 12, 13 | upper | 2050 | 5.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2020 | 2.55
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2025 | 2.6
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2030 | 2.65
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2040 | 2.7
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | ctrl | 2050 | 2.75
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2025 | 2.25
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | lower | 2050 | 2.5
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2025 | 2.75
208 HP hybrid,new apart | Heat pump, gas-hybrid - single-family house - new building | Technology specific data | Heat efficiency (annual average, net, total system, floor heating) [p.u.] | p.u. |  | P, N |  | upper | 2050 | 3
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 50
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 50
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 50
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 50
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 50
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 25
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 25
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 75
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 75
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0.65
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0.65
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0.65
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0.65
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0.65
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0.4
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0.4
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0.7
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0.7
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0.1
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0.1
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0.1
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0.1
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0.1
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0.15
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0.15
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2020 | 4.2
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2025 | 4.2
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2030 | 4.2
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2040 | 4.2
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2050 | 4.2
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2025 | 3
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2050 | 3
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2025 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2050 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2020 | 25
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2025 | 25
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2030 | 30
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2040 | 30
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2050 | 30
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2025 | 20
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2050 | 20
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2025 | 30
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2050 | 30
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2020 | 52.45
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2025 | 49.25
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2030 | 48.05
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2040 | 45.45
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2050 | 42.85
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | lower | 2025 | 43.575
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | lower | 2050 | 38.425
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | upper | 2025 | 60.775
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | upper | 2050 | 54.775
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2020 | 3.45
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2025 | 4.25
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2030 | 5.05
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2040 | 5.45
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2050 | 5.85
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2025 | 2.125
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2050 | 2.925
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2025 | 6.375
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2050 | 8.775
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 49
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 45
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 43
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 40
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 37
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 41.45
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 35.5
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 54.4
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 46
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | ctrl | 2020 | 4.14
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | ctrl | 2025 | 4.0375
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | ctrl | 2030 | 3.9376
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | ctrl | 2040 | 3.7451
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | ctrl | 2050 | 3.562
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | lower | 2025 | 3.4319
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | lower | 2050 | 3.0277
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | upper | 2025 | 4.845
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K, H |  | upper | 2050 | 4.2744
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 2.898
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 2.8263
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 2.7563
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 2.6216
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 2.4934
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 2.4023
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 2.1194
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 3.3915
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 2.9921
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2020 | 1.242
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2025 | 1.2113
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2030 | 1.1813
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2040 | 1.1235
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2050 | 1.0686
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | lower | 2025 | 1.0296
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | lower | 2050 | 0.90831
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | upper | 2025 | 1.4535
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | upper | 2050 | 1.2823
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2020 | 425
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2025 | 435
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2030 | 445
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2040 | 465
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2050 | 485
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | lower | 2025 | 425
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | lower | 2050 | 430
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | upper | 2025 | 445
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | upper | 2050 | 500
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2020 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2025 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2030 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2040 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2050 | 6
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2025 | 4
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2050 | 4
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2025 | 8
215 Solar heating,ex single | Solar heating system - single-family house - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2050 | 8
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 3000
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 2800
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 2500
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 2250
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 2000
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 2000
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 1500
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 4000
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 3000
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0.65
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0.65
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0.65
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0.65
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0.65
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0.4
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0.4
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0.7
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0.7
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2020 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2025 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2030 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2040 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2050 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2025 | 100
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2050 | 100
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2025 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2050 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2020 | 20
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2025 | 25
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2030 | 30
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2040 | 30
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2050 | 30
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2025 | 20
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2050 | 25
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2025 | 30
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2050 | 35
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2020 | 417
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2025 | 442
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2030 | 451.5
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2040 | 439.25
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2050 | 417
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | lower | 2025 | 310
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | lower | 2050 | 261.5
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | upper | 2025 | 609
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | upper | 2050 | 566
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 207
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 238
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 252.5
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 245.25
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 234
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 170
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 175.5
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 340
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 351
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2020 | 210
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2025 | 204
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2030 | 199
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2040 | 194
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | ctrl | 2050 | 183
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2025 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | lower | 2050 | 86
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2025 | 269
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 | F |  | upper | 2050 | 215
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 81
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 77.5
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 74
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 70.5
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 67
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 65.875
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 56.95
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 93
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 80.4
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 52.65
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 50.375
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 48.1
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 45.825
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 43.55
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 42.8188
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 37.0175
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 60.45
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 52.26
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2020 | 28.35
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2025 | 27.125
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2030 | 25.9
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2040 | 24.675
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2050 | 23.45
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | lower | 2025 | 23.0562
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | lower | 2050 | 19.9325
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | upper | 2025 | 32.55
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | upper | 2050 | 28.14
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | ctrl | 2020 | 425
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | ctrl | 2025 | 435
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | ctrl | 2030 | 450
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | ctrl | 2040 | 475
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | ctrl | 2050 | 500
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | lower | 2025 | 300
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | lower | 2050 | 400
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | upper | 2025 | 450
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  |  | 1 | upper | 2050 | 550
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2020 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2025 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2030 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2040 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2050 | 200
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2025 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2050 | 140
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2025 | 290
215 Solar heating,ex apart | Solar heating system - apartment complex - existing building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2050 | 290
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 50
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 50
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 50
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 50
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 50
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 25
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 25
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 75
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 75
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0.65
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0.65
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0.65
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0.65
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0.65
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0.4
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0.4
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0.7
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0.7
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2020 | 4.2
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2025 | 4.2
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2030 | 4.2
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2040 | 4.2
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2050 | 4.2
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2025 | 3
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2050 | 3
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2025 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2050 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2020 | 25
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2025 | 25
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2030 | 30
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2040 | 30
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2050 | 30
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2025 | 20
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2050 | 20
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2025 | 30
215 Solar heating,new single | Solar heating system - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2050 | 30
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 66.45
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 65.25
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 65.05
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 62.45
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 59.85
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 45.125
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 34.925
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 92.375
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 83.775
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 3.45
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 4.25
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 5.05
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 5.45
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 5.85
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 2.125
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 2.925
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 6.375
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 8.775
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 63
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 61
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 60
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 57
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 54
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 43
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 32
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 86
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 75
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 2.4
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 2.25
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 2.1
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 2
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 1.9
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 1.9125
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 1.615
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 2.7
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 2.4
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.56
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.4625
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.365
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.3
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.235
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.2431
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.0497
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 1.755
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.56
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2020 | 0.84
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2025 | 0.7875
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2030 | 0.735
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2040 | 0.7
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | ctrl | 2050 | 0.665
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | lower | 2025 | 0.66937
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | lower | 2050 | 0.56525
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | upper | 2025 | 0.945
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 | D |  | upper | 2050 | 0.84
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2020 | 425
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2025 | 435
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2030 | 445
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2040 | 465
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2050 | 485
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | lower | 2025 | 425
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | lower | 2050 | 430
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | upper | 2025 | 445
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | upper | 2050 | 500
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2020 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2025 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2030 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2040 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2050 | 6
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2025 | 4
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2050 | 4
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2025 | 8
215 Solar heating,new single | Solar heating system - single-family house - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2050 | 8
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 3000
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 2800
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 2500
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 2250
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 2000
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 2000
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 1500
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 4000
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 3000
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0.65
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0.65
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0.65
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0.65
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0.65
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0.4
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0.4
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0.7
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 70
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2020 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2030 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2040 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | ctrl | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | lower | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  | B, I | 1 | upper | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2020 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2025 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2030 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2040 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | ctrl | 2050 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2025 | 100
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | lower | 2050 | 100
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2025 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | A, I | 1 | upper | 2050 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2020 | 20
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2025 | 25
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2030 | 30
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2040 | 30
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | ctrl | 2050 | 30
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2025 | 20
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | lower | 2050 | 25
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2025 | 30
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  | C | 1 | upper | 2050 | 35
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2020 | 414
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2025 | 480
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2030 | 524.5
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2040 | 503.25
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | ctrl | 2050 | 486
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | lower | 2025 | 318
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | lower | 2050 | 364.5
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | upper | 2025 | 637
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | E, H |  | upper | 2050 | 728
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 207
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 238
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 252.5
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 245.25
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 234
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 170
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 175.5
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 340
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 351
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 207
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 242
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 272
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 258
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 252
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 148
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 189
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 297
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 377
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2020 | 81
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2025 | 77.5
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2030 | 74
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2040 | 70.5
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | ctrl | 2050 | 67
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2025 | 65.875
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | lower | 2050 | 56.95
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2025 | 93
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | K |  | upper | 2050 | 80.4
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 52.65
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 50.375
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 48.1
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 45.825
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 43.55
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 42.8188
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 37.0175
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 60.45
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 52.26
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 28.35
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 27.125
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 25.9
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 24.675
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 23.45
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 23.0562
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 19.9325
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 32.55
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 28.14
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2020 | 425
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2025 | 435
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2030 | 450
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2040 | 475
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | ctrl | 2050 | 500
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | lower | 2025 | 300
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | lower | 2050 | 400
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | upper | 2025 | 450
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Performance (output per collector area) [kWh/m2/y] | kWh/m2/y |  | J | 1 | upper | 2050 | 550
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2020 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2025 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2030 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2040 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | ctrl | 2050 | 200
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2025 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | lower | 2050 | 140
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2025 | 290
215 Solar heating,new apart | Solar heating system - apartment complex - new building | Technology specific data | Solar collector area [m2] | m2 |  | I | 1, 6 | upper | 2050 | 290
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 100
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 100
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | lower | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | lower | 2050 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | upper | 2025 | 1
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | upper | 2050 | 100
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2020 | 3
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2025 | 3
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2030 | 3
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2040 | 3
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | ctrl | 2050 | 3
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2025 | 2
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | lower | 2050 | 2
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2025 | 7
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  |  |  | upper | 2050 | 7
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 25
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 25
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 30
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Environment | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2020 | 24
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2025 | 24
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2030 | 23
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2040 | 22
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2050 | 21
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | lower | 2025 | 20.4
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | lower | 2050 | 17.85
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | upper | 2025 | 28.8
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | upper | 2050 | 25.2
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 24
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 24
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 23
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 22
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 21
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 20.4
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 17.85
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 28.8
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 25.2
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2020 | 2.691
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2025 | 2.6244
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2030 | 2.5594
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2040 | 2.4343
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2050 | 2.3153
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | lower | 2025 | 2.2307
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | lower | 2050 | 1.968
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | upper | 2025 | 3.1493
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | upper | 2050 | 2.7784
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 1.8837
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 1.8371
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 1.7916
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 1.704
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 1.6207
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 1.5615
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 1.3776
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 2.2045
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 1.9448
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0.8073
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0.78732
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0.76783
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0.73029
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0.69459
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0.66922
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0.5904
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0.94478
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0.83351
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
216 Electric heating,new single | Electric heating - single-family house - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Minimum load (of full load) [p.u.] | p.u. |  |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Primary regulation (per 30 seconds) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Secondary regulation (per minute) [p.u.] | p.u. |  |  |  | upper | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Electric regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Auxiliary Electricity consumption [kWh_e/y] | kWh_e/y |  |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of hot tap water demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2020 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2030 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2040 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | ctrl | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | lower | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Expected share of space heating demand covered by unit [p.u.] | p.u. |  |  |  | upper | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2020 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2030 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2040 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | ctrl | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | lower | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | lower | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | upper | 2025 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat efficiency (annual average, net) [p.u.] | p.u. |  | A |  | upper | 2050 | 1
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | ctrl | 2020 | 160
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | ctrl | 2025 | 160
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | ctrl | 2030 | 160
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | ctrl | 2040 | 160
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | ctrl | 2050 | 160
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | lower | 2025 | 100
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | lower | 2050 | 100
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | upper | 2025 | 250
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Heat production capacity for one unit [kW_h] | kW_h |  | B |  | upper | 2050 | 250
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2020 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2025 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2030 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2040 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | ctrl | 2050 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2025 | 25
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | lower | 2050 | 25
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2025 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Energy/technical data | Technical economic lifetime [years] | years |  |  |  | upper | 2050 | 30
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Environment | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Annual O&M (time spent on manual maintenance) [hours/unit/y] | hours/unit/y |  |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2020 | 49
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2025 | 47
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2030 | 46
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2040 | 44
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | ctrl | 2050 | 42
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | lower | 2025 | 39.95
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | lower | 2050 | 35.7
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | upper | 2025 | 56.4
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (*total) [€/unit/y, 2020] | EUR/unit/y, | 2020 | C, E |  | upper | 2050 | 50.4
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (electricity cost) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2020 | 49
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2025 | 47
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2030 | 46
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2040 | 44
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | ctrl | 2050 | 42
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2025 | 39.95
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | lower | 2050 | 35.7
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2025 | 56.4
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Fixed O&M (other) [€/unit/y, 2020] | EUR/unit/y, | 2020 |  |  | upper | 2050 | 50.4
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2020 | 109.71
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2025 | 106.9945
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2030 | 104.3463
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2040 | 99.2448
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | ctrl | 2050 | 94.3927
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | lower | 2025 | 90.9454
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | lower | 2050 | 80.2338
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | upper | 2025 | 128.3934
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (*total) [k€/unit, 2020] | kEUR/unit, | 2020 | D, E, F | 4, 5 | upper | 2050 | 113.2713
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (additional) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 76.797
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 74.8962
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 73.0424
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 69.4714
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 66.0749
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 63.6618
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 56.1637
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 89.8754
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (equipment) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 79.2899
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2020 | 32.913
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2025 | 32.0984
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2030 | 31.3039
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2040 | 29.7734
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | ctrl | 2050 | 28.3178
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2025 | 27.2836
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | lower | 2050 | 24.0702
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2025 | 38.518
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Nominal investment (installation) [k€/unit, 2020] | kEUR/unit, | 2020 |  |  | upper | 2050 | 33.9814
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2020 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2030 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2040 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | ctrl | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | lower | 2050 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2025 | 0
216 Electric heating,new apart | Electric heating - apartment complex - new building | Financial data | Variable O&M (*total) [€/kWh, 2020] | EUR/kWh, | 2020 |  |  | upper | 2050 | 0

## Notes
ws | description
201 Oil boiler, ex single | 14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
201 Oil boiler, ex single | A. The minimum heat output for a pressure atomisation burner is in the range of 13 kW. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity below 13 kW is limited or non-existing. Hence, the investme...
201 Oil boiler, ex single | B. Domestic fuel oil can be desulphoried to the lower than 10 ppm Sulpur
201 Oil boiler, ex single | C. The last limit for Nox for Blaue Engel were 110 mg/kWh. The value is based on this. In Practise the value can be lower. In 2050 is assumed flue gas cleaning for Nox
201 Oil boiler, ex single | E. Data for emissions can be found at emission inventories envs.au.dk
201 Oil boiler, ex single | F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
201 Oil boiler, ex single | G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons. In the case HVO becomes feasible condensing technology will work well
201 Oil boiler, ex single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
201 Oil boiler, ex single | J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
201 Oil boiler, ex single | M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
201 Oil boiler, ex single | N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]
201 Oil boiler, new single | 14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
201 Oil boiler, new single | A. The minimum heat output for a pressure atomisation burner is in the range of 13 kW. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity below 13 kW is limited or non-existing. Hence, the investme...
201 Oil boiler, new single | E. Data for emissions can be found at emission inventories envs.au.dk
201 Oil boiler, new single | F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
201 Oil boiler, new single | G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons.
201 Oil boiler, new single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
201 Oil boiler, new single | J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
201 Oil boiler, new single | M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
201 Oil boiler, new single | N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]
201 Oil boiler, new apart | 14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
201 Oil boiler, new apart | E. Data for emissions can be found at emission inventories envs.au.dk
201 Oil boiler, new apart | F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
201 Oil boiler, new apart | G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons.
201 Oil boiler, new apart | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
201 Oil boiler, new apart | J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
201 Oil boiler, new apart | M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
201 Oil boiler, new apart | N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]
201 Oil boiler, new apart | O. Investment cost for 2020 have been estimated based on a survey of publicly offered prices and interviews with installers. Data has been collected during October and November 2020.
202 Gas boiler, ex single | 31. Danish District Heating Association, information given to the 2012 survey for the report
202 Gas boiler, ex single | A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1] and observed efficiences for condensing boilers according to [4]. Efficiencies of the condensing gas boiler is approx. 99 % but when accounting for heat losses from the hot water ta...
202 Gas boiler, ex single | B. A slight improvement of efficiency is still possible over the next decades is assumed
202 Gas boiler, ex single | C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
202 Gas boiler, ex single | D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
202 Gas boiler, ex single | F. Ref [5] gives 5 mg/kWh, This is less than 2 g/GJ.
202 Gas boiler, ex single | G. Data for emissions can be found at emission inventories envs.au.dk
202 Gas boiler, ex single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies. The harmonisation of gas quality in EU, the more severe competition with district heating and electrical heat pumps, and the improvements in the manufacturing cost ar...
202 Gas boiler, ex single | J. This assumes a service agreement costing 127 €/a excluding VAT and approx. 55 €/a on average for spare parts .
202 Gas boiler, ex single | K. Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the...
202 Gas boiler, ex single | L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
202 Gas boiler, ex single | M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
202 Gas boiler, ex single | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
202 Gas boiler, ex single | U. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity of the boilers is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
202 Gas boiler, ex single | V. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
202 Gas boiler, ex apart | 31. Danish District Heating Association, information given to the 2012 survey for the report
202 Gas boiler, ex apart | A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
202 Gas boiler, ex apart | B. A slight improvement of efficiency is still possible over the next decades is assumed
202 Gas boiler, ex apart | C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
202 Gas boiler, ex apart | D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
202 Gas boiler, ex apart | G. Data for emissions can be found at emission inventories envs.au.dk
202 Gas boiler, ex apart | L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
202 Gas boiler, ex apart | M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
202 Gas boiler, ex apart | N. The emissions are assumed to be very similar to the ones for domestic boilers. This is believed to be a conservative estimate.
202 Gas boiler, ex apart | O. Based on a 160 kW boiler (new building) and 400 kW (existing building)
202 Gas boiler, ex apart | Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
202 Gas boiler, ex apart | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
202 Gas boiler, ex apart | U. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity of the boilers is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
202 Gas boiler, new single | 33. Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
202 Gas boiler, new single | A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
202 Gas boiler, new single | B. A slight improvement of efficiency is still possible over the next decades is assumed
202 Gas boiler, new single | C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
202 Gas boiler, new single | D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
202 Gas boiler, new single | E. NOx emission will decrease as an average. The level proposed for 2030 is already achievable today by some gas boilers.
202 Gas boiler, new single | F. Ref [5] gives 5 mg/kWh, This is less than 2 g/GJ.
202 Gas boiler, new single | G. Data for emissions can be found at emission inventories envs.au.dk
202 Gas boiler, new single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies. The harmonisation of gas quality in EU, the more severe competition with district heating and electrical heat pumps, and the improvements in the manufacturing cost ar...
202 Gas boiler, new single | J. This assumes a service agreement costing 127 €/a excluding VAT and approx. 55 €/a on average for spare parts .
202 Gas boiler, new single | L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
202 Gas boiler, new single | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
202 Gas boiler, new single | V. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
202 Gas boiler, new apart | 33. Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
202 Gas boiler, new apart | A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
202 Gas boiler, new apart | B. A slight improvement of efficiency is still possible over the next decades is assumed
202 Gas boiler, new apart | C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
202 Gas boiler, new apart | D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
202 Gas boiler, new apart | E. NOx emission will decrease as an average. The level proposed for 2030 is already achievable today by some gas boilers.
202 Gas boiler, new apart | K. Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the...
202 Gas boiler, new apart | L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
202 Gas boiler, new apart | M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
202 Gas boiler, new apart | N. The emissions are assumed to be very similar to the ones for domestic boilers. This is believed to be a conservative estimate.
202 Gas boiler, new apart | O. Based on a 160 kW boiler (new building) and 400 kW (existing building)
202 Gas boiler, new apart | P. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
202 Gas boiler, new apart | Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
202 Gas boiler, new apart | S. Service cost interpolated from manufacturers information (2020)
202 Gas boiler, new apart | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH indirect,new single | 10. Interview with market actors and web price survey, 2020
203 DH indirect,new single | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH indirect,new single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH indirect,new single | D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
203 DH indirect,new single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH indirect,new single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH indirect,new single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH indirect,new single | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH indirect,new single | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH indirect,new single | C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH indirect,new single | D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
203 DH indirect,ex single | 10. Interview with market actors and web price survey, 2020
203 DH indirect,ex single | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH indirect,ex single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH indirect,ex single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH indirect,ex single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH indirect,ex single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH indirect,ex single | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH indirect,ex single | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH indirect,ex single | M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
203 DH indirect,ex single | N. The emissions are assumed to be very similar to the ones for domestic boilers. This is believed to be a conservative estimate.
203 DH indirect,ex single | O. Based on a 160 kW boiler (new building) and 400 kW (existing building)
203 DH indirect,ex single | P. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
203 DH indirect,ex single | Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
203 DH indirect,ex single | S. Service cost interpolated from manufacturers information (2020)
203 DH indirect,ex single | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH indirect,ex apart | 10. Interview with market actors and web price survey, 2020
203 DH indirect,ex apart | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH indirect,ex apart | 10. Interview with market actors and web price survey, 2020
203 DH indirect,ex apart | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
203 DH indirect,ex apart | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH indirect,ex apart | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH indirect,ex apart | D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
203 DH indirect,ex apart | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH indirect,ex apart | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH indirect,ex apart | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH indirect,ex apart | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH indirect,ex apart | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH indirect,new apart | 10. Interview with market actors and web price survey, 2020
203 DH indirect,new apart | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH indirect,new apart | 10. Interview with market actors and web price survey, 2020
203 DH indirect,new apart | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
203 DH indirect,new apart | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH indirect,new apart | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH indirect,new apart | D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
203 DH indirect,new apart | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH indirect,new apart | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH indirect,new apart | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH indirect,new apart | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH indirect,new apart | P. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
203 DH indirect,new apart | Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
203 DH indirect,new apart | S. Service cost interpolated from manufacturers information (2020)
203 DH indirect,new apart | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,new single | 10. Interview with market actors and web price survey, 2020. The stated cost represent a situation with competitive pricing.
203 DH direct,new single | B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a...
203 DH direct,new single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH direct,new single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH direct,new single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,new single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,new single | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH direct,new single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH direct,new single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,new single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,new single | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH direct,new single | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,ex single | 10. Interview with market actors and web price survey, 2020. The stated cost represent a situation with competitive pricing.
203 DH direct,ex single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH direct,ex single | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
203 DH direct,ex single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH direct,ex single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,ex single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,ex single | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH direct,ex single | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,ex single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,ex single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,ex single | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,ex single | P. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
203 DH direct,ex single | Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
203 DH direct,ex single | S. Service cost interpolated from manufacturers information (2020)
203 DH direct,ex single | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,ex apart | 10. Interview with market actors and web price survey, 2020
203 DH direct,ex apart | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
203 DH direct,ex apart | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH direct,ex apart | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
203 DH direct,ex apart | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH direct,ex apart | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,ex apart | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,ex apart | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,ex apart | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,ex apart | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,ex apart | H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substati...
203 DH direct,ex apart | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,new apart | 10. Interview with market actors and web price survey, 2020
203 DH direct,new apart | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
203 DH direct,new apart | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
203 DH direct,new apart | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
203 DH direct,new apart | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
203 DH direct,new apart | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,new apart | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,new apart | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,new apart | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
203 DH direct,new apart | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
203 DH direct,new apart | I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.
203 DH direct,new apart | P. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
203 DH direct,new apart | Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
203 DH direct,new apart | S. Service cost interpolated from manufacturers information (2020)
203 DH direct,new apart | T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,ex single | 10. Interview with market actors and web price survey, 2020
204 Biomass auto,ex single | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
204 Biomass auto,ex single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
204 Biomass auto,ex single | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
204 Biomass auto,ex single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
204 Biomass auto,ex single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
204 Biomass auto,ex single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,ex single | 10. Estimate by Ea Energy Analyses, 2020
204 Biomass auto,ex single | A. Nominal heat delivered in 2020 from 10-20 kW in single family houses. In small units (20 kW and less) the insignificant economy of scale (se section on economy of scale) the savings achieved by reducing the capacity of the boiler is limited or non-existing. Hence, the investment cost is not in...
204 Biomass auto,ex single | B. Efficiency development from [2]
204 Biomass auto,ex single | C. EN303-5 measurement method
204 Biomass auto,ex single | D. Prerequisite: house with central heating system
204 Biomass auto,ex single | E. Chimney
204 Biomass auto,ex single | F. Large price span mainly due to finish, design, control features etc.
204 Biomass auto,ex single | G. Improved real life conditions for flue gas condensation technology will increase the efficiency to >100% (based on NCV)
204 Biomass auto,ex single | H. Fuel storage
204 Biomass auto,ex single | I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
204 Biomass auto,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,ex single | K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
204 Biomass auto,ex single | L. Including dismantling and disposal of existing boiler
204 Biomass auto,ex single | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
204 Biomass auto,ex single | N. For loading fuel manually from bags and removing ash
204 Biomass auto,new single | 10. Interview with market actors and web price survey, 2020
204 Biomass auto,new single | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
204 Biomass auto,new single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
204 Biomass auto,new single | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
204 Biomass auto,new single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
204 Biomass auto,new single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
204 Biomass auto,new single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,new single | 10. Estimate by Ea Energy Analyses, 2020
204 Biomass auto,new single | A. Nominal heat delivered in 2020 from 10-20 kW in single family houses. In small units (20 kW and less) the insignificant economy of scale (se section on economy of scale) the savings achieved by reducing the capacity of the boiler is limited or non-existing. Hence, the investment cost is not in...
204 Biomass auto,new single | B. Efficiency development from [2]
204 Biomass auto,new single | C. EN303-5 measurement method
204 Biomass auto,new single | G. Improved real life conditions for flue gas condensation technology will increase the efficiency to >100% (based on NCV)
204 Biomass auto,new single | H. Fuel storage
204 Biomass auto,new single | I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
204 Biomass auto,new single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,new single | K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
204 Biomass auto,new single | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
204 Biomass auto,new single | N. For loading fuel manually from bags and removing ash
204 Biomass auto,ex apart | 10. Interview with market actors and web price survey, 2020
204 Biomass auto,ex apart | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
204 Biomass auto,ex apart | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
204 Biomass auto,ex apart | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
204 Biomass auto,ex apart | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
204 Biomass auto,ex apart | 8. Interview with market actors and web price survey, 2020
204 Biomass auto,ex apart | A. Nominal heat delivered in 2020 from 100 – 500 kW unit or a cascade of smaller units in apartment complexes
204 Biomass auto,ex apart | B. Efficiency development from [5]
204 Biomass auto,ex apart | C. EN303-5 measurement method
204 Biomass auto,ex apart | D. Prerequisite: house with central heating system
204 Biomass auto,ex apart | E. Fuel storage
204 Biomass auto,ex apart | F. Contemporary value from [6]
204 Biomass auto,ex apart | I. The cost is based on a unit with a capacity of 200 kW and assuming the cost for this unit is equally split between an initial cost and a linear dependence on the capacity of the unit
204 Biomass auto,ex apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,ex apart | K. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
204 Biomass auto,ex apart | L. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
204 Biomass auto,ex apart | I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
204 Biomass auto,ex apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,ex apart | K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
204 Biomass auto,ex apart | L. Including dismantling and disposal of existing boiler
204 Biomass auto,ex apart | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
204 Biomass auto,ex apart | N. For loading fuel manually from bags and removing ash
204 Biomass auto,new apart | 10. Interview with market actors and web price survey, 2020
204 Biomass auto,new apart | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
204 Biomass auto,new apart | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
204 Biomass auto,new apart | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
204 Biomass auto,new apart | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
204 Biomass auto,new apart | 8. Interview with market actors and web price survey, 2020
204 Biomass auto,new apart | A. Nominal heat delivered in 2020 from 100 – 500 kW unit or a cascade of smaller units in apartment complexes
204 Biomass auto,new apart | B. Efficiency development from [5]
204 Biomass auto,new apart | C. EN303-5 measurement method
204 Biomass auto,new apart | E. Fuel storage
204 Biomass auto,new apart | F. Contemporary value from [6]
204 Biomass auto,new apart | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
204 Biomass auto,new apart | I. The cost is based on a unit with a capacity of 200 kW and assuming the cost for this unit is equally split between an initial cost and a linear dependence on the capacity of the unit
204 Biomass auto,new apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
204 Biomass auto,new apart | K. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
204 Biomass auto,new apart | L. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
204 Biomass auto,new apart | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
204 Biomass auto,new apart | N. For loading fuel manually from bags and removing ash
205 Biomass manual,ex single | 10. Interview with market actors and web price survey, 2020
205 Biomass manual,ex single | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
205 Biomass manual,ex single | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
205 Biomass manual,ex single | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
205 Biomass manual,ex single | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
205 Biomass manual,ex single | 9. Interview with market actors and web price survey, 2020
205 Biomass manual,ex single | A. Nominal heat delivery in 2020 from 20-40 kW. Capacity is of little importance as all heat from a batch of firewood is supplied to the storage tank
205 Biomass manual,ex single | B. EN303-5 measurement method
205 Biomass manual,ex single | C. Prerequisite: house with central heating system
205 Biomass manual,ex single | D. Storage tank
205 Biomass manual,ex single | E. Chimney
205 Biomass manual,ex single | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
205 Biomass manual,ex single | G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
205 Biomass manual,ex single | H. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
205 Biomass manual,ex single | K. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
205 Biomass manual,ex single | L. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
205 Biomass manual,ex single | I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
205 Biomass manual,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
205 Biomass manual,ex single | K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
205 Biomass manual,ex single | L. Including dismantling and disposal of existing boiler
205 Biomass manual,ex single | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
205 Biomass manual,ex single | N. For loading fuel manually from bags and removing ash
206 Wood stove,single, ex tank | 10. Interview with market actors and web price survey, 2020
206 Wood stove,single, ex tank | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
206 Wood stove,single, ex tank | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
206 Wood stove,single, ex tank | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
206 Wood stove,single, ex tank | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
206 Wood stove,single, ex tank | 8. Interview with market actors and web price survey, 2020
206 Wood stove,single, ex tank | A. DIN Plus measurement method
206 Wood stove,single, ex tank | C. The share of space heating covered by a wood stove depends on the options to regularly charge the stove with wood logs and of the location of the stove in the house. With regularly charging and a central location of the stove, the coverage can be up to 80 % of the heating demand in the house. ...
206 Wood stove,single, ex tank | D. More automatic stoves are expected in the future(2030) Therefore, an increment in investment is expected. After this period, it is expected that the technology becomes generic and investment will decrease while still assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent ...
206 Wood stove,single, ex tank | E. Nominal heat delivery in 2020 from 4-10 kW
206 Wood stove,single, ex tank | F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
206 Wood stove,single, ex tank | G. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly.
206 Wood stove,single, ex tank | H. Emission of particles in marketed stoves has decreased by 20% the last 3 years according to (9). Values from previous TC adjusted accordingly.
206 Wood stove,single, ex tank | I. Values decreasing due to more automatic stoves potentially with draught stabilisers. Values likely to further decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries as well as in Danish developments. Filters would increase investment, probab...
206 Wood stove,single, ex tank | J. Following Note D, more advanced stoves will include an electricity demand for conttrol system and draught stabiliser. The estimate is 50 W in operation only when the stove is fired, e.g. 150 times 4 h.
206 Wood stove,single, ex tank | K. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
206 Wood stove,single, ex tank | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
206 Wood stove,single, ex tank | N. For loading fuel manually from bags and removing ash
206 Wood stove, single n w tank | 10. Interview with market actors and web price survey, 2020
206 Wood stove, single n w tank | A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
206 Wood stove, single n w tank | C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
206 Wood stove, single n w tank | D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
206 Wood stove, single n w tank | E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
206 Wood stove, single n w tank | 8. Interview with market actors and web price survey, 2020
206 Wood stove, single n w tank | A. DIN Plus measurement method
206 Wood stove, single n w tank | C. The share of space heating covered by a wood stove depends on the options to regularly charge the stove with wood logs and of the location of the stove in the house. With regularly charging and a central location of the stove, the coverage can be up to 80 % of the heating demand in the house. ...
206 Wood stove, single n w tank | D. More automatic stoves are expected in the future(2030) Therefore, an increment in investment is expected. After this period, it is expected that the technology becomes generic and investment will decrease while still assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent ...
206 Wood stove, single n w tank | F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
206 Wood stove, single n w tank | G. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly.
206 Wood stove, single n w tank | H. Emission of particles in marketed stoves has decreased by 20% the last 3 years according to (9). Values from previous TC adjusted accordingly.
206 Wood stove, single n w tank | I. Values decreasing due to more automatic stoves potentially with draught stabilisers. Values likely to further decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries as well as in Danish developments. Filters would increase investment, probab...
206 Wood stove, single n w tank | J. Following Note D, more advanced stoves will include an electricity demand for conttrol system and draught stabiliser. The estimate is 50 W in operation only when the stove is fired, e.g. 150 times 4 h.
206 Wood stove, single n w tank | K. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
206 Wood stove, single n w tank | L. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
206 Wood stove, single n w tank | I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
206 Wood stove, single n w tank | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
206 Wood stove, single n w tank | K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
206 Wood stove, single n w tank | L. Including dismantling and disposal of existing boiler
206 Wood stove, single n w tank | M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
206 Wood stove, single n w tank | N. For loading fuel manually from bags and removing ash
207 HP air-water,ex single | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP air-water,ex single | A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
207 HP air-water,ex single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-water,ex single | C. Typically cascade solution of smaller heat pumps.
207 HP air-water,ex single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-water,ex single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-water,ex single | F. Including spare parts.
207 HP air-water,ex single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-water,ex single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-water,ex single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-water,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-water,ex single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-water,ex single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-water,ex single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-water,ex single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-water,ex single | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-water,ex single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-water,ex single | Q. Based on a ground source with horizontal collector
207 HP air-water,ex single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-water,ex single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-water,ex single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-water,ex single | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-water,ex single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-water,ex single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-water,ex single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-water,ex single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-water,ex single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-water,ex single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-water,ex single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-water,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,ex apart | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP air-water,ex apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP air-water,ex apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-water,ex apart | C. Typically cascade solution of smaller heat pumps.
207 HP air-water,ex apart | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-water,ex apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-water,ex apart | F. Including spare parts.
207 HP air-water,ex apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-water,ex apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-water,ex apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-water,ex apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-water,ex apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-water,ex apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-water,ex apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-water,ex apart | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-water,ex apart | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-water,ex apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-water,ex apart | Q. Based on a ground source with horizontal collector
207 HP air-water,ex apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-water,ex apart | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-water,ex apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-water,ex apart | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-water,ex apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-water,ex apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-water,ex apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-water,ex apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-water,ex apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-water,ex apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-water,ex apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-water,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water LPP,ex single | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP air-water LPP,ex single | A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
207 HP air-water LPP,ex single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-water LPP,ex single | C. Typically cascade solution of smaller heat pumps.
207 HP air-water LPP,ex single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-water LPP,ex single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-water LPP,ex single | F. Including spare parts.
207 HP air-water LPP,ex single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-water LPP,ex single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-water LPP,ex single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-water LPP,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-water LPP,ex single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-water LPP,ex single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-water LPP,ex single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-water LPP,ex single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-water LPP,ex single | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-water LPP,ex single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-water LPP,ex single | Q. Based on a ground source with horizontal collector
207 HP air-water LPP,ex single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-water LPP,ex single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-water LPP,ex single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-water LPP,ex single | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-water LPP,ex single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-water LPP,ex single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-water LPP,ex single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-water LPP,ex single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-water LPP,ex single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-water LPP,ex single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-water LPP,ex single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-water LPP,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water LPP,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,new single | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP air-water,new single | A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
207 HP air-water,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-water,new single | C. Typically cascade solution of smaller heat pumps.
207 HP air-water,new single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-water,new single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-water,new single | F. Including spare parts.
207 HP air-water,new single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-water,new single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-water,new single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-water,new single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-water,new single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-water,new single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-water,new single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-water,new single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-water,new single | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-water,new single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-water,new single | Q. Based on a ground source with horizontal collector
207 HP air-water,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-water,new single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-water,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-water,new single | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-water,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-water,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-water,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-water,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-water,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-water,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-water,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-water,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,new apart | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP air-water,new apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP air-water,new apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-water,new apart | C. Typically cascade solution of smaller heat pumps.
207 HP air-water,new apart | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-water,new apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-water,new apart | F. Including spare parts.
207 HP air-water,new apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-water,new apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-water,new apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-water,new apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-water,new apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-water,new apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-water,new apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-water,new apart | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-water,new apart | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-water,new apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-water,new apart | Q. Based on a ground source with horizontal collector
207 HP air-water,new apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-water,new apart | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-water,new apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-water,new apart | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-water,new apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-water,new apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-water,new apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-water,new apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-water,new apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-water,new apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-water,new apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-water,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-water,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,ex single | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP ground-water,ex single | A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
207 HP ground-water,ex single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP ground-water,ex single | C. Typically cascade solution of smaller heat pumps.
207 HP ground-water,ex single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP ground-water,ex single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP ground-water,ex single | F. Including spare parts.
207 HP ground-water,ex single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP ground-water,ex single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP ground-water,ex single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP ground-water,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP ground-water,ex single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP ground-water,ex single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP ground-water,ex single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP ground-water,ex single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP ground-water,ex single | O. Data is very limited and therefore this value is highly uncertain.
207 HP ground-water,ex single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP ground-water,ex single | Q. Based on a ground source with horizontal collector
207 HP ground-water,ex single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP ground-water,ex single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP ground-water,ex single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP ground-water,ex single | U. Based on a air-to-air heat pump with one indoor component.
207 HP ground-water,ex single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP ground-water,ex single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP ground-water,ex single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP ground-water,ex single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP ground-water,ex single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP ground-water,ex single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP ground-water,ex single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP ground-water,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,ex apart | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP ground-water,ex apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP ground-water,ex apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP ground-water,ex apart | C. Typically cascade solution of smaller heat pumps.
207 HP ground-water,ex apart | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP ground-water,ex apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP ground-water,ex apart | F. Including spare parts.
207 HP ground-water,ex apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP ground-water,ex apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP ground-water,ex apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP ground-water,ex apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP ground-water,ex apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP ground-water,ex apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP ground-water,ex apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP ground-water,ex apart | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP ground-water,ex apart | O. Data is very limited and therefore this value is highly uncertain.
207 HP ground-water,ex apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP ground-water,ex apart | Q. Based on a ground source with horizontal collector
207 HP ground-water,ex apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP ground-water,ex apart | S. Assumed the same as corresponding air-sourced heat pumps
207 HP ground-water,ex apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP ground-water,ex apart | U. Based on a air-to-air heat pump with one indoor component.
207 HP ground-water,ex apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP ground-water,ex apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP ground-water,ex apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP ground-water,ex apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP ground-water,ex apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP ground-water,ex apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP ground-water,ex apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP ground-water,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,new single | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP ground-water,new single | A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
207 HP ground-water,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP ground-water,new single | C. Typically cascade solution of smaller heat pumps.
207 HP ground-water,new single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP ground-water,new single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP ground-water,new single | F. Including spare parts.
207 HP ground-water,new single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP ground-water,new single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP ground-water,new single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP ground-water,new single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP ground-water,new single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP ground-water,new single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP ground-water,new single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP ground-water,new single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP ground-water,new single | O. Data is very limited and therefore this value is highly uncertain.
207 HP ground-water,new single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP ground-water,new single | Q. Based on a ground source with horizontal collector
207 HP ground-water,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP ground-water,new single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP ground-water,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP ground-water,new single | U. Based on a air-to-air heat pump with one indoor component.
207 HP ground-water,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP ground-water,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP ground-water,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP ground-water,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP ground-water,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP ground-water,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP ground-water,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP ground-water,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,new apart | Heat efficiency (annual average, net, floor heating) [p.u.]
207 HP ground-water,new apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP ground-water,new apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP ground-water,new apart | C. Typically cascade solution of smaller heat pumps.
207 HP ground-water,new apart | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP ground-water,new apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP ground-water,new apart | F. Including spare parts.
207 HP ground-water,new apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP ground-water,new apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP ground-water,new apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP ground-water,new apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP ground-water,new apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP ground-water,new apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP ground-water,new apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP ground-water,new apart | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP ground-water,new apart | O. Data is very limited and therefore this value is highly uncertain.
207 HP ground-water,new apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP ground-water,new apart | Q. Based on a ground source with horizontal collector
207 HP ground-water,new apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP ground-water,new apart | S. Assumed the same as corresponding air-sourced heat pumps
207 HP ground-water,new apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP ground-water,new apart | U. Based on a air-to-air heat pump with one indoor component.
207 HP ground-water,new apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP ground-water,new apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP ground-water,new apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP ground-water,new apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP ground-water,new apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP ground-water,new apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP ground-water,new apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP ground-water,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ground-water,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-air,ex single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP air-air,ex single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-air,ex single | C. Typically cascade solution of smaller heat pumps.
207 HP air-air,ex single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-air,ex single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-air,ex single | F. Including spare parts.
207 HP air-air,ex single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-air,ex single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-air,ex single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-air,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-air,ex single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-air,ex single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-air,ex single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-air,ex single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-air,ex single | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-air,ex single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-air,ex single | Q. Based on a ground source with horizontal collector
207 HP air-air,ex single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-air,ex single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-air,ex single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-air,ex single | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-air,ex single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-air,ex single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-air,ex single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-air,ex single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-air,ex single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-air,ex single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-air,ex single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-air,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-air,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-air,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-air,new single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP air-air,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP air-air,new single | C. Typically cascade solution of smaller heat pumps.
207 HP air-air,new single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP air-air,new single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP air-air,new single | F. Including spare parts.
207 HP air-air,new single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP air-air,new single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP air-air,new single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP air-air,new single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP air-air,new single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP air-air,new single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP air-air,new single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP air-air,new single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP air-air,new single | O. Data is very limited and therefore this value is highly uncertain.
207 HP air-air,new single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP air-air,new single | Q. Based on a ground source with horizontal collector
207 HP air-air,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP air-air,new single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP air-air,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP air-air,new single | U. Based on a air-to-air heat pump with one indoor component.
207 HP air-air,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP air-air,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP air-air,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP air-air,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP air-air,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP air-air,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP air-air,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP air-air,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-air,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP air-air,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ventilation,new single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP ventilation,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP ventilation,new single | C. Typically cascade solution of smaller heat pumps.
207 HP ventilation,new single | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP ventilation,new single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP ventilation,new single | F. Including spare parts.
207 HP ventilation,new single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP ventilation,new single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP ventilation,new single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP ventilation,new single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP ventilation,new single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP ventilation,new single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP ventilation,new single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP ventilation,new single | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP ventilation,new single | O. Data is very limited and therefore this value is highly uncertain.
207 HP ventilation,new single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP ventilation,new single | Q. Based on a ground source with horizontal collector
207 HP ventilation,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP ventilation,new single | S. Assumed the same as corresponding air-sourced heat pumps
207 HP ventilation,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP ventilation,new single | U. Based on a air-to-air heat pump with one indoor component.
207 HP ventilation,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP ventilation,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP ventilation,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP ventilation,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP ventilation,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP ventilation,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP ventilation,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP ventilation,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ventilation,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ventilation,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ventilation,new apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
207 HP ventilation,new apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
207 HP ventilation,new apart | C. Typically cascade solution of smaller heat pumps.
207 HP ventilation,new apart | D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
207 HP ventilation,new apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
207 HP ventilation,new apart | F. Including spare parts.
207 HP ventilation,new apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
207 HP ventilation,new apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
207 HP ventilation,new apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
207 HP ventilation,new apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
207 HP ventilation,new apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
207 HP ventilation,new apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
207 HP ventilation,new apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
207 HP ventilation,new apart | N. Based on discussions with suppliers and the length of available insurance plans.
207 HP ventilation,new apart | O. Data is very limited and therefore this value is highly uncertain.
207 HP ventilation,new apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
207 HP ventilation,new apart | Q. Based on a ground source with horizontal collector
207 HP ventilation,new apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
207 HP ventilation,new apart | S. Assumed the same as corresponding air-sourced heat pumps
207 HP ventilation,new apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
207 HP ventilation,new apart | U. Based on a air-to-air heat pump with one indoor component.
207 HP ventilation,new apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
207 HP ventilation,new apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
207 HP ventilation,new apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
207 HP ventilation,new apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
207 HP ventilation,new apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
207 HP ventilation,new apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
207 HP ventilation,new apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
207 HP ventilation,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ventilation,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
207 HP ventilation,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,ex single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
208 HP hybrid,ex single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
208 HP hybrid,ex single | C. Typically cascade solution of smaller heat pumps.
208 HP hybrid,ex single | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
208 HP hybrid,ex single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
208 HP hybrid,ex single | F. Including spare parts.
208 HP hybrid,ex single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
208 HP hybrid,ex single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
208 HP hybrid,ex single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
208 HP hybrid,ex single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
208 HP hybrid,ex single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
208 HP hybrid,ex single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
208 HP hybrid,ex single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
208 HP hybrid,ex single | N. Based on discussions with suppliers and the length of available insurance plans.
208 HP hybrid,ex single | O. Data is very limited and therefore this value is highly uncertain.
208 HP hybrid,ex single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
208 HP hybrid,ex single | Q. Based on a ground source with horizontal collector
208 HP hybrid,ex single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
208 HP hybrid,ex single | S. Assumed the same as corresponding air-sourced heat pumps
208 HP hybrid,ex single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
208 HP hybrid,ex single | U. Based on a air-to-air heat pump with one indoor component.
208 HP hybrid,ex single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
208 HP hybrid,ex single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
208 HP hybrid,ex single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
208 HP hybrid,ex single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
208 HP hybrid,ex single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
208 HP hybrid,ex single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
208 HP hybrid,ex single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
208 HP hybrid,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,ex apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
208 HP hybrid,ex apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
208 HP hybrid,ex apart | C. Typically cascade solution of smaller heat pumps.
208 HP hybrid,ex apart | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
208 HP hybrid,ex apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
208 HP hybrid,ex apart | F. Including spare parts.
208 HP hybrid,ex apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
208 HP hybrid,ex apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
208 HP hybrid,ex apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
208 HP hybrid,ex apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
208 HP hybrid,ex apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
208 HP hybrid,ex apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
208 HP hybrid,ex apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
208 HP hybrid,ex apart | N. Based on discussions with suppliers and the length of available insurance plans.
208 HP hybrid,ex apart | O. Data is very limited and therefore this value is highly uncertain.
208 HP hybrid,ex apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
208 HP hybrid,ex apart | Q. Based on a ground source with horizontal collector
208 HP hybrid,ex apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
208 HP hybrid,ex apart | S. Assumed the same as corresponding air-sourced heat pumps
208 HP hybrid,ex apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
208 HP hybrid,ex apart | U. Based on a air-to-air heat pump with one indoor component.
208 HP hybrid,ex apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
208 HP hybrid,ex apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
208 HP hybrid,ex apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
208 HP hybrid,ex apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
208 HP hybrid,ex apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
208 HP hybrid,ex apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
208 HP hybrid,ex apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
208 HP hybrid,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,new single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
208 HP hybrid,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
208 HP hybrid,new single | C. Typically cascade solution of smaller heat pumps.
208 HP hybrid,new single | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
208 HP hybrid,new single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
208 HP hybrid,new single | F. Including spare parts.
208 HP hybrid,new single | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
208 HP hybrid,new single | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
208 HP hybrid,new single | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
208 HP hybrid,new single | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
208 HP hybrid,new single | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
208 HP hybrid,new single | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
208 HP hybrid,new single | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
208 HP hybrid,new single | N. Based on discussions with suppliers and the length of available insurance plans.
208 HP hybrid,new single | O. Data is very limited and therefore this value is highly uncertain.
208 HP hybrid,new single | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
208 HP hybrid,new single | Q. Based on a ground source with horizontal collector
208 HP hybrid,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
208 HP hybrid,new single | S. Assumed the same as corresponding air-sourced heat pumps
208 HP hybrid,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
208 HP hybrid,new single | U. Based on a air-to-air heat pump with one indoor component.
208 HP hybrid,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
208 HP hybrid,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
208 HP hybrid,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
208 HP hybrid,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
208 HP hybrid,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
208 HP hybrid,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
208 HP hybrid,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
208 HP hybrid,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,new apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
208 HP hybrid,new apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
208 HP hybrid,new apart | C. Typically cascade solution of smaller heat pumps.
208 HP hybrid,new apart | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
208 HP hybrid,new apart | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
208 HP hybrid,new apart | F. Including spare parts.
208 HP hybrid,new apart | G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
208 HP hybrid,new apart | H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
208 HP hybrid,new apart | I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
208 HP hybrid,new apart | J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
208 HP hybrid,new apart | K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
208 HP hybrid,new apart | L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
208 HP hybrid,new apart | M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
208 HP hybrid,new apart | N. Based on discussions with suppliers and the length of available insurance plans.
208 HP hybrid,new apart | O. Data is very limited and therefore this value is highly uncertain.
208 HP hybrid,new apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
208 HP hybrid,new apart | Q. Based on a ground source with horizontal collector
208 HP hybrid,new apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
208 HP hybrid,new apart | S. Assumed the same as corresponding air-sourced heat pumps
208 HP hybrid,new apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
208 HP hybrid,new apart | U. Based on a air-to-air heat pump with one indoor component.
208 HP hybrid,new apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
208 HP hybrid,new apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
208 HP hybrid,new apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
208 HP hybrid,new apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
208 HP hybrid,new apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
208 HP hybrid,new apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
208 HP hybrid,new apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
208 HP hybrid,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
208 HP hybrid,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,ex single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
215 Solar heating,ex single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
215 Solar heating,ex single | C. Typically cascade solution of smaller heat pumps.
215 Solar heating,ex single | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
215 Solar heating,ex single | E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 20...
215 Solar heating,ex single | 6. Recommendation: Converting solar thermal collector area into installed capacity (m2 to kWth). Technical note, IEA SHC 2004.
215 Solar heating,ex single | A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
215 Solar heating,ex single | B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
215 Solar heating,ex single | C. Increase due to better materials/fluids.
215 Solar heating,ex single | D. Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
215 Solar heating,ex single | E. Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
215 Solar heating,ex single | F. Electricity for solar pump and control. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewab...
215 Solar heating,ex single | G. Pollution associated with the small amount of electricity needed for operation is neglected.
215 Solar heating,ex single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
215 Solar heating,ex single | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
215 Solar heating,ex single | J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
215 Solar heating,ex single | K. Based on data from interviews with installers during creation of this data sheet
215 Solar heating,ex single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
215 Solar heating,ex single | S. Assumed the same as corresponding air-sourced heat pumps
215 Solar heating,ex single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
215 Solar heating,ex single | U. Based on a air-to-air heat pump with one indoor component.
215 Solar heating,ex single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
215 Solar heating,ex single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
215 Solar heating,ex single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
215 Solar heating,ex single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
215 Solar heating,ex single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
215 Solar heating,ex single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
215 Solar heating,ex single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
215 Solar heating,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,ex single | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,ex apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
215 Solar heating,ex apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
215 Solar heating,ex apart | C. Typically cascade solution of smaller heat pumps.
215 Solar heating,ex apart | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
215 Solar heating,ex apart | 1. Solvarme faktablade, www.altomsolvarme.dk.
215 Solar heating,ex apart | A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
215 Solar heating,ex apart | B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
215 Solar heating,ex apart | C. Increase due to better materials/fluids.
215 Solar heating,ex apart | D. Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
215 Solar heating,ex apart | E. Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
215 Solar heating,ex apart | F. Electricity for solar pump and control. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewab...
215 Solar heating,ex apart | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
215 Solar heating,ex apart | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
215 Solar heating,ex apart | N. Based on discussions with suppliers and the length of available insurance plans.
215 Solar heating,ex apart | O. Data is very limited and therefore this value is highly uncertain.
215 Solar heating,ex apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
215 Solar heating,ex apart | Q. Based on a ground source with horizontal collector
215 Solar heating,ex apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
215 Solar heating,ex apart | S. Assumed the same as corresponding air-sourced heat pumps
215 Solar heating,ex apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
215 Solar heating,ex apart | U. Based on a air-to-air heat pump with one indoor component.
215 Solar heating,ex apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
215 Solar heating,ex apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
215 Solar heating,ex apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
215 Solar heating,ex apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
215 Solar heating,ex apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
215 Solar heating,ex apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
215 Solar heating,ex apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
215 Solar heating,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,ex apart | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,new single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
215 Solar heating,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
215 Solar heating,new single | C. Typically cascade solution of smaller heat pumps.
215 Solar heating,new single | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
215 Solar heating,new single | 1. Solvarme faktablade, www.altomsolvarme.dk.
215 Solar heating,new single | A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
215 Solar heating,new single | B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
215 Solar heating,new single | C. Increase due to better materials/fluids.
215 Solar heating,new single | D. Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
215 Solar heating,new single | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
215 Solar heating,new single | J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
215 Solar heating,new single | K. Based on data from interviews with installers during creation of this data sheet
215 Solar heating,new single | G. Pollution associated with the small amount of electricity needed for operation is neglected.
215 Solar heating,new single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
215 Solar heating,new single | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
215 Solar heating,new single | J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
215 Solar heating,new single | K. Based on data from interviews with installers during creation of this data sheet
215 Solar heating,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
215 Solar heating,new single | S. Assumed the same as corresponding air-sourced heat pumps
215 Solar heating,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
215 Solar heating,new single | U. Based on a air-to-air heat pump with one indoor component.
215 Solar heating,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
215 Solar heating,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
215 Solar heating,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
215 Solar heating,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
215 Solar heating,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
215 Solar heating,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
215 Solar heating,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
215 Solar heating,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,new apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
215 Solar heating,new apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
215 Solar heating,new apart | C. Typically cascade solution of smaller heat pumps.
215 Solar heating,new apart | Heat efficiency (annual average, net, total system, floor heating) [p.u.]
215 Solar heating,new apart | 1. Solvarme faktablade, www.altomsolvarme.dk.
215 Solar heating,new apart | A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
215 Solar heating,new apart | B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
215 Solar heating,new apart | C. Increase due to better materials/fluids.
215 Solar heating,new apart | E. Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
215 Solar heating,new apart | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
215 Solar heating,new apart | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
215 Solar heating,new apart | K. Based on data from interviews with installers during creation of this data sheet
215 Solar heating,new apart | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
215 Solar heating,new apart | N. Based on discussions with suppliers and the length of available insurance plans.
215 Solar heating,new apart | O. Data is very limited and therefore this value is highly uncertain.
215 Solar heating,new apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
215 Solar heating,new apart | Q. Based on a ground source with horizontal collector
215 Solar heating,new apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
215 Solar heating,new apart | S. Assumed the same as corresponding air-sourced heat pumps
215 Solar heating,new apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
215 Solar heating,new apart | U. Based on a air-to-air heat pump with one indoor component.
215 Solar heating,new apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
215 Solar heating,new apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
215 Solar heating,new apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
215 Solar heating,new apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
215 Solar heating,new apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
215 Solar heating,new apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
215 Solar heating,new apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
215 Solar heating,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
215 Solar heating,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
216 Electric heating,new single | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
216 Electric heating,new single | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
216 Electric heating,new single | C. Typically cascade solution of smaller heat pumps.
216 Electric heating,new single | 5. Based on data from interviews with installers during creation of this data sheet
216 Electric heating,new single | A. Annual efficiency based on 100 % space heating efficiency and hot water efficiency. In addition, distribution heat losses compared to water based heating systems are saved, typically in the range of 5-10 %.
216 Electric heating,new single | C. Assuming change of heating elements in the hot water tank every 10 years.
216 Electric heating,new single | D. The price includes the complete system including room heaters and hot tap water preparation.
216 Electric heating,new single | E. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
216 Electric heating,new single | F. Including costs of wiring and procurement and installation of radiators
216 Electric heating,new single | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
216 Electric heating,new single | J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
216 Electric heating,new single | K. Based on data from interviews with installers during creation of this data sheet
216 Electric heating,new single | G. Pollution associated with the small amount of electricity needed for operation is neglected.
216 Electric heating,new single | H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
216 Electric heating,new single | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
216 Electric heating,new single | J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
216 Electric heating,new single | K. Based on data from interviews with installers during creation of this data sheet
216 Electric heating,new single | R. The ration between installation and equipment is maintained in the upper and lower boundaries
216 Electric heating,new single | S. Assumed the same as corresponding air-sourced heat pumps
216 Electric heating,new single | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
216 Electric heating,new single | U. Based on a air-to-air heat pump with one indoor component.
216 Electric heating,new single | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
216 Electric heating,new single | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
216 Electric heating,new single | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
216 Electric heating,new single | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
216 Electric heating,new single | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
216 Electric heating,new single | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
216 Electric heating,new single | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
216 Electric heating,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
216 Electric heating,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
216 Electric heating,new single | AC. Including domestic hot water storage tank and auxiliary equipment.
216 Electric heating,new apart | A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
216 Electric heating,new apart | B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
216 Electric heating,new apart | C. Typically cascade solution of smaller heat pumps.
216 Electric heating,new apart | 5. Based on data from interviews with installers during creation of this data sheet
216 Electric heating,new apart | A. Annual efficiency based on 100 % space heating efficiency and hot water efficiency. In addition, distribution heat losses compared to water based heating systems are saved, typically in the range of 5-10 %.
216 Electric heating,new apart | B. Assuming 150 apartments.
216 Electric heating,new apart | C. Assuming change of heating elements in the hot water tank every 10 years.
216 Electric heating,new apart | D. The price includes the complete system including room heaters and hot tap water preparation.
216 Electric heating,new apart | E. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
216 Electric heating,new apart | F. Including costs of wiring and procurement and installation of radiators
216 Electric heating,new apart | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
216 Electric heating,new apart | K. Based on data from interviews with installers during creation of this data sheet
216 Electric heating,new apart | I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
216 Electric heating,new apart | N. Based on discussions with suppliers and the length of available insurance plans.
216 Electric heating,new apart | O. Data is very limited and therefore this value is highly uncertain.
216 Electric heating,new apart | P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
216 Electric heating,new apart | Q. Based on a ground source with horizontal collector
216 Electric heating,new apart | R. The ration between installation and equipment is maintained in the upper and lower boundaries
216 Electric heating,new apart | S. Assumed the same as corresponding air-sourced heat pumps
216 Electric heating,new apart | T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
216 Electric heating,new apart | U. Based on a air-to-air heat pump with one indoor component.
216 Electric heating,new apart | V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
216 Electric heating,new apart | W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
216 Electric heating,new apart | X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
216 Electric heating,new apart | Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
216 Electric heating,new apart | Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
216 Electric heating,new apart | AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to...
216 Electric heating,new apart | AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. S...
216 Electric heating,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
216 Electric heating,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.
216 Electric heating,new apart | AC. Including domestic hot water storage tank and auxiliary equipment.

## Ref
ws | description
201 Oil boiler, ex single | 1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
201 Oil boiler, ex single | 2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
201 Oil boiler, ex single | 3. BOILSIM http://www.boilsim.com/.2011
201 Oil boiler, ex single | 4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
201 Oil boiler, ex single | 5. http://www.blauer-engel.de/_downloads/publikationen/erfolgsbilanz/ Erfolgsbilanz_Heiztechnologien.pdf (Rules for NOX). This is not present at the Blauer Engel Homepage, but can be found at the Internet.2011
201 Oil boiler, ex single | 11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
201 Oil boiler, ex single | 14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
201 Oil boiler, new single | 1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
201 Oil boiler, new single | 2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
201 Oil boiler, new single | 3. BOILSIM http://www.boilsim.com/.2011
201 Oil boiler, new single | 4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
201 Oil boiler, new single | 11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
201 Oil boiler, new single | 14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
201 Oil boiler, new apart | 1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
201 Oil boiler, new apart | 2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
201 Oil boiler, new apart | 3. BOILSIM http://www.boilsim.com/.2011
201 Oil boiler, new apart | 4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
201 Oil boiler, new apart | 11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
201 Oil boiler, new apart | 14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
202 Gas boiler, ex single | 1. Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
202 Gas boiler, ex single | 2. Facts and figures about domestic gas boilers. Compilation of results covering 25 years of testing at DGC's laboratory February 2016, updated 2017.Jean Schweitzer, DGC
202 Gas boiler, ex single | 3. Study "Ecodesign of Boilers and Combi-boilers" (VHK) for the European Commission, DG Transport and Energy (DG TREN). Task 4 Section 3.1.
202 Gas boiler, ex single | 4. DGC, 2020 "Dokumentation af villagaskedlers faktiske virkningsgrader". Projektrapport.
202 Gas boiler, ex single | 5. Start stop emissions of domestic appliances. H. Hüppelshäuser and F. Jansen. Ruhrgas. IGRC 1998.
202 Gas boiler, ex single | 6. HMN: http://salg.naturgas.dk.
202 Gas boiler, ex single | 7. DGC project : Evaluation of the NOx emissions of the Danish population of gas boilers below 120 kW
202 Gas boiler, ex single | 28. Facts and figures about domestic gas boilers. A compilation of results covering 25 years of testing at DGC's laboratory. DGC February 2016
202 Gas boiler, ex single | 29. Investigations on 25 gas boilers lifetime with HMN boiler statistics. 743-48 Jean Schweitzer, DGC Sept. 2016
202 Gas boiler, ex single | 30. DGC Statistics, Efficiency and Emission test reports from district heating plants, up to and including 2014
202 Gas boiler, ex single | 31. Danish District Heating Association, information given to the 2012 survey for the report
202 Gas boiler, ex apart | 6. HMN: http://salg.naturgas.dk.
202 Gas boiler, ex apart | 7. DGC project : Evaluation of the NOx emissions of the Danish population of gas boilers below 120 kW
202 Gas boiler, ex apart | 30. DGC Statistics, Efficiency and Emission test reports from district heating plants, up to and including 2014
202 Gas boiler, ex apart | 31. Danish District Heating Association, information given to the 2012 survey for the report
202 Gas boiler, new single | 1. Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
202 Gas boiler, new single | 2. Facts and figures about domestic gas boilers. Compilation of results covering 25 years of testing at DGC's laboratory February 2016, updated 2017.Jean Schweitzer, DGC
202 Gas boiler, new single | 3. Study "Ecodesign of Boilers and Combi-boilers" (VHK) for the European Commission, DG Transport and Energy (DG TREN). Task 4 Section 3.1.
202 Gas boiler, new single | 5. Start stop emissions of domestic appliances. H. Hüppelshäuser and F. Jansen. Ruhrgas. IGRC 1998.
202 Gas boiler, new single | 6. HMN: http://salg.naturgas.dk.
202 Gas boiler, new single | 28. Facts and figures about domestic gas boilers. A compilation of results covering 25 years of testing at DGC's laboratory. DGC February 2016
202 Gas boiler, new single | 29. Investigations on 25 gas boilers lifetime with HMN boiler statistics. 743-48 Jean Schweitzer, DGC Sept. 2016
202 Gas boiler, new single | 33. Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
202 Gas boiler, new apart | 1. Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
202 Gas boiler, new apart | 31. Danish District Heating Association, information given to the 2012 survey for the report
202 Gas boiler, new apart | 33. Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
203 DH indirect,new single | 8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
203 DH indirect,new single | 9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
203 DH indirect,new single | 10. Interview with market actors and web price survey, 2020
203 DH indirect,ex single | 8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
203 DH indirect,ex single | 9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
203 DH indirect,ex single | 10. Interview with market actors and web price survey, 2020
203 DH indirect,ex apart | 2. Communication with Gemina Termix, www.termix.dk. 2011
203 DH indirect,ex apart | 4. Communication with Danfoss Redan, www.redan.danfoss.com. Technology data for individual heat production and energy transport, 2011
203 DH indirect,ex apart | 7. Prices from different providers of substations, 2016
203 DH indirect,ex apart | 8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
203 DH indirect,ex apart | 10. Interview with market actors and web price survey, 2020
203 DH indirect,new apart | 2. Communication with Gemina Termix, www.termix.dk. 2011
203 DH indirect,new apart | 4. Communication with Danfoss Redan, www.redan.danfoss.com. Technology data for individual heat production and energy transport, 2011
203 DH indirect,new apart | 7. Prices from different providers of substations, 2016
203 DH indirect,new apart | 8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
203 DH indirect,new apart | 10. Interview with market actors and web price survey, 2020
203 DH direct,new single | 8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
203 DH direct,new single | 9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
203 DH direct,new single | 10. Interview with market actors and web price survey, 2020. The stated cost represent a situation with competitive pricing.
203 DH direct,ex single | 8. Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
203 DH direct,ex single | 9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
203 DH direct,ex single | 10. Interview with market actors and web price survey, 2020. The stated cost represent a situation with competitive pricing.
203 DH direct,ex apart | 8. Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
203 DH direct,ex apart | 9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
203 DH direct,ex apart | 10. Interview with market actors and web price survey, 2020
203 DH direct,new apart | 8. Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
203 DH direct,new apart | 9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
203 DH direct,new apart | 10. Interview with market actors and web price survey, 2020
204 Biomass auto,ex single | 1. www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg
204 Biomass auto,ex single | 2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
204 Biomass auto,ex single | 3. Lot 15: Solid fuel small combustion installations-Base Case definition
204 Biomass auto,ex single | 4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
204 Biomass auto,ex single | 5. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
204 Biomass auto,ex single | 6. Estimate by the Danish Energy Agency and Energinet, 2017
204 Biomass auto,ex single | 7. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
204 Biomass auto,ex single | 8. Interview with market actors and web price survey, 2020
204 Biomass auto,ex single | 9. Estimate based on user interview, 2020
204 Biomass auto,ex single | 10. Estimate by Ea Energy Analyses, 2020
204 Biomass auto,new single | 1. www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg
204 Biomass auto,new single | 2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
204 Biomass auto,new single | 3. Lot 15: Solid fuel small combustion installations-Base Case definition
204 Biomass auto,new single | 4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
204 Biomass auto,new single | 5. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
204 Biomass auto,new single | 6. Estimate by the Danish Energy Agency and Energinet, 2017
204 Biomass auto,new single | 7. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
204 Biomass auto,new single | 8. Interview with market actors and web price survey, 2020
204 Biomass auto,new single | 9. Estimate based on user interview, 2020
204 Biomass auto,new single | 10. Estimate by Ea Energy Analyses, 2020
204 Biomass auto,ex apart | 1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro
204 Biomass auto,ex apart | 2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
204 Biomass auto,ex apart | 3. Energibesparelser - det behøver ikke være så svært; Energibranchen.dk, nr. 3, september 2009
204 Biomass auto,ex apart | 4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
204 Biomass auto,ex apart | 5. Estimate by the Danish Energy Agency and Energinet, 2017
204 Biomass auto,ex apart | 6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
204 Biomass auto,ex apart | 7. Estimate by Ea Energy Analyses, 2020
204 Biomass auto,ex apart | 8. Interview with market actors and web price survey, 2020
204 Biomass auto,new apart | 1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro
204 Biomass auto,new apart | 2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
204 Biomass auto,new apart | 3. Energibesparelser - det behøver ikke være så svært; Energibranchen.dk, nr. 3, september 2009
204 Biomass auto,new apart | 4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
204 Biomass auto,new apart | 5. Estimate by the Danish Energy Agency and Energinet, 2017
204 Biomass auto,new apart | 6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
204 Biomass auto,new apart | 7. Estimate by Ea Energy Analyses, 2020
204 Biomass auto,new apart | 8. Interview with market actors and web price survey, 2020
205 Biomass manual,ex single | 1. www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg
205 Biomass manual,ex single | 2. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro
205 Biomass manual,ex single | 3. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
205 Biomass manual,ex single | 4. Lot 15: Solid fuel small combustion installations-Base Case definition
205 Biomass manual,ex single | 5. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
205 Biomass manual,ex single | 7. Estimate by the Danish Energy Agency and Energinet, 2017
205 Biomass manual,ex single | 8. Estimate by Ea Energy Analyses, 2020
205 Biomass manual,ex single | 9. Interview with market actors and web price survey, 2020
206 Wood stove,single, ex tank | 1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
206 Wood stove,single, ex tank | 2. Lot 15: Solid fuel small combustion installations-Base Case definition.
206 Wood stove,single, ex tank | 3. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE no. 102, 2014
206 Wood stove,single, ex tank | 4. Estimate by the Danish Energy Agency and Energinet, 2017
206 Wood stove,single, ex tank | 5. Estimate by Ea Energy Analyses, 2020
206 Wood stove,single, ex tank | 6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
206 Wood stove,single, ex tank | 7. https://www.teknologisk.dk/ydelser/danske-braendeovne-er-blevet-bedre-for-miljoeet/33283
206 Wood stove,single, ex tank | 8. Interview with market actors and web price survey, 2020
206 Wood stove, single n w tank | 1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
206 Wood stove, single n w tank | 2. Lot 15: Solid fuel small combustion installations-Base Case definition.
206 Wood stove, single n w tank | 3. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
206 Wood stove, single n w tank | 4. Estimate by the Danish Energy Agency and Energinet, 2017
206 Wood stove, single n w tank | 5. Estimate by Ea Energy Analyses, 2020
206 Wood stove, single n w tank | 6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
206 Wood stove, single n w tank | 7. https://www.teknologisk.dk/ydelser/danske-braendeovne-er-blevet-bedre-for-miljoeet/33283
206 Wood stove, single n w tank | 8. Interview with market actors and web price survey, 2020
207 HP air-water,ex single | 1. Interviews with various installation companies.
207 HP air-water,ex single | 2. Teknologisk Institute.
207 HP air-water,ex single | 3. Installation company
207 HP air-water,ex single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-water,ex single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,ex single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-water,ex single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-water,ex single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-water,ex single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-water,ex single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-water,ex single | 11. Bosch 2020, conversation
207 HP air-water,ex single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-water,ex single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-water,ex single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,ex single | 15. ENS heat pump sale statistics
207 HP air-water,ex single | 16. Danfoss, 2015, information provided at workshop
207 HP air-water,ex single | 17. Bosch, 2015 , information provided at workshop
207 HP air-water,ex single | 18. Market and Statistics Report, EHPA 2014
207 HP air-water,ex single | 19. Energistyrelsen, 2015, conversation
207 HP air-water,ex single | 20. Teknologisk Institut, 2015, conversation
207 HP air-water,ex single | 21. Nilan, 2015, conversation
207 HP air-water,ex single | 22. Genvex, 2015, conversation
207 HP air-water,ex single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-water,ex single | 24. Sparenergi.dk, 2015
207 HP air-water,ex single | 25. Energinet.dk, 2015, conversation
207 HP air-water,ex single | 26. Cronborg, 2015, conversation
207 HP air-water,ex single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-water,ex single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-water,ex single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP air-water,ex apart | 1. Interviews with various installation companies.
207 HP air-water,ex apart | 2. Teknologisk Institute.
207 HP air-water,ex apart | 3. Installation company
207 HP air-water,ex apart | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-water,ex apart | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,ex apart | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-water,ex apart | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-water,ex apart | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-water,ex apart | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-water,ex apart | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-water,ex apart | 11. Bosch 2020, conversation
207 HP air-water,ex apart | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-water,ex apart | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-water,ex apart | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,ex apart | 15. ENS heat pump sale statistics
207 HP air-water,ex apart | 16. Danfoss, 2015, information provided at workshop
207 HP air-water,ex apart | 17. Bosch, 2015 , information provided at workshop
207 HP air-water,ex apart | 18. Market and Statistics Report, EHPA 2014
207 HP air-water,ex apart | 19. Energistyrelsen, 2015, conversation
207 HP air-water,ex apart | 20. Teknologisk Institut, 2015, conversation
207 HP air-water,ex apart | 21. Nilan, 2015, conversation
207 HP air-water,ex apart | 22. Genvex, 2015, conversation
207 HP air-water,ex apart | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-water,ex apart | 24. Sparenergi.dk, 2015
207 HP air-water,ex apart | 25. Energinet.dk, 2015, conversation
207 HP air-water,ex apart | 26. Cronborg, 2015, conversation
207 HP air-water,ex apart | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-water,ex apart | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-water,ex apart | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP air-water LPP,ex single | 1. Interviews with various installation companies.
207 HP air-water LPP,ex single | 2. Teknologisk Institute.
207 HP air-water LPP,ex single | 3. Installation company
207 HP air-water LPP,ex single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-water LPP,ex single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water LPP,ex single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-water LPP,ex single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-water LPP,ex single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-water LPP,ex single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-water LPP,ex single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-water LPP,ex single | 11. Bosch 2020, conversation
207 HP air-water LPP,ex single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-water LPP,ex single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-water LPP,ex single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water LPP,ex single | 15. ENS heat pump sale statistics
207 HP air-water LPP,ex single | 16. Danfoss, 2015, information provided at workshop
207 HP air-water LPP,ex single | 17. Bosch, 2015 , information provided at workshop
207 HP air-water LPP,ex single | 18. Market and Statistics Report, EHPA 2014
207 HP air-water LPP,ex single | 19. Energistyrelsen, 2015, conversation
207 HP air-water LPP,ex single | 20. Teknologisk Institut, 2015, conversation
207 HP air-water LPP,ex single | 21. Nilan, 2015, conversation
207 HP air-water LPP,ex single | 22. Genvex, 2015, conversation
207 HP air-water LPP,ex single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-water LPP,ex single | 24. Sparenergi.dk, 2015
207 HP air-water LPP,ex single | 25. Energinet.dk, 2015, conversation
207 HP air-water LPP,ex single | 26. Cronborg, 2015, conversation
207 HP air-water LPP,ex single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-water LPP,ex single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-water LPP,ex single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP air-water,new single | 1. Interviews with various installation companies.
207 HP air-water,new single | 2. Teknologisk Institute.
207 HP air-water,new single | 3. Installation company
207 HP air-water,new single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-water,new single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,new single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-water,new single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-water,new single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-water,new single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-water,new single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-water,new single | 11. Bosch 2020, conversation
207 HP air-water,new single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-water,new single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-water,new single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,new single | 15. ENS heat pump sale statistics
207 HP air-water,new single | 16. Danfoss, 2015, information provided at workshop
207 HP air-water,new single | 17. Bosch, 2015 , information provided at workshop
207 HP air-water,new single | 18. Market and Statistics Report, EHPA 2014
207 HP air-water,new single | 19. Energistyrelsen, 2015, conversation
207 HP air-water,new single | 20. Teknologisk Institut, 2015, conversation
207 HP air-water,new single | 21. Nilan, 2015, conversation
207 HP air-water,new single | 22. Genvex, 2015, conversation
207 HP air-water,new single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-water,new single | 24. Sparenergi.dk, 2015
207 HP air-water,new single | 25. Energinet.dk, 2015, conversation
207 HP air-water,new single | 26. Cronborg, 2015, conversation
207 HP air-water,new single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-water,new single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-water,new single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP air-water,new apart | 1. Interviews with various installation companies.
207 HP air-water,new apart | 2. Teknologisk Institute.
207 HP air-water,new apart | 3. Installation company
207 HP air-water,new apart | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-water,new apart | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,new apart | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-water,new apart | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-water,new apart | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-water,new apart | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-water,new apart | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-water,new apart | 11. Bosch 2020, conversation
207 HP air-water,new apart | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-water,new apart | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-water,new apart | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-water,new apart | 15. ENS heat pump sale statistics
207 HP air-water,new apart | 16. Danfoss, 2015, information provided at workshop
207 HP air-water,new apart | 17. Bosch, 2015 , information provided at workshop
207 HP air-water,new apart | 18. Market and Statistics Report, EHPA 2014
207 HP air-water,new apart | 19. Energistyrelsen, 2015, conversation
207 HP air-water,new apart | 20. Teknologisk Institut, 2015, conversation
207 HP air-water,new apart | 21. Nilan, 2015, conversation
207 HP air-water,new apart | 22. Genvex, 2015, conversation
207 HP air-water,new apart | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-water,new apart | 24. Sparenergi.dk, 2015
207 HP air-water,new apart | 25. Energinet.dk, 2015, conversation
207 HP air-water,new apart | 26. Cronborg, 2015, conversation
207 HP air-water,new apart | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-water,new apart | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-water,new apart | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP ground-water,ex single | 1. Interviews with various installation companies.
207 HP ground-water,ex single | 2. Teknologisk Institute.
207 HP ground-water,ex single | 3. Installation company
207 HP ground-water,ex single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP ground-water,ex single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,ex single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP ground-water,ex single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP ground-water,ex single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP ground-water,ex single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP ground-water,ex single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP ground-water,ex single | 11. Bosch 2020, conversation
207 HP ground-water,ex single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP ground-water,ex single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP ground-water,ex single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,ex single | 15. ENS heat pump sale statistics
207 HP ground-water,ex single | 16. Danfoss, 2015, information provided at workshop
207 HP ground-water,ex single | 17. Bosch, 2015 , information provided at workshop
207 HP ground-water,ex single | 18. Market and Statistics Report, EHPA 2014
207 HP ground-water,ex single | 19. Energistyrelsen, 2015, conversation
207 HP ground-water,ex single | 20. Teknologisk Institut, 2015, conversation
207 HP ground-water,ex single | 21. Nilan, 2015, conversation
207 HP ground-water,ex single | 22. Genvex, 2015, conversation
207 HP ground-water,ex single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP ground-water,ex single | 24. Sparenergi.dk, 2015
207 HP ground-water,ex single | 25. Energinet.dk, 2015, conversation
207 HP ground-water,ex single | 26. Cronborg, 2015, conversation
207 HP ground-water,ex single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP ground-water,ex single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP ground-water,ex single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP ground-water,ex apart | 1. Interviews with various installation companies.
207 HP ground-water,ex apart | 2. Teknologisk Institute.
207 HP ground-water,ex apart | 3. Installation company
207 HP ground-water,ex apart | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP ground-water,ex apart | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,ex apart | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP ground-water,ex apart | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP ground-water,ex apart | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP ground-water,ex apart | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP ground-water,ex apart | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP ground-water,ex apart | 11. Bosch 2020, conversation
207 HP ground-water,ex apart | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP ground-water,ex apart | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP ground-water,ex apart | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,ex apart | 15. ENS heat pump sale statistics
207 HP ground-water,ex apart | 16. Danfoss, 2015, information provided at workshop
207 HP ground-water,ex apart | 17. Bosch, 2015 , information provided at workshop
207 HP ground-water,ex apart | 18. Market and Statistics Report, EHPA 2014
207 HP ground-water,ex apart | 19. Energistyrelsen, 2015, conversation
207 HP ground-water,ex apart | 20. Teknologisk Institut, 2015, conversation
207 HP ground-water,ex apart | 21. Nilan, 2015, conversation
207 HP ground-water,ex apart | 22. Genvex, 2015, conversation
207 HP ground-water,ex apart | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP ground-water,ex apart | 24. Sparenergi.dk, 2015
207 HP ground-water,ex apart | 25. Energinet.dk, 2015, conversation
207 HP ground-water,ex apart | 26. Cronborg, 2015, conversation
207 HP ground-water,ex apart | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP ground-water,ex apart | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP ground-water,ex apart | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP ground-water,new single | 1. Interviews with various installation companies.
207 HP ground-water,new single | 2. Teknologisk Institute.
207 HP ground-water,new single | 3. Installation company
207 HP ground-water,new single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP ground-water,new single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,new single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP ground-water,new single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP ground-water,new single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP ground-water,new single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP ground-water,new single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP ground-water,new single | 11. Bosch 2020, conversation
207 HP ground-water,new single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP ground-water,new single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP ground-water,new single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,new single | 15. ENS heat pump sale statistics
207 HP ground-water,new single | 16. Danfoss, 2015, information provided at workshop
207 HP ground-water,new single | 17. Bosch, 2015 , information provided at workshop
207 HP ground-water,new single | 18. Market and Statistics Report, EHPA 2014
207 HP ground-water,new single | 19. Energistyrelsen, 2015, conversation
207 HP ground-water,new single | 20. Teknologisk Institut, 2015, conversation
207 HP ground-water,new single | 21. Nilan, 2015, conversation
207 HP ground-water,new single | 22. Genvex, 2015, conversation
207 HP ground-water,new single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP ground-water,new single | 24. Sparenergi.dk, 2015
207 HP ground-water,new single | 25. Energinet.dk, 2015, conversation
207 HP ground-water,new single | 26. Cronborg, 2015, conversation
207 HP ground-water,new single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP ground-water,new single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP ground-water,new single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP ground-water,new apart | 1. Interviews with various installation companies.
207 HP ground-water,new apart | 2. Teknologisk Institute.
207 HP ground-water,new apart | 3. Installation company
207 HP ground-water,new apart | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP ground-water,new apart | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,new apart | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP ground-water,new apart | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP ground-water,new apart | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP ground-water,new apart | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP ground-water,new apart | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP ground-water,new apart | 11. Bosch 2020, conversation
207 HP ground-water,new apart | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP ground-water,new apart | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP ground-water,new apart | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ground-water,new apart | 15. ENS heat pump sale statistics
207 HP ground-water,new apart | 16. Danfoss, 2015, information provided at workshop
207 HP ground-water,new apart | 17. Bosch, 2015 , information provided at workshop
207 HP ground-water,new apart | 18. Market and Statistics Report, EHPA 2014
207 HP ground-water,new apart | 19. Energistyrelsen, 2015, conversation
207 HP ground-water,new apart | 20. Teknologisk Institut, 2015, conversation
207 HP ground-water,new apart | 21. Nilan, 2015, conversation
207 HP ground-water,new apart | 22. Genvex, 2015, conversation
207 HP ground-water,new apart | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP ground-water,new apart | 24. Sparenergi.dk, 2015
207 HP ground-water,new apart | 25. Energinet.dk, 2015, conversation
207 HP ground-water,new apart | 26. Cronborg, 2015, conversation
207 HP ground-water,new apart | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP ground-water,new apart | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP ground-water,new apart | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP air-air,ex single | 1. Interviews with various installation companies.
207 HP air-air,ex single | 2. Teknologisk Institute.
207 HP air-air,ex single | 3. Installation company
207 HP air-air,ex single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-air,ex single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-air,ex single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-air,ex single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-air,ex single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-air,ex single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-air,ex single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-air,ex single | 11. Bosch 2020, conversation
207 HP air-air,ex single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-air,ex single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-air,ex single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-air,ex single | 15. ENS heat pump sale statistics
207 HP air-air,ex single | 16. Danfoss, 2015, information provided at workshop
207 HP air-air,ex single | 17. Bosch, 2015 , information provided at workshop
207 HP air-air,ex single | 18. Market and Statistics Report, EHPA 2014
207 HP air-air,ex single | 19. Energistyrelsen, 2015, conversation
207 HP air-air,ex single | 20. Teknologisk Institut, 2015, conversation
207 HP air-air,ex single | 21. Nilan, 2015, conversation
207 HP air-air,ex single | 22. Genvex, 2015, conversation
207 HP air-air,ex single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-air,ex single | 24. Sparenergi.dk, 2015
207 HP air-air,ex single | 25. Energinet.dk, 2015, conversation
207 HP air-air,ex single | 26. Cronborg, 2015, conversation
207 HP air-air,ex single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-air,ex single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-air,ex single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP air-air,new single | 1. Interviews with various installation companies.
207 HP air-air,new single | 2. Teknologisk Institute.
207 HP air-air,new single | 3. Installation company
207 HP air-air,new single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP air-air,new single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-air,new single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP air-air,new single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP air-air,new single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP air-air,new single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP air-air,new single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP air-air,new single | 11. Bosch 2020, conversation
207 HP air-air,new single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP air-air,new single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP air-air,new single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP air-air,new single | 15. ENS heat pump sale statistics
207 HP air-air,new single | 16. Danfoss, 2015, information provided at workshop
207 HP air-air,new single | 17. Bosch, 2015 , information provided at workshop
207 HP air-air,new single | 18. Market and Statistics Report, EHPA 2014
207 HP air-air,new single | 19. Energistyrelsen, 2015, conversation
207 HP air-air,new single | 20. Teknologisk Institut, 2015, conversation
207 HP air-air,new single | 21. Nilan, 2015, conversation
207 HP air-air,new single | 22. Genvex, 2015, conversation
207 HP air-air,new single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP air-air,new single | 24. Sparenergi.dk, 2015
207 HP air-air,new single | 25. Energinet.dk, 2015, conversation
207 HP air-air,new single | 26. Cronborg, 2015, conversation
207 HP air-air,new single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP air-air,new single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP air-air,new single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP ventilation,new single | 1. Interviews with various installation companies.
207 HP ventilation,new single | 2. Teknologisk Institute.
207 HP ventilation,new single | 3. Installation company
207 HP ventilation,new single | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP ventilation,new single | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ventilation,new single | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP ventilation,new single | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP ventilation,new single | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP ventilation,new single | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP ventilation,new single | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP ventilation,new single | 11. Bosch 2020, conversation
207 HP ventilation,new single | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP ventilation,new single | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP ventilation,new single | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ventilation,new single | 15. ENS heat pump sale statistics
207 HP ventilation,new single | 16. Danfoss, 2015, information provided at workshop
207 HP ventilation,new single | 17. Bosch, 2015 , information provided at workshop
207 HP ventilation,new single | 18. Market and Statistics Report, EHPA 2014
207 HP ventilation,new single | 19. Energistyrelsen, 2015, conversation
207 HP ventilation,new single | 20. Teknologisk Institut, 2015, conversation
207 HP ventilation,new single | 21. Nilan, 2015, conversation
207 HP ventilation,new single | 22. Genvex, 2015, conversation
207 HP ventilation,new single | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP ventilation,new single | 24. Sparenergi.dk, 2015
207 HP ventilation,new single | 25. Energinet.dk, 2015, conversation
207 HP ventilation,new single | 26. Cronborg, 2015, conversation
207 HP ventilation,new single | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP ventilation,new single | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP ventilation,new single | 29. SCOP values from "Varmepumpelisten" and supplier websites.
207 HP ventilation,new apart | 1. Interviews with various installation companies.
207 HP ventilation,new apart | 2. Teknologisk Institute.
207 HP ventilation,new apart | 3. Installation company
207 HP ventilation,new apart | 4. Dialogue with heat pump experts at Danish Technological Institute, 2020
207 HP ventilation,new apart | 5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ventilation,new apart | 6. "Den Lille Blå om Varmepumper" published by elforsk.dk
207 HP ventilation,new apart | 7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
207 HP ventilation,new apart | 8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
207 HP ventilation,new apart | 9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
207 HP ventilation,new apart | 10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
207 HP ventilation,new apart | 11. Bosch 2020, conversation
207 HP ventilation,new apart | 12. DVI (Dansk Varmepumpe Industri) 2020, conversation
207 HP ventilation,new apart | 13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
207 HP ventilation,new apart | 14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
207 HP ventilation,new apart | 15. ENS heat pump sale statistics
207 HP ventilation,new apart | 16. Danfoss, 2015, information provided at workshop
207 HP ventilation,new apart | 17. Bosch, 2015 , information provided at workshop
207 HP ventilation,new apart | 18. Market and Statistics Report, EHPA 2014
207 HP ventilation,new apart | 19. Energistyrelsen, 2015, conversation
207 HP ventilation,new apart | 20. Teknologisk Institut, 2015, conversation
207 HP ventilation,new apart | 21. Nilan, 2015, conversation
207 HP ventilation,new apart | 22. Genvex, 2015, conversation
207 HP ventilation,new apart | 23. Heat implementation scenarios until 2030, Ecofys 2013
207 HP ventilation,new apart | 24. Sparenergi.dk, 2015
207 HP ventilation,new apart | 25. Energinet.dk, 2015, conversation
207 HP ventilation,new apart | 26. Cronborg, 2015, conversation
207 HP ventilation,new apart | 27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
207 HP ventilation,new apart | 28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
207 HP ventilation,new apart | 29. SCOP values from "Varmepumpelisten" and supplier websites.
215 Solar heating,ex single | 1. Solvarme faktablade, www.altomsolvarme.dk.
215 Solar heating,ex single | 6. Recommendation: Converting solar thermal collector area into installed capacity (m2 to kWth). Technical note, IEA SHC 2004.
215 Solar heating,ex apart | 1. Solvarme faktablade, www.altomsolvarme.dk.
215 Solar heating,new single | 1. Solvarme faktablade, www.altomsolvarme.dk.
215 Solar heating,new apart | 1. Solvarme faktablade, www.altomsolvarme.dk.
216 Electric heating,new single | 4. Peter Strøm from “EL-Strøm A/S”, personnaly communication.
216 Electric heating,new single | 5. Based on data from interviews with installers during creation of this data sheet
216 Electric heating,new apart | 4. Peter Strøm from “EL-Strøm A/S”, personnaly communication.
216 Electric heating,new apart | 5. Based on data from interviews with installers during creation of this data sheet

## 201 Oil boiler, ex single
Technology |  | Oil boiler (mineral oil fired, < 10 % FAME) - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 20 | 20 | 20 | 20 | 20 | 13 | 30 | 13 | 30 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.92 | 0.92 | 0.93 | 0.94 | 0.95 | 0.92 | 0.95 | 0.92 | 0.98 | N | 1,2,3,4,14
| Auxiliary Electricity consumption [kWh_e/y] | 140 | 130 | 120 | 115 | 110 | 100 | 160 | 90 | 150 | M | 11
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
| Primary regulation (per 30 seconds) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary regulation (per minute) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Minimum load (of full load) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
| SO2 [g/GJ_i] | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 0 | 10 | 0 | 10 | B,E
| PM2.5 [g/GJ_i] | 5 | 5 | 5 | 5 | 5 | 0 | 10 | 0 | 10 | E
| NOX [g/GJ_i] | 52 | 52 | 52 | 52 | 52 | 0 | 100 | 0 | 100 | C,E | 5
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 5.6 | 5.4936 | 5.3898 | 5.1898 | 4.9997 | 4.6695 | 6.8137 | 4.2497 | 6.2496 | F, H, J
| Nominal investment (equipment) [k€/unit, 2020] | 4.3 | 4.1936 | 4.0898 | 3.8898 | 3.6997 | 3.5645 | 5.2013 | 3.1447 | 4.6246 | H
| Nominal investment (installation) [k€/unit, 2020] | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.105 | 1.6124 | 1.105 | 1.625 | H
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 184.5808 | 181.3466 | 178.7321 | 169.6216 | 160.4311 | 154.2782 | 217.5651 | 136.2891 | 192.9151
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 9.66 | 11.05 | 12.12 | 12.535 | 12.87 | 8.5 | 13.6 | 10.53 | 17.55 | M
| Fixed O&M (other) [€/unit/y, 2020] | 174.9208 | 170.2966 | 166.6121 | 157.0866 | 147.5611 | 145.7782 | 203.9651 | 125.7591 | 175.3651
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
3. BOILSIM http://www.boilsim.com/.2011
4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
5. http://www.blauer-engel.de/_downloads/publikationen/erfolgsbilanz/ Erfolgsbilanz_Heiztechnologien.pdf (Rules for NOX). This is not present at the Blauer Engel Homepage, but can be found at the Internet.2011
11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
Notes:
A. The minimum heat output for a pressure atomisation burner is in the range of 13 kW. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity below 13 kW is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
B. Domestic fuel oil can be desulphoried to the lower than 10 ppm Sulpur
C. The last limit for Nox for Blaue Engel were 110 mg/kWh. The value is based on this. In Practise the value can be lower. In 2050 is assumed flue gas cleaning for Nox
E. Data for emissions can be found at emission inventories envs.au.dk
F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons. In the case HVO becomes feasible condensing technology will work well
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]

## 201 Oil boiler, ex apart
Technology |  | Oil boiler (mineral oil fired, < 10 % FAME) - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | A, I
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to -
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to -
| Heat efficiency (annual average, net) [p.u.] | 0.92 | 0.92 | 0.93 | 0.94 | 0.95 | 0.92 | 0.95 | 0.92 | 0.98 | G, N | 1, 2, 3, 4, 14
| Auxiliary Electricity consumption [kWh_e/y] | 1400 | 1350 | 1300 | 1250 | 1200 | 1000 | 1800 | 500 | 1500 | M | 11
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
| Primary regulation (per 30 seconds) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary regulation (per minute) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Minimum load (of full load) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
| SO2 [g/GJ_i] | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 0 | 10 | 0 | 10 | B,E
| PM2.5 [g/GJ_i] | 5 | 5 | 5 | 5 | 5 | 0 | 10 | 0 | 10 | E
| NOX [g/GJ_i] | 52 | 52 | 52 | 52 | 52 | 0 | 100 | 0 | 100 | C,E
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 32.6025 | 31.7955 | 31.0086 | 29.4926 | 28.0507 | 27.0262 | 38.1547 | 23.8431 | 33.6608 | F, H, J
| Nominal investment (equipment) [k€/unit, 2020] | 26.082 | 25.4364 | 24.8069 | 23.5941 | 22.4405 | 21.621 | 30.5237 | 19.0745 | 26.9286
| Nominal investment (installation) [k€/unit, 2020] | 6.5205 | 6.3591 | 6.2017 | 5.8985 | 5.6101 | 5.4052 | 7.6309 | 4.7686 | 6.7322
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 1038.8081 | 1042.8305 | 1057.9309 | 1067.6258 | 1076.5208 | 888.2819 | 1249.1074 | 903.5503 | 1293.151
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 96.6 | 114.75 | 131.3 | 136.25 | 140.4 | 85 | 153 | 58.5 | 175.5
| Fixed O&M (other) [€/unit/y, 2020] | 942.2081 | 928.0805 | 926.6309 | 931.3758 | 936.1208 | 803.2819 | 1096.1074 | 845.0503 | 1117.651
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
3. BOILSIM http://www.boilsim.com/.2011
4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
7. Rapsolie til opvarmning,Teknik, økonomi og miljø. Videncentret for biomasse 2001.
11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
Notes:
A. The minimum heat output for a pressure atomisation burner is in the range of 13 kW. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity below 13 kW is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
B. Domestic fuel oil can be desulphoried to the lower than 10 ppm Sulpur
C. The last limit for Nox for Blaue Engel were 110 mg/kWh. The value is based on this. In Practise the value can be lower. In 2050 is assumed flue gas cleaning for Nox
E. Data for emissions can be found at emission inventories envs.au.dk
F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons.
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]

## 201 Oil boiler, new single
Technology |  | Oil boiler (bio oil) - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 | A, I
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to -
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to -
| Heat efficiency (annual average, net) [p.u.] | 0.88 | 0.9 | 0.92 | 0.93 | 0.94 | 0.85 | 0.95 | 0.9 | 0.98 | G, N | 1, 2, 3, 4, 14
| Auxiliary Electricity consumption [kWh_e/y] | 100 | 95 | 90 | 82 | 75 | 75 | 125 | 60 | 100 | M | 11
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
| Primary regulation (per 30 seconds) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary regulation (per minute) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Minimum load (of full load) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
| SO2 [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 1 | 0 | 1 | E
| PM2.5 [g/GJ_i] | 5 | 5 | 5 | 5 | 5 | 0 | 10 | 0 | 10 | E
| NOX [g/GJ_i] | 52 | 52 | 52 | 52 | 52 | 0 | 100 | 0 | 100 | E
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 7 | 6.8267 | 6.6578 | 6.3323 | 6.0227 | 5.8027 | 8.1921 | 5.1193 | 7.2272 | F, H, J,
| Nominal investment (equipment) [k€/unit, 2020] | 4.9 | 4.7787 | 4.6604 | 4.4326 | 4.2159 | 4.0619 | 5.7345 | 3.5835 | 5.0591
| Nominal investment (installation) [k€/unit, 2020] | 2.1 | 2.048 | 1.9973 | 1.8997 | 1.8068 | 1.7408 | 2.4576 | 1.5358 | 2.1682
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 185.5577 | 181.7918 | 178.5491 | 169.1563 | 159.6576 | 154.5961 | 218.0102 | 135.626 | 191.8101
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 6.9 | 8.075 | 9.09 | 8.938 | 8.775 | 6.375 | 10.625 | 7.02 | 11.7
| Fixed O&M (other) [€/unit/y, 2020] | 178.6577 | 173.7168 | 169.4591 | 160.2183 | 150.8826 | 148.2211 | 207.3852 | 128.606 | 180.1101
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
3. BOILSIM http://www.boilsim.com/.2011
4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
Notes:
A. The minimum heat output for a pressure atomisation burner is in the range of 13 kW. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity below 13 kW is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
E. Data for emissions can be found at emission inventories envs.au.dk
F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons.
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]

## 201 Oil boiler, new apart
Technology |  | Oil boiler (bio oil) - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 100 | 1000 | 100 | 1000
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.88 | 0.9 | 0.92 | 0.93 | 0.94 | 0.85 | 0.95 | 0.9 | 0.98 | N, G | 1,2,3,4,14
| Auxiliary Electricity consumption [kWh_e/y] | 900 | 750 | 520 | 500 | 480 | 400 | 900 | 200 | 600 | M | 11
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
| Primary regulation (per 30 seconds) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary regulation (per minute) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Minimum load (of full load) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
| SO2 [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 1 | 0 | 1 | E
| PM2.5 [g/GJ_i] | 5 | 5 | 5 | 5 | 5 | 0 | 10 | 0 | 10 | E
| NOX [g/GJ_i] | 52 | 52 | 52 | 52 | 52 | 0 | 100 | 0 | 100 | E
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 26.082 | 25.4364 | 24.8069 | 23.5941 | 22.4405 | 21.621 | 30.5237 | 19.0745 | 26.9286 | F, H, K, J, O
| Nominal investment (equipment) [k€/unit, 2020] | 18.2574 | 17.8055 | 17.3648 | 16.5158 | 15.7084 | 15.1347 | 21.3666 | 13.3521 | 18.8501
| Nominal investment (installation) [k€/unit, 2020] | 7.8246 | 7.6309 | 7.4421 | 7.0782 | 6.7322 | 6.4863 | 9.1571 | 5.7223 | 8.0786
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 751.0195 | 740.4614 | 733.1723 | 737.0503 | 740.6083 | 632.4128 | 906.143 | 624.9201 | 889.2604 | M
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 62.1 | 63.75 | 52.52 | 54.5 | 56.16 | 34 | 76.5 | 23.4 | 70.2
| Fixed O&M (other) [€/unit/y, 2020] | 688.9195 | 676.7114 | 680.6523 | 682.5503 | 684.4483 | 598.4128 | 829.643 | 601.5201 | 819.0604
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
2. RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
3. BOILSIM http://www.boilsim.com/.2011
4. Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
11. Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
14. Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
Notes:
E. Data for emissions can be found at emission inventories envs.au.dk
F. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
G. Burners for liqued raw biofuel is not suited for condensing boilers for different reasons.
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
J. Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
M. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]
O. Investment cost for 2020 have been estimated based on a survey of publicly offered prices and interviews with installers. Data has been collected during October and November 2020.

## 202 Gas boiler, ex single
Technology |  | Natural gas boiler - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | U
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.97 | 0.97 | 0.98 | 0.99 | 0.99 | 0.95 | 1 | 0.98 | 1.02 | A, B, M | 1,4, 28
| Auxiliary Electricity consumption [kWh_e/y] | 140 | 130 | 120 | 110 | 100 | 100 | 160 | 90 | 150 | T | 28
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 18 | 22 | 18 | 22 |  | 2, 29
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: -
Secondary regulation (per minute) [p.u.] | bar: -
Minimum load (of full load) [p.u.] | bar: -
Warm start-up time [hours] | bar: -
Cold start-up time [hours] | bar: -
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | G, | 5
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | D, E, G | 3.7
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | F, G | 5
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 3.9 | 3.8035 | 3.7093 | 3.528 | 3.3555 | 3.2329 | 4.5642 | 2.8522 | 4.0266 | V, C
| Nominal investment (equipment) [k€/unit, 2020] | 2.73 | 2.6624 | 2.5965 | 2.4696 | 2.3488 | 2.2631 | 3.1949 | 1.9965 | 2.8186
| Nominal investment (installation) [k€/unit, 2020] | 1.17 | 1.141 | 1.1128 | 1.0584 | 1.0066 | 0.96988 | 1.3692 | 0.85565 | 1.208
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | K
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 191.5808 | 188.3466 | 186.7321 | 176.5511 | 170.2101 | 160.2282 | 225.9651 | 144.7891 | 204.9151 | J | 33
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 9.66 | 11.05 | 12.12 | 11.99 | 11.7 | 8.5 | 13.6 | 10.53 | 17.55 | T
| Fixed O&M (other) [€/unit/y, 2020] | 181.9208 | 177.2966 | 174.6121 | 164.5611 | 158.5101 | 151.7282 | 212.3651 | 134.2591 | 187.3651
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
2. Facts and figures about domestic gas boilers. Compilation of results covering 25 years of testing at DGC's laboratory February 2016, updated 2017.Jean Schweitzer, DGC
3. Study "Ecodesign of Boilers and Combi-boilers" (VHK) for the European Commission, DG Transport and Energy (DG TREN). Task 4 Section 3.1.
4. DGC, 2020 "Dokumentation af villagaskedlers faktiske virkningsgrader". Projektrapport.
5. Start stop emissions of domestic appliances. H. Hüppelshäuser and F. Jansen. Ruhrgas. IGRC 1998.
6. HMN: http://salg.naturgas.dk.
7. DGC project : Evaluation of the NOx emissions of the Danish population of gas boilers below 120 kW
28. Facts and figures about domestic gas boilers. A compilation of results covering 25 years of testing at DGC's laboratory. DGC February 2016
29. Investigations on 25 gas boilers lifetime with HMN boiler statistics. 743-48 Jean Schweitzer, DGC Sept. 2016
30. DGC Statistics, Efficiency and Emission test reports from district heating plants, up to and including 2014
31. Danish District Heating Association, information given to the 2012 survey for the report
Notes:
A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1] and observed efficiences for condensing boilers according to [4]. Efficiencies of the condensing gas boiler is approx. 99 % but when accounting for heat losses from the hot water tank of approx. 2 %, a net efficiency for the system of approx. 97 % is obtained.
B. A slight improvement of efficiency is still possible over the next decades is assumed
C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
F. Ref [5] gives 5 mg/kWh, This is less than 2 g/GJ.
G. Data for emissions can be found at emission inventories envs.au.dk
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies. The harmonisation of gas quality in EU, the more severe competition with district heating and electrical heat pumps, and the improvements in the manufacturing cost are the reason for such hypothesis. The statistics of Naturgas Fyn (today "NGF Nature Energy") shows that the costs have already decreased between 2012 and 2015.
J. This assumes a service agreement costing 127 €/a excluding VAT and approx. 55 €/a on average for spare parts .
K. Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
U. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity of the boilers is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
V. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.

## 202 Gas boiler, ex apart
Technology |  | Natural gas boiler - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 400 | 400 | 400 | 400 | 400 | 300 | 500 | 300 | 500
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 0.99 | 1.03 | 1 | 1.04 | A,B,L,O,P,M | 30, 31
| Auxiliary Electricity consumption [kWh_e/y] | 700 | 650 | 600 | 550 | 500 | 500 | 1000 | 250 | 750 | T,M | 30
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 | M | 31
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: -
Secondary regulation (per minute) [p.u.] | bar: -
Minimum load (of full load) [p.u.] | bar: -
Warm start-up time [hours] | bar: -
Cold start-up time [hours] | bar: -
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | N, G
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | N, G | 3.7
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | F,N,G,D
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | N, G
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | N, G
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 27.4738 | 26.8928 | 26.3262 | 25.2346 | 24.1965 | 19.5942 | 38.3392 | 17.8753 | 34.2947 | C
| Nominal investment (equipment) [k€/unit, 2020] | 21.979 | 21.5142 | 21.0609 | 20.1877 | 19.3572 | 15.6753 | 30.6714 | 14.3002 | 27.4358
| Nominal investment (installation) [k€/unit, 2020] | 5.4948 | 5.3786 | 5.2652 | 5.0469 | 4.8393 | 3.9188 | 7.6678 | 3.5751 | 6.8589
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 6
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 665.904 | 660.7332 | 654.6604 | 627.7554 | 179.0503 | 562.2909 | 790.0819 | 148.3252 | 218.1755 | C, O, P, S
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 48.3 | 55.25 | 60.6 | 59.95 | 58.5 | 42.5 | 85 | 29.25 | 87.75
| Fixed O&M (other) [€/unit/y, 2020] | 617.604 | 605.4832 | 594.0604 | 567.8054 | 120.5503 | 519.7909 | 705.0819 | 119.0752 | 130.4255
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
6. HMN: http://salg.naturgas.dk.
7. DGC project : Evaluation of the NOx emissions of the Danish population of gas boilers below 120 kW
30. DGC Statistics, Efficiency and Emission test reports from district heating plants, up to and including 2014
31. Danish District Heating Association, information given to the 2012 survey for the report
Notes:
A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
B. A slight improvement of efficiency is still possible over the next decades is assumed
C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
G. Data for emissions can be found at emission inventories envs.au.dk
L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
N. The emissions are assumed to be very similar to the ones for domestic boilers. This is believed to be a conservative estimate.
O. Based on a 160 kW boiler (new building) and 400 kW (existing building)
Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
U. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity of the boilers is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.

## 202 Gas boiler, new single
Technology |  | Natural gas boiler - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 14 | 14 | 14 | 14 | 14 | 10 | 20 | 10 | 20 | U
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.97 | 0.97 | 0.98 | 0.99 | 0.99 | 0.95 | 1 | 0.98 | 1.02 | A, B | 1.28
| Auxiliary Electricity consumption [kWh_e/y] | 140 | 130 | 120 | 110 | 100 | 100 | 160 | 90 | 150 | T | 28
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 18 | 22 | 18 | 22 |  | 2, 29
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: -
Secondary regulation (per minute) [p.u.] | bar: -
Minimum load (of full load) [p.u.] | bar: -
Warm start-up time [hours] | bar: -
Cold start-up time [hours] | bar: -
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | G,
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | D, E, G | 3
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | F, G | 5
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 3.9 | 3.8035 | 3.7093 | 3.528 | 3.3555 | 2.3092 | 6.5202 | 2.0373 | 5.7523 | V, C
| Nominal investment (equipment) [k€/unit, 2020] | 2.73 | 2.6624 | 2.5965 | 2.4696 | 2.3488 | 1.6165 | 4.5642 | 1.4261 | 2.8186
| Nominal investment (installation) [k€/unit, 2020] | 1.17 | 1.141 | 1.1128 | 1.0584 | 1.0066 | 0.69277 | 1.9561 | 0.61118 | 1.208
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 1.4286 | 2.8571 | 1.4286 | 2.8571 |  | 6
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 191.5808 | 188.3466 | 186.7321 | 176.5511 | 170.2101 | 160.2282 | 225.9651 | 144.7891 | 204.9151 | J | 33
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 9.66 | 11.05 | 12.12 | 11.99 | 11.7 | 8.5 | 13.6 | 10.53 | 17.55
| Fixed O&M (other) [€/unit/y, 2020] | 181.9208 | 177.2966 | 174.6121 | 164.5611 | 158.5101 | 151.7282 | 212.3651 | 134.2591 | 187.3651
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
2. Facts and figures about domestic gas boilers. Compilation of results covering 25 years of testing at DGC's laboratory February 2016, updated 2017.Jean Schweitzer, DGC
3. Study "Ecodesign of Boilers and Combi-boilers" (VHK) for the European Commission, DG Transport and Energy (DG TREN). Task 4 Section 3.1.
5. Start stop emissions of domestic appliances. H. Hüppelshäuser and F. Jansen. Ruhrgas. IGRC 1998.
6. HMN: http://salg.naturgas.dk.
28. Facts and figures about domestic gas boilers. A compilation of results covering 25 years of testing at DGC's laboratory. DGC February 2016
29. Investigations on 25 gas boilers lifetime with HMN boiler statistics. 743-48 Jean Schweitzer, DGC Sept. 2016
33. Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
Notes:
A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
B. A slight improvement of efficiency is still possible over the next decades is assumed
C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
E. NOx emission will decrease as an average. The level proposed for 2030 is already achievable today by some gas boilers.
F. Ref [5] gives 5 mg/kWh, This is less than 2 g/GJ.
G. Data for emissions can be found at emission inventories envs.au.dk
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies. The harmonisation of gas quality in EU, the more severe competition with district heating and electrical heat pumps, and the improvements in the manufacturing cost are the reason for such hypothesis. The statistics of Naturgas Fyn (today "NGF Nature Energy") shows that the costs have already decreased between 2012 and 2015.
J. This assumes a service agreement costing 127 €/a excluding VAT and approx. 55 €/a on average for spare parts .
L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
V. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.

## 202 Gas boiler, new apart
Technology |  | Natural gas boiler - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 100 | 200 | 100 | 200
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1.01 | 1.01 | 1.02 | 1.02 | 1.02 | 0.99 | 1.03 | 1 | 1.04 | A,B,L,O,P,M | 30, 31, 1
| Auxiliary Electricity consumption [kWh_e/y] | 700 | 650 | 600 | 550 | 500 | 500 | 1000 | 250 | 750 | T,M
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 | M | 31
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: -
Secondary regulation (per minute) [p.u.] | bar: -
Minimum load (of full load) [p.u.] | bar: -
Warm start-up time [hours] | bar: -
Cold start-up time [hours] | bar: -
Environment |  | -: 3.7
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | N
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | N
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | F,N
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | N
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | N
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 22.68 | 22.1186 | 21.5712 | 20.5166 | 19.5135 | 18.8008 | 26.5424 | 16.5865 | 23.4162 | C, O, P
| Nominal investment (equipment) [k€/unit, 2020] | 15.876 | 15.483 | 15.0998 | 14.3616 | 13.6595 | 13.1606 | 18.5797 | 11.6105 | 16.3914
| Nominal investment (installation) [k€/unit, 2020] | 6.804 | 6.6356 | 6.4714 | 6.155 | 5.8541 | 5.6403 | 7.9627 | 4.9759 | 7.0249
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 33
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 665.904 | 660.7332 | 654.6604 | 627.7554 | 179.0503 | 562.2909 | 790.0819 | 148.3252 | 218.1755 | C, O, P, S
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 48.3 | 55.25 | 60.6 | 59.95 | 58.5 | 42.5 | 85 | 29.25 | 87.75
| Fixed O&M (other) [€/unit/y, 2020] | 617.604 | 605.4832 | 594.0604 | 567.8054 | 120.5503 | 519.7909 | 705.0819 | 119.0752 | 130.4255
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
1. Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
31. Danish District Heating Association, information given to the 2012 survey for the report
33. Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
Notes:
A. Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
B. A slight improvement of efficiency is still possible over the next decades is assumed
C. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
D. Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
E. NOx emission will decrease as an average. The level proposed for 2030 is already achievable today by some gas boilers.
K. Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L. Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
M. The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
N. The emissions are assumed to be very similar to the ones for domestic boilers. This is believed to be a conservative estimate.
O. Based on a 160 kW boiler (new building) and 400 kW (existing building)
P. Investment cost for 2020 have been estimated based on three sources: 1) survey of publicly offered prices, 2) interviews with installers, 3) data from the energy savings obligation provided by the Danish Energy Agency. Data has been collected during October and November 2020.
Q. There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
S. Service cost interpolated from manufacturers information (2020)
T. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 203 DH indirect,new single
Technology |  | Indirect district heating substation - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 12 | 12 | 12 | 12 | 12 | 5 | 15 | 5 | 15 | H
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.96 | 0.96 | 0.97 | 0.97 | 0.98 | 0.95 | 0.99 | 0.95 | 0.99 | B, I | 9
| Auxiliary Electricity consumption [kWh_e/y] | 60 | 55 | 50 | 40 | 35 | 40 | 80 | 25 | 75 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.41 | 2.34 | 2.28 | 2.15 | 2.03 | 2.0485 | 3.5 | 1.7255 | 3.25 | F | 10
| Nominal investment (equipment) [k€/unit, 2020] | 1.687 | 1.638 | 1.596 | 1.505 | 1.421 | 1.434 | 2.45 | 1.2078 | 2.275
| Nominal investment (installation) [k€/unit, 2020] | 0.723 | 0.702 | 0.684 | 0.645 | 0.609 | 0.61455 | 1.05 | 0.51765 | 0.975
| Nominal investment (additional) [k€/unit, 2020] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C, E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 53.14 | 52.175 | 51.05 | 48.36 | 46.095 | 40.4 | 69.8 | 32.925 | 68.775 | D, F | 8
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 4.14 | 4.675 | 5.05 | 4.36 | 4.095 | 3.4 | 6.8 | 2.925 | 8.775
| Fixed O&M (other) [€/unit/y, 2020] | 49 | 47.5 | 46 | 44 | 42 | 37 | 63 | 30 | 60
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
10. Interview with market actors and web price survey, 2020
Notes:
B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203 DH indirect,ex single
Technology |  | Indirect district heating substation - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 12 | 12 | 12 | 12 | 12 | 5 | 30 | 5 | 30 | H
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.96 | 0.96 | 0.97 | 0.97 | 0.98 | 0.95 | 0.99 | 0.95 | 0.99 | B, I | 9
| Auxiliary Electricity consumption [kWh_e/y] | 120 | 110 | 100 | 80 | 75 | 50 | 125 | 50 | 100 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.41 | 2.34 | 2.28 | 2.15 | 2.03 | 2.0485 | 3.5 | 1.7255 | 3.25 | F | 10
| Nominal investment (equipment) [k€/unit, 2020] | 1.2773 | 1.2402 | 1.2084 | 1.1395 | 1.0759 | 1.0857 | 1.855 | 0.91451 | 1.7225
| Nominal investment (installation) [k€/unit, 2020] | 1.1327 | 1.0998 | 1.0716 | 1.0105 | 0.9541 | 0.9628 | 1.645 | 0.81098 | 1.5275
| Nominal investment (additional) [k€/unit, 2020] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 46.0693 | 45.601 | 46.6101 | 45.1281 | 43.6576 | 39.3141 | 54.8102 | 36.805 | 52.6101
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 8.28 | 9.35 | 10.1 | 8.72 | 8.775 | 4.25 | 10.625 | 5.85 | 11.7
| Fixed O&M (other) [€/unit/y, 2020] | 37.7893 | 36.251 | 36.5101 | 36.4081 | 34.8826 | 35.0641 | 44.1852 | 30.955 | 40.9101 | C, F
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
10. Interview with market actors and web price survey, 2020
Notes:
B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203 DH indirect,ex apart
Technology |  | Indirect district heating substation - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 400 | 400 | 400 | 400 | 400 | 150 | 500 | 150 | 500 | A, H
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.98 | 1 | B, I
| Auxiliary Electricity consumption [kWh_e/y] | 600 | 550 | 500 | 450 | 400 | 400 | 1000 | 250 | 800 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 16.56 | 16.1501 | 15.7504 | 14.9803 | 14.248 | 13.7276 | 19.3801 | 12.1108 | 17.0976 | F | 2, 4, 7, 10
| Nominal investment (equipment) [k€/unit, 2020] | 11.592 | 11.3051 | 11.0253 | 10.4862 | 9.9736 | 9.6093 | 13.5661 | 8.4775 | 11.9683
| Nominal investment (installation) [k€/unit, 2020] | 4.968 | 4.845 | 4.7251 | 4.4941 | 4.2744 | 4.1183 | 5.814 | 3.6332 | 5.1293
| Nominal investment (additional) [k€/unit, 2020] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | C, E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 140.4 | 143.25 | 144.5 | 138.55 | 131.8 | 110.5 | 201.5 | 94.25 | 198.6 | D
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 41.4 | 46.75 | 50.5 | 49.05 | 46.8 | 34 | 85 | 29.25 | 93.6
| Fixed O&M (other) [€/unit/y, 2020] | 99 | 96.5 | 94 | 89.5 | 85 | 76.5 | 116.5 | 65 | 105
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
2. Communication with Gemina Termix, www.termix.dk. 2011
4. Communication with Danfoss Redan, www.redan.danfoss.com. Technology data for individual heat production and energy transport, 2011
7. Prices from different providers of substations, 2016
8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
10. Interview with market actors and web price survey, 2020
Notes:
A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203 DH indirect,new apart
Technology |  | Indirect district heating substation - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 150 | 500 | 150 | 500 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.98 | 1 | B, I
| Auxiliary Electricity consumption [kWh_e/y] | 350 | 325 | 300 | 250 | 250 | 250 | 500 | 200 | 400 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 11.592 | 11.3051 | 11.0253 | 10.4862 | 9.9736 | 9.6093 | 13.5661 | 8.4775 | 11.9683 | F | 2, 4, 7, 10
| Nominal investment (equipment) [k€/unit, 2020] | 8.1144 | 7.9136 | 7.7177 | 7.3404 | 6.9815 | 6.7265 | 9.4963 | 5.9343 | 8.3778
| Nominal investment (installation) [k€/unit, 2020] | 3.4776 | 3.3915 | 3.3076 | 3.1459 | 2.9921 | 2.8828 | 4.0698 | 2.5433 | 3.5905 | C,E
| Nominal investment (additional) [k€/unit, 2020] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 107.15 | 109.125 | 109.3 | 102.25 | 100.25 | 89.25 | 140.5 | 79.4 | 132.8 | D | 8
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 24.15 | 27.625 | 30.3 | 27.25 | 29.25 | 21.25 | 42.5 | 23.4 | 46.8
| Fixed O&M (other) [€/unit/y, 2020] | 83 | 81.5 | 79 | 75 | 71 | 68 | 98 | 56 | 86
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
2. Communication with Gemina Termix, www.termix.dk. 2011
4. Communication with Danfoss Redan, www.redan.danfoss.com. Technology data for individual heat production and energy transport, 2011
7. Prices from different providers of substations, 2016
8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
10. Interview with market actors and web price survey, 2020
Notes:
A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203 DH direct,new single
Technology |  | Direct district heating substation - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 12 | 12 | 12 | 12 | 12 | 5 | 15 | 5 | 15 | H
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.99 | 1 | B, I | 9
| Auxiliary Electricity consumption [kWh_e/y] | 40 | 40 | 35 | 32 | 30 | 30 | 50 | 22.5 | 37.5 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.17 | 2.11 | 2.06 | 1.97 | 1.87 | 1.8445 | 3.5 | 1.5895 | 3.25 | F | 10
| Nominal investment (equipment) [k€/unit, 2020] | 1.0416 | 1.0128 | 0.9888 | 0.9456 | 0.8976 | 0.88536 | 1.68 | 0.76296 | 1.56
| Nominal investment (installation) [k€/unit, 2020] | 1.1284 | 1.0972 | 1.0712 | 1.0244 | 0.9724 | 0.95914 | 1.82 | 0.82654 | 1.69
| Nominal investment (additional) [k€/unit, 2020] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C, E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 48.76 | 48.4 | 47.535 | 45.488 | 42.51 | 37.55 | 64.25 | 26.6325 | 58.3875
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 2.76 | 3.4 | 3.535 | 3.488 | 3.51 | 2.55 | 4.25 | 2.6325 | 4.3875 | F
| Fixed O&M (other) [€/unit/y, 2020] | 46 | 45 | 44 | 42 | 39 | 35 | 60 | 24 | 54 | F
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
10. Interview with market actors and web price survey, 2020. The stated cost represent a situation with competitive pricing.
Notes:
B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.

## 203 DH direct,ex single
Technology |  | Direct district heating substation - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 12 | 12 | 12 | 12 | 12 | 5 | 15 | 5 | 15 | H, J
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.99 | 1 | I | 9
| Auxiliary Electricity consumption [kWh_e/y] | 40 | 40 | 35 | 32 | 30 | 30 | 50 | 22.5 | 37.5 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.17 | 2.11 | 2.06 | 1.97 | 1.87 | 1.8445 | 3.5 | 1.5895 | 3.25 |  | 10
| Nominal investment (equipment) [k€/unit, 2020] | 1.0416 | 1.0128 | 0.9888 | 0.9456 | 0.8976 | 0.88536 | 1.68 | 0.76296 | 1.56
| Nominal investment (installation) [k€/unit, 2020] | 1.1284 | 1.0972 | 1.0712 | 1.0244 | 0.9724 | 0.95914 | 1.82 | 0.82654 | 1.69
| Nominal investment (additional) [k€/unit, 2020] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | C, E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 48.76 | 48.4 | 47.535 | 45.488 | 42.51 | 37.55 | 64.25 | 26.6325 | 58.3875 | D, F | 8
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 2.76 | 3.4 | 3.535 | 3.488 | 3.51 | 2.55 | 4.25 | 2.6325 | 4.3875
| Fixed O&M (other) [€/unit/y, 2020] | 46 | 45 | 44 | 42 | 39 | 35 | 60 | 24 | 54 | J
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
8. Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
10. Interview with market actors and web price survey, 2020. The stated cost represent a situation with competitive pricing.
Notes:
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203 DH direct,ex apart
Technology |  | Direct district heating substation - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 400 | 400 | 400 | 400 | 400 | 150 | 500 | 150 | 500 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.99 | 1 | I | 9
| Auxiliary Electricity consumption [kWh_e/y] | 200 | 200 | 175 | 165 | 150 | 150 | 300 | 125 | 250 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 12.3165 | 12.0117 | 11.7143 | 11.1416 | 10.5969 | 10.2099 | 14.414 | 9.0074 | 12.7163 | D, F | 10
| Nominal investment (equipment) [k€/unit, 2020] | 8.6215 | 8.4082 | 8.2 | 7.7991 | 7.4178 | 7.1469 | 10.0898 | 6.3052 | 8.9014
| Nominal investment (installation) [k€/unit, 2020] | 3.6949 | 3.6035 | 3.5143 | 3.3425 | 3.1791 | 3.063 | 4.3242 | 2.7022 | 3.8149 | E
| Nominal investment (additional) [k€/unit, 2020] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | C, E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 88.8 | 90 | 88.675 | 85.985 | 82.55 | 75.75 | 113.5 | 74.625 | 109.25 |  | 8
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 13.8 | 17 | 17.675 | 17.985 | 17.55 | 12.75 | 25.5 | 14.625 | 29.25
| Fixed O&M (other) [€/unit/y, 2020] | 75 | 73 | 71 | 68 | 65 | 63 | 88 | 60 | 80
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
8. Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
10. Interview with market actors and web price survey, 2020
Notes:
A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203 DH direct,new apart
Technology |  | Direct district heating substation - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 150 | 500 | 150 | 500 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.99 | 1 | I | 9
| Auxiliary Electricity consumption [kWh_e/y] | 200 | 195 | 180 | 175 | 150 | 150 | 300 | 125 | 250 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 8.5 | 8.2896 | 8.0844 | 7.6892 | 7.3133 | 7.0462 | 9.9475 | 6.2163 | 8.7759 | F | 10
| Nominal investment (equipment) [k€/unit, 2020] | 5.95 | 5.8027 | 5.6591 | 5.3824 | 5.1193 | 4.9323 | 6.9633 | 4.3514 | 6.1431
| Nominal investment (installation) [k€/unit, 2020] | 2.55 | 2.4869 | 2.4253 | 2.3068 | 2.194 | 2.1139 | 2.9843 | 1.8649 | 2.6328
| Nominal investment (additional) [k€/unit, 2020] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | C, E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 76.8 | 78.075 | 78.18 | 76.575 | 72.55 | 59.75 | 101.5 | 64.625 | 99.25 | J, D | 8
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 13.8 | 16.575 | 18.18 | 19.075 | 17.55 | 12.75 | 25.5 | 14.625 | 29.25
| Fixed O&M (other) [€/unit/y, 2020] | 63 | 61.5 | 60 | 57.5 | 55 | 47 | 76 | 50 | 70
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
8. Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
9. Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
10. Interview with market actors and web price survey, 2020
Notes:
A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 204 Biomass auto,ex single
Technology |  | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 10 | 10 | 10 | 10 | 8 | 8 | 15 | 6 | 12 | A | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.76 | 0.92 | 0.85 | 0.96 | B, G | 2
| Auxiliary Electricity consumption [kWh_e/y] | 240 | 230 | 220 | 210 | 200 | 180 | 280 | 150 | 250 |  | 4
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 3, 10
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 18 | 32 | 18 | 32 |  | 5
| PM2.5 [g/GJ_i] | 14 | 14 | 11 | 9 | 9 | 8 | 20 | 4 | 14 | C, K, M | 1, 7
| NOX [g/GJ_i] | 70 | 60 | 50 | 45 | 40 | 40 | 80 | 32 | 48
| CH4 [g/GJ_i] | 2 | 2 | 1 | 1 | 0 | 0 | 4 | 0 | 2
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 1 | 7 | 1 | 7 |  | 9
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 4.8645 | 4.7441 | 4.6267 | 4.4005 | 4.1853 | 3.3209 | 6.6417 | 2.9297 | 5.8595 |  | 8
| Nominal investment (equipment) [k€/unit, 2020] | 3.7943 | 3.7004 | 3.6088 | 3.4324 | 3.2646 | 2.5903 | 5.1806 | 2.7749 | 3.9175
| Nominal investment (installation) [k€/unit, 2020] | 1.0702 | 1.0437 | 1.0179 | 0.96811 | 0.92077 | 0.73059 | 1.4612 | 0.78266 | 1.1049
| Nominal investment (additional) [k€/unit, 2020] | 6 | 6 | 6 | 6 | 6 | 5.1 | 7.2 | 5.1 | 7.2
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 374.1385 | 367.6694 | 362.764 | 346.7131 | 331.3661 | 311.2015 | 441.5432 | 279.3212 | 383.411 | I | 6
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 16.56 | 19.55 | 22.22 | 22.89 | 23.4 | 15.3 | 23.8 | 17.55 | 29.25 | J
| Fixed O&M (other) [€/unit/y, 2020] | 357.5785 | 348.1194 | 340.544 | 323.8231 | 307.9661 | 295.9015 | 417.7432 | 261.7712 | 354.161
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 20 | 20 | 20 | 20 | 16 | 8 | 45 | 6 | 36 | N | 9
Technology specific data
References:
1. www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg
2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
3. Lot 15: Solid fuel small combustion installations-Base Case definition
4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
5. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
6. Estimate by the Danish Energy Agency and Energinet, 2017
7. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
8. Interview with market actors and web price survey, 2020
9. Estimate based on user interview, 2020
10. Estimate by Ea Energy Analyses, 2020
Notes:
A. Nominal heat delivered in 2020 from 10-20 kW in single family houses. In small units (20 kW and less) the insignificant economy of scale (se section on economy of scale) the savings achieved by reducing the capacity of the boiler is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boiler installed
B. Efficiency development from [2]
C. EN303-5 measurement method
D. Prerequisite: house with central heating system
E. Chimney
F. Large price span mainly due to finish, design, control features etc.
G. Improved real life conditions for flue gas condensation technology will increase the efficiency to >100% (based on NCV)
H. Fuel storage
I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
L. Including dismantling and disposal of existing boiler
M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
N. For loading fuel manually from bags and removing ash

## 204 Biomass auto,new single
Technology |  | Biomass boiler, automatic stoking , wood pellets or wood chips - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 10 | 8 | 8 | 8 | 8 | 6 | 12 | 6 | 10 | A | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.78 | 0.79 | 0.8 | 0.82 | 0.85 | 0.7 | 0.85 | 0.80485 | 0.95515 | B, G | 2
| Auxiliary Electricity consumption [kWh_e/y] | 190 | 185 | 180 | 170 | 160 | 175 | 250 | 150 | 200 |  | 4
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 3+10
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 18 | 32 | 18 | 32 |  | 5
| PM2.5 [g/GJ_i] | 14 | 14 | 11 | 9 | 9 | 8 | 20 | 4 | 14 | C, K, M | 1+7
| NOX [g/GJ_i] | 70 | 60 | 50 | 45 | 40 | 40 | 80 | 32 | 48
| CH4 [g/GJ_i] | 2 | 2 | 1 | 1 | 0 | 0 | 4 | 0 | 2
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 1 | 7 | 1 | 7 |  | 9
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 4.7 | 4.5837 | 4.4702 | 4.2517 | 4.0438 | 3.2086 | 6.4171 | 2.8307 | 5.6613 |  | 8
| Nominal investment (equipment) [k€/unit, 2020] | 3.666 | 3.5753 | 3.4868 | 3.3163 | 3.1542 | 2.5027 | 5.0054 | 2.681 | 3.785
| Nominal investment (installation) [k€/unit, 2020] | 1.034 | 1.0084 | 0.98345 | 0.93537 | 0.88964 | 0.70589 | 1.4118 | 0.75619 | 1.0676
| Nominal investment (additional) [k€/unit, 2020] | 5 | 5 | 5 | 5 | 5 | 4.25 | 6 | 4.25 | 6 | H
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 375.3597 | 368.2417 | 362.52 | 346.1491 | 330.4821 | 314.5142 | 444.27 | 282.5478 | 381.9264 | I | 6
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 13.11 | 15.725 | 18.18 | 18.53 | 18.72 | 14.875 | 21.25 | 17.55 | 23.4 | J
| Fixed O&M (other) [€/unit/y, 2020] | 362.2497 | 352.5167 | 344.34 | 327.6191 | 311.7621 | 299.6392 | 423.02 | 264.9978 | 358.5264
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 20 | 16 | 16 | 16 | 16 | 6 | 36 | 6 | 30 | N | 9
Technology specific data
References:
1. www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg
2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
3. Lot 15: Solid fuel small combustion installations-Base Case definition
4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
5. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
6. Estimate by the Danish Energy Agency and Energinet, 2017
7. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
8. Interview with market actors and web price survey, 2020
9. Estimate based on user interview, 2020
10. Estimate by Ea Energy Analyses, 2020
Notes:
A. Nominal heat delivered in 2020 from 10-20 kW in single family houses. In small units (20 kW and less) the insignificant economy of scale (se section on economy of scale) the savings achieved by reducing the capacity of the boiler is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boiler installed
B. Efficiency development from [2]
C. EN303-5 measurement method
G. Improved real life conditions for flue gas condensation technology will increase the efficiency to >100% (based on NCV)
H. Fuel storage
I. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. PM2.5/PMtot = 90% according to [7]. Values from previous TC adjusted accordingly
M. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment
N. For loading fuel manually from bags and removing ash

## 204 Biomass auto,ex apart
Technology |  | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 400 | 400 | 400 | 400 | 400 | 200 | 600 | 200 | 600 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.85 | 0.87 | 0.9 | 0.9 | 0.9 | 0.79144 | 0.90856 | 0.8508 | 0.9492 | B | 2
| Auxiliary Electricity consumption [kWh_e/y] | 2400 | 2300 | 2200 | 2100 | 2000 | 2200 | 3000 | 1800 | 2500
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 3+7
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 18 | 32 | 18 | 32 |  | 4
| PM2.5 [g/GJ_i] | 14 | 14 | 11 | 9 | 9 | 8 | 20 | 4 | 14 | C, K, L | 6
| NOX [g/GJ_i] | 70 | 60 | 50 | 45 | 40 | 40 | 80 | 32 | 48 |  | 2
| CH4 [g/GJ_i] | 2 | 2 | 1 | 1 | 0 | 0 | 4 | 0 | 2 |  | 1+2
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 1 | 7 | 1 | 7 |  | 4
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 88 | 85.8219 | 83.6977 | 79.6057 | 75.7138 | 72.9486 | 102.9863 | 64.3567 | 90.8566 |  | 8
| Nominal investment (equipment) [k€/unit, 2020] | 70.4 | 68.6575 | 66.9582 | 63.6846 | 60.571 | 58.3589 | 82.389 | 51.4854 | 72.6853
| Nominal investment (installation) [k€/unit, 2020] | 17.6 | 17.1644 | 16.7395 | 15.9211 | 15.1428 | 14.5897 | 20.5973 | 12.8713 | 18.1713
| Nominal investment (additional) [k€/unit, 2020] | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 12.41 | 17.52 | 12.41 | 17.52 | E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 1501.3852 | 1490.7483 | 1497.4215 | 1449.6114 | 1387.2013 | 1264.0201 | 1785.8456 | 1181.3312 | 1666.8517 | F, I | 5
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 165.6 | 195.5 | 222.2 | 228.9 | 234 | 187 | 255 | 210.6 | 292.5 | J
| Fixed O&M (other) [€/unit/y, 2020] | 1335.7852 | 1295.2483 | 1275.2215 | 1220.7114 | 1153.2013 | 1077.0201 | 1530.8456 | 970.7312 | 1374.3517
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 40 | 40 | 40 | 40 | 40 | 10 | 90 | 10 | 90 |  | 7
Technology specific data
References:
1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro
2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
3. Energibesparelser - det behøver ikke være så svært; Energibranchen.dk, nr. 3, september 2009
4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
5. Estimate by the Danish Energy Agency and Energinet, 2017
6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
7. Estimate by Ea Energy Analyses, 2020
8. Interview with market actors and web price survey, 2020
Notes:
A. Nominal heat delivered in 2020 from 100 – 500 kW unit or a cascade of smaller units in apartment complexes
B. Efficiency development from [5]
C. EN303-5 measurement method
D. Prerequisite: house with central heating system
E. Fuel storage
F. Contemporary value from [6]
I. The cost is based on a unit with a capacity of 200 kW and assuming the cost for this unit is equally split between an initial cost and a linear dependence on the capacity of the unit
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
L. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment

## 204 Biomass auto,new apart
Technology |  | Biomass boiler, automatic stoking , wood pellets or wood chips - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 80 | 400 | 80 | 400 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.85 | 0.87 | 0.9 | 0.9 | 0.9 | 0.79144 | 0.90856 | 0.8508 | 0.9492 | B | 2
| Auxiliary Electricity consumption [kWh_e/y] | 1400 | 1360 | 1320 | 1280 | 1250 | 1200 | 2000 | 1000 | 1800
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 3+7
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 18 | 32 | 18 | 32 |  | 4
| PM2.5 [g/GJ_i] | 14 | 14 | 11 | 9 | 9 | 8 | 20 | 4 | 14 | C, K, L | 6
| NOX [g/GJ_i] | 70 | 60 | 50 | 45 | 40 | 40 | 80 | 32 | 48 |  | 2
| CH4 [g/GJ_i] | 2 | 2 | 1 | 1 | 0 | 0 | 4 | 0 | 2 |  | 1+2
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 1 | 7 | 1 | 7 |  | 4
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 53 | 51.6882 | 50.4088 | 47.9444 | 45.6 | 43.935 | 62.0258 | 38.7603 | 54.7204 | H | 8
| Nominal investment (equipment) [k€/unit, 2020] | 42.4 | 41.3505 | 40.3271 | 38.3555 | 36.5 | 35.148 | 49.6207 | 31.0252 | 43.7763
| Nominal investment (installation) [k€/unit, 2020] | 10.6 | 10.3376 | 10.0818 | 9.5889 | 9.1 | 8.787 | 12.4052 | 7.7351 | 10.9441
| Nominal investment (additional) [k€/unit, 2020] | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 7.48 | 10.56 | 7.48 | 10.56 | E
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 999.8081 | 991.2034 | 991.0529 | 954.0489 | 916.6258 | 841.9633 | 1184.7638 | 777.7507 | 1106.5812 | F, I | 5
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 96.6 | 115.6 | 133.32 | 139.52 | 146.25 | 102 | 170 | 117 | 210.6 | J
| Fixed O&M (other) [€/unit/y, 2020] | 903.2081 | 875.6034 | 857.7329 | 814.5289 | 770.3758 | 739.9633 | 1014.7638 | 660.7507 | 895.9812
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 32 | 32 | 32 | 32 | 32 | 12 | 100 | 12 | 100 |  | 7
Technology specific data
References:
1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro
2. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
3. Energibesparelser - det behøver ikke være så svært; Energibranchen.dk, nr. 3, september 2009
4. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
5. Estimate by the Danish Energy Agency and Energinet, 2017
6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
7. Estimate by Ea Energy Analyses, 2020
8. Interview with market actors and web price survey, 2020
Notes:
A. Nominal heat delivered in 2020 from 100 – 500 kW unit or a cascade of smaller units in apartment complexes
B. Efficiency development from [5]
C. EN303-5 measurement method
E. Fuel storage
F. Contemporary value from [6]
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
I. The cost is based on a unit with a capacity of 200 kW and assuming the cost for this unit is equally split between an initial cost and a linear dependence on the capacity of the unit
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly
L. Values likely to decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries. Filters would increase investment

## 205 Biomass manual,ex single
Technology |  | Biomass boiler, manual stoking, wood logs - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 30 | 25 | 20 | 20 | 20 | 15 | 50 | 15 | 50 | A | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 0.82 | 0.83 | 0.86 | 0.87 | 0.88 | 0.7 | 0.89515 | 0.80485 | 0.95515 |  | 3
| Auxiliary Electricity consumption [kWh_e/y] | 200 | 190 | 180 | 160 | 150 | 150 | 250 | 100 | 200 |  | 5+8
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 4+8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 18 | 32 | 18 | 32 |  | 6
| PM2.5 [g/GJ_i] | 14 | 14 | 11 | 9 | 9 | 8 | 20 | 4 | 14 | B, H | 4+8
| NOX [g/GJ_i] | 70 | 60 | 50 | 45 | 40 | 40 | 80 | 32 | 48 |  | 2+3
| CH4 [g/GJ_i] | 2 | 2 | 1 | 1 | 0 | 0 | 4 | 0 | 2
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 1 | 7 | 1 | 7 |  | 6
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 6.42 | 5.2176 | 4.0708 | 3.8717 | 3.6824 | 4.4349 | 6.2611 | 3.1301 | 4.4189 |  | 9
| Nominal investment (equipment) [k€/unit, 2020] | 4.494 | 3.6523 | 2.8495 | 2.7102 | 2.5777 | 3.1045 | 4.3828 | 2.1911 | 3.0933
| Nominal investment (installation) [k€/unit, 2020] | 1.926 | 1.5653 | 1.2212 | 1.1615 | 1.1047 | 1.3305 | 1.8783 | 0.93902 | 1.3257
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 434.1154 | 425.5836 | 418.0981 | 399.7561 | 381.3151 | 360.7685 | 512.5703 | 320.9003 | 441.7299 | F | 7
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 13.8 | 16.15 | 18.18 | 17.44 | 17.55 | 12.75 | 21.25 | 11.7 | 23.4 | G
| Fixed O&M (other) [€/unit/y, 2020] | 420.3154 | 409.4336 | 399.9181 | 382.3161 | 363.7651 | 348.0185 | 491.3203 | 309.2003 | 418.3299
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 60 | 50 | 40 | 40 | 40 | 15 | 200 | 15 | 200 |  | 7
Technology specific data
References:
1. www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg
2. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro
3. Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform
4. Lot 15: Solid fuel small combustion installations-Base Case definition
5. Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
7. Estimate by the Danish Energy Agency and Energinet, 2017
8. Estimate by Ea Energy Analyses, 2020
9. Interview with market actors and web price survey, 2020
Notes:
A. Nominal heat delivery in 2020 from 20-40 kW. Capacity is of little importance as all heat from a batch of firewood is supplied to the storage tank
B. EN303-5 measurement method
C. Prerequisite: house with central heating system
D. Storage tank
E. Chimney
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly

## 206 Wood stove,single, ex tank
Technology |  | Wood stove without water tank, wood logs - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 5 | 4 | 4 | 4 | 4 | 4 | 8 | 4 | 8 | E
| Expected share of space heating demand covered by unit [p.u.] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.6 | 0.2 | 0.6 | C
| Expected share of hot tap water demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat efficiency (annual average, net) [p.u.] | 0.7 | 0.72 | 0.75 | 0.75 | 0.75 | 0.62485 | 0.77515 | 0.67485 | 0.82515
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 30 | 30 | 30 | 0 | 0 | 25 | 40 | J
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2+5
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 3
| PM2.5 [g/GJ_i] | 28.8 | 25.2 | 21.6 | 18 | 18 | 18 | 180 | 10.8 | 144 | A, G, H, I | 1+6+7
| NOX [g/GJ_i] | 90 | 90 | 90 | 90 | 90 | 85.08 | 120 | 85.08 | 120
| CH4 [g/GJ_i] | 125 | 100 | 100 | 100 | 100 | 75 | 200 | 50 | 175 |  | 1+3
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 3
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.52 | 1.9661 | 3.5 | 3.3289 | 3.1661 | 1.6712 | 2.3593 | 2.6912 | 3.7994 | F | 8
| Nominal investment (equipment) [k€/unit, 2020] | 2.13 | 1.5961 | 3.15 | 2.996 | 2.8495 | 1.3567 | 1.9153 | 2.6912 | 3.4194
| Nominal investment (installation) [k€/unit, 2020] | 0.39 | 0.37 | 0.35 | 0.33289 | 0.31661 | 0.3145 | 0.444 | 0.26912 | 0.37994
| Nominal investment (additional) [k€/unit, 2020] | 1.6 | 1.2483 | 1.2174 | 1.1579 | 1.1013 | 1.2 | 2 | 1.08 | 2
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 145 | 141.4111 | 200.183 | 195.423 | 190.663 | 120.1994 | 169.6933 | 162.0051 | 219.906 | D | 4
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 3.03 | 3.27 | 3.51 | 0 | 0 | 2.925 | 4.68 | K
| Fixed O&M (other) [€/unit/y, 2020] | 145 | 141.4111 | 197.153 | 192.153 | 187.153 | 120.1994 | 169.6933 | 159.0801 | 215.226
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 50 | 40 | 40 | 40 | 40 | 20 | 120 | 20 | 120 |  | 5
Technology specific data
References:
1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
2. Lot 15: Solid fuel small combustion installations-Base Case definition.
3. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE no. 102, 2014
4. Estimate by the Danish Energy Agency and Energinet, 2017
5. Estimate by Ea Energy Analyses, 2020
6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
7. https://www.teknologisk.dk/ydelser/danske-braendeovne-er-blevet-bedre-for-miljoeet/33283
8. Interview with market actors and web price survey, 2020
Notes:
A. DIN Plus measurement method
C. The share of space heating covered by a wood stove depends on the options to regularly charge the stove with wood logs and of the location of the stove in the house. With regularly charging and a central location of the stove, the coverage can be up to 80 % of the heating demand in the house. Approximately 10 % larger is possible for stoves with a water tank. Taking into consideration that normally the average residents will have difficulties with regular fuel charging, the expected share of space heating covered by the wood stove without a water tank will be in the range of 20 % to 60 %
D. More automatic stoves are expected in the future(2030) Therefore, an increment in investment is expected. After this period, it is expected that the technology becomes generic and investment will decrease while still assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
E. Nominal heat delivery in 2020 from 4-10 kW
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly.
H. Emission of particles in marketed stoves has decreased by 20% the last 3 years according to (9). Values from previous TC adjusted accordingly.
I. Values decreasing due to more automatic stoves potentially with draught stabilisers. Values likely to further decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries as well as in Danish developments. Filters would increase investment, probably by 1/4-1/3.
J. Following Note D, more advanced stoves will include an electricity demand for conttrol system and draught stabiliser. The estimate is 50 W in operation only when the stove is fired, e.g. 150 times 4 h.
K. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 206 Wood stove, single n w tank
Technology |  | Wood stove with water tank - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 12 | 10 | 10 | 10 | 10 | 8 | 12 | 8 | 12
| Expected share of space heating demand covered by unit [p.u.] | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.2 | 0.7 | 0.2 | 0.7 | C
| Expected share of hot tap water demand covered by unit [p.u.] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.4 | 0.1 | 0.4
| Heat efficiency (annual average, net) [p.u.] | 0.7 | 0.72 | 0.75 | 0.75 | 0.75 | 0.62485 | 0.77515 | 0.67485 | 0.82515
| Auxiliary Electricity consumption [kWh_e/y] | 140 | 135 | 160 | 150 | 130 | 110 | 180 | 100 | 160 | J
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2+5
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 25 | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 3
| PM2.5 [g/GJ_i] | 28.8 | 25.2 | 21.6 | 18 | 18 | 18 | 108 | 10.8 | 72 | A, G, H, I | 1+6+7
| NOX [g/GJ_i] | 90 | 90 | 90 | 90 | 90 | 85.08 | 120 | 85.08 | 120
| CH4 [g/GJ_i] | 125 | 100 | 100 | 100 | 100 | 75 | 200 | 50 | 175 |  | 1+3
| N2O [g/GJ_i] | 4 | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 3
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 4 | 3.2508 | 4.5 | 4.28 | 4.0707 | 2.7632 | 3.901 | 3.4601 | 4.8849 |  | 8
| Nominal investment (equipment) [k€/unit, 2020] | 3.4 | 2.7632 | 3.825 | 3.638 | 3.4601 | 2.3487 | 3.3158 | 2.9411 | 4.1522
| Nominal investment (installation) [k€/unit, 2020] | 0.6 | 0.48762 | 0.675 | 0.642 | 0.61061 | 0.41448 | 0.58515 | 0.51902 | 0.73273
| Nominal investment (additional) [k€/unit, 2020] | 1.6 | 1.3003 | 1.2681 | 1.2061 | 1.1472 | 1 | 2 | 1 | 1.7
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 191.5808 | 220.7831 | 250.9761 | 247.1151 | 242.8731 | 187.726 | 264.7107 | 206.2101 | 291.5361 | D | 4
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 9.66 | 11.475 | 16.16 | 16.35 | 15.21 | 9.35 | 15.3 | 11.7 | 18.72 | F
| Fixed O&M (other) [€/unit/y, 2020] | 181.9208 | 209.3081 | 234.8161 | 230.7651 | 227.6631 | 178.376 | 249.4107 | 194.5101 | 272.8161
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 48 | 40 | 40 | 40 | 40 | 24 | 120 | 24 | 120 |  | 5
Technology specific data
References:
1. Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
2. Lot 15: Solid fuel small combustion installations-Base Case definition.
3. Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
4. Estimate by the Danish Energy Agency and Energinet, 2017
5. Estimate by Ea Energy Analyses, 2020
6. EMEP Guidebook (https://www.eea.europa.eu/publications/emep-eea-guidebook-2019) and advice from verenum.ch
7. https://www.teknologisk.dk/ydelser/danske-braendeovne-er-blevet-bedre-for-miljoeet/33283
8. Interview with market actors and web price survey, 2020
Notes:
A. DIN Plus measurement method
C. The share of space heating covered by a wood stove depends on the options to regularly charge the stove with wood logs and of the location of the stove in the house. With regularly charging and a central location of the stove, the coverage can be up to 80 % of the heating demand in the house. Approximately 10 % larger is possible for stoves with a water tank. Taking into consideration that normally the average residents will have difficulties with regular fuel charging, the expected share of space heating covered by the wood stove without a water tank will be in the range of 20 % to 60 %
D. More automatic stoves are expected in the future(2030) Therefore, an increment in investment is expected. After this period, it is expected that the technology becomes generic and investment will decrease while still assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies
F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
G. PM2.5/PMtot = 90% according to (12). Values from previous TC adjusted accordingly.
H. Emission of particles in marketed stoves has decreased by 20% the last 3 years according to (9). Values from previous TC adjusted accordingly.
I. Values decreasing due to more automatic stoves potentially with draught stabilisers. Values likely to further decrease significantly if electrostatic filters become mandatory, a tendency seen in neighbouring countries as well as in Danish developments. Filters would increase investment, probably by 1/5-1/4.
J. Following Note D, more advanced stoves will include an electricity demand for conttrol system and draught stabiliser. The estimate is 50 W in operation only when the stove is fired, e.g. 150 times 4 h.

## 207 HP air-water,ex single
Technology |  | Heat pump, Air-to-water - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 7 | 7 | 7 | 7 | 7 | 5 | 15 | 5 | 15 | A | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 3.15 | 3.3 | 3.45 | 3.6 | 3.7 | 2.85 | 3.75 | 3.3 | 4.35 | G, I, K, L, Z | 4,5,6,7,8,9,10
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA | 2
| Technical economic lifetime [years] | 16 | 16 | 16 | 16 | 16 | 14 | 20 | 14 | 20
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H | 3
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 10.953 | 10.103 | 9.2529 | 8.5634 | 7.874 | 7.4497 | 12.9396 | 5.9055 | 9.8425 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 6.9208 | 6.5748 | 6.2287 | 5.9173 | 5.6059 | 5.1007 | 9.1812 | 4.2044 | 7.0073 | B | 1
| Nominal investment (installation) [k€/unit, 2020] | 4.0322 | 3.5282 | 3.0242 | 2.6461 | 2.2681 | 2.349 | 3.7584 | 1.7011 | 2.8352 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 311.4094 | 227.5913 | 224.3101 | 218.2211 | 212.1321 | 175.2125 | 273.4227 | 194.8089 | 229.4553
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 311.4094 | 227.5913 | 224.3101 | 218.2211 | 212.1321 | 175.2125 | 273.4227 | 194.8089 | 229.4553 | E,F | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 4.05 | 4.25 | 4.4 | 4.55 | 4.65 | 3.35 | 4.65 | 3.85 | 5.15 | G, I, L | 4,5,6,7,8,9,10
Notes:
A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP air-water,ex apart
Technology |  | Heat pump, Air-to-water - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 320 | 320 | 320 | 320 | 320 | 300 | 500 | 300 | 500 | A,C | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 2.9 | 3.05 | 3.2 | 3.35 | 3.5 | 2.65 | 3.4 | 3.1 | 4 | G,I,K,L,Z | 4, 5, 11, 12
| Auxiliary Electricity consumption [kWh_e/y] | 600 | 550 | 500 | 450 | 400 | 400 | 1000 | 250 | 800 | AA
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H | 3
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 220.1342 | 197.1141 | 174.094 | 155.9295 | 137.7651 | 167.547 | 236.5369 | 103.3238 | 172.2064 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 179.8658 | 161.8792 | 143.8926 | 129.5034 | 115.1141 | 137.5973 | 194.255 | 86.3356 | 143.8926 | AC | 1
| Nominal investment (installation) [k€/unit, 2020] | 40.2685 | 35.2349 | 30.2013 | 26.4262 | 22.651 | 29.9497 | 42.2819 | 16.9883 | 28.3138 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 3465.8537 | 3448.8915 | 3430.3294 | 3387.4743 | 3343.8191 | 3302.5756 | 3620.7075 | 3208.4716 | 3508.4167
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 41.4 | 46.75 | 50.5 | 49.05 | 46.8 | 34 | 85 | 29.25 | 93.6 | J
| Fixed O&M (other) [€/unit/y, 2020] | 3424.4537 | 3402.1415 | 3379.8294 | 3338.4243 | 3297.0191 | 3268.5756 | 3535.7075 | 3179.2216 | 3414.8167 | D | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 3.7 | 3.85 | 3.95 | 4.1 | 4.25 | 3.15 | 4.3 | 3.6 | 4.7 | G I,L | 4, 5, 11, 12
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP air-water LPP,ex single
Technology |  | Heat pump, Air-to-water, low-price product - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 7 | 7 | 7 | 7 | 7 | 5 | 15 | 5 | 15 | A | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 3 | 3.15 | 3.3 | 3.45 | 3.55 | 2.7 | 3.55 | 3.15 | 4.15 | M,O | 29
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA | 2
| Technical economic lifetime [years] | 12 | 12 | 12 | 12 | 12 | 10 | 20 | 10 | 20 | O,N
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H | 3
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 8.596 | 7.8638 | 7.1315 | 6.5482 | 5.9648 | 6.2255 | 9.1651 | 4.4736 | 7.456 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 4.5638 | 4.3356 | 4.1074 | 3.902 | 3.6966 | 3.8765 | 5.4067 | 2.7725 | 4.6208 | B | 1
| Nominal investment (installation) [k€/unit, 2020] | 4.0322 | 3.5282 | 3.0242 | 2.6461 | 2.2681 | 2.349 | 3.7584 | 1.7011 | 2.8352 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 359.7315 | 275.9134 | 272.6322 | 266.5432 | 260.4543 | 223.5346 | 321.7449 | 243.1311 | 277.7774
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 359.7315 | 275.9134 | 272.6322 | 266.5432 | 260.4543 | 223.5346 | 321.7449 | 243.1311 | 277.7774 | E | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 4 | 4.2 | 4.35 | 4.5 | 4.6 | 3.3 | 4.6 | 3.8 | 5.05 | M,O
Notes:
A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP air-water,new single
Technology |  | Heat pump, Air-to-water - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 8 | 3 | 6 | A | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 2.95 | 3.1 | 3.25 | 3.4 | 3.5 | 2.65 | 3.45 | 3.15 | 4.05 | G,I,K,L,Z | 4,5,6,7,8,9,10
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA | 2
| Technical economic lifetime [years] | 16 | 16 | 16 | 16 | 16 | 14 | 20 | 14 | 20
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H | 3
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 6.0711 | 5.7273 | 5.3835 | 5.0801 | 4.7767 | 5.3188 | 9.1275 | 3.8213 | 5.9709 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 4.4604 | 4.2374 | 4.0144 | 3.8136 | 3.6129 | 3.953 | 7.1409 | 2.8903 | 4.5162 | B | 1
| Nominal investment (installation) [k€/unit, 2020] | 1.6107 | 1.4899 | 1.3691 | 1.2664 | 1.1638 | 1.3658 | 1.9866 | 0.93101 | 1.4547 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 277.0516 | 193.2334 | 189.9523 | 183.8633 | 177.7743 | 140.8547 | 239.0649 | 160.4511 | 195.0974
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 277.0516 | 193.2334 | 189.9523 | 183.8633 | 177.7743 | 140.8547 | 239.0649 | 160.4511 | 195.0974 | E,F | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 3.75 | 3.95 | 4.15 | 4.25 | 4.35 | 3.25 | 4.2 | 3.75 | 4.95 | G,I,L | 4,5,6,7,8,9,10
Notes:
A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP air-water,new apart
Technology |  | Heat pump, Air-to-water - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 | A,C | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 2.75 | 2.9 | 3 | 3.15 | 3.25 | 2.5 | 3.15 | 2.9 | 3.8 | G,I,K,L,Z | 4, 5, 11, 12
| Auxiliary Electricity consumption [kWh_e/y] | 350 | 325 | 300 | 250 | 250 | 250 | 500 | 200 | 400 | AA
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H | 3
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 123.4899 | 110.3758 | 97.2617 | 86.9617 | 76.6617 | 93.8195 | 132.451 | 57.4963 | 95.8272 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 92.8859 | 83.5973 | 74.3087 | 66.8779 | 59.447 | 71.0577 | 100.3168 | 44.5852 | 74.3087 | AC | 1
| Nominal investment (installation) [k€/unit, 2020] | 30.604 | 26.7785 | 22.953 | 20.0839 | 17.2148 | 22.7617 | 32.1342 | 12.9111 | 21.5185 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 2233.9896 | 2215.1524 | 2195.5153 | 2151.0601 | 2111.655 | 2075.2115 | 2363.5934 | 1988.0075 | 2247.0026
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 24.15 | 27.625 | 30.3 | 27.25 | 29.25 | 21.25 | 42.5 | 23.4 | 46.8 | J
| Fixed O&M (other) [€/unit/y, 2020] | 2209.8396 | 2187.5274 | 2165.2153 | 2123.8101 | 2082.405 | 2053.9615 | 2321.0934 | 1964.6075 | 2200.2026 | D | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 3.45 | 3.6 | 3.75 | 3.85 | 3.95 | 3 | 3.85 | 3.4 | 4.5 | G I,L | 4, 5, 11, 12
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP ground-water,ex single
Technology |  | Heat pump, Ground source - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 7 | 7 | 7 | 7 | 7 | 5 | 15 | 5 | 15 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 3.45 | 3.55 | 3.65 | 3.8 | 3.85 | 3.05 | 3.75 | 3.45 | 4.35 | G, I, K, L, Z | 4,5,6,7,8,9,10
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA | 2
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 18 | 40 | 18 | 40 | P | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 14.5056 | 13.7803 | 13.055 | 12.4023 | 11.7495 | 11.2215 | 16.3221 | 8.8121 | 14.6869 | Q
| Nominal investment (equipment) [k€/unit, 2020] | 7.0604 | 6.7074 | 6.3544 | 6.0366 | 5.7189 | 6.1208 | 8.903 | 4.2892 | 7.1487 | Q, R, B
| Nominal investment (installation) [k€/unit, 2020] | 7.4452 | 7.0729 | 6.7007 | 6.3656 | 6.0306 | 5.1007 | 7.4192 | 4.523 | 7.5383 | Q, R, AB
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 287.2483 | 203.4302 | 200.149 | 194.06 | 187.971 | 151.0514 | 249.2617 | 170.6479 | 205.2942
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 287.2483 | 203.4302 | 200.149 | 194.06 | 187.971 | 151.0514 | 249.2617 | 170.6479 | 205.2942 | E,F,S
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 4.35 | 4.45 | 4.55 | 4.65 | 4.7 | 3.85 | 4.95 | 4.15 | 5.35 | G, I, L | 4,5,6,7,8,9,10
Notes:
A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP ground-water,ex apart
Technology |  | Heat pump, Ground source - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 320 | 320 | 320 | 320 | 320 | 300 | 500 | 300 | 500 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 3.2 | 3.3 | 3.4 | 3.55 | 3.6 | 2.85 | 3.45 | 3.15 | 4 | G, I, K, L, Z | 4, 5, 11, 12
| Auxiliary Electricity consumption [kWh_e/y] | 600 | 550 | 500 | 450 | 400 | 400 | 1000 | 250 | 800 | AA | 2
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 18 | 40 | 18 | 40 | P | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 205.1007 | 189.7181 | 174.3356 | 161.2604 | 148.1852 | 161.2604 | 227.6617 | 111.1389 | 185.2315 | T
| Nominal investment (equipment) [k€/unit, 2020] | 115.9732 | 107.2752 | 98.5772 | 91.1839 | 83.7906 | 91.1839 | 128.7302 | 62.843 | 104.7383 | T, R, AC
| Nominal investment (installation) [k€/unit, 2020] | 89.1275 | 82.443 | 75.7584 | 70.0765 | 64.3946 | 70.0765 | 98.9315 | 48.296 | 80.4933 | T, R, AB
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 2144.7506 | 2127.7884 | 2109.2263 | 2066.3712 | 2022.716 | 1981.4725 | 2299.6044 | 1887.3685 | 2187.3136
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 41.4 | 46.75 | 50.5 | 49.05 | 46.8 | 34 | 85 | 29.25 | 93.6 | J
| Fixed O&M (other) [€/unit/y, 2020] | 2103.3506 | 2081.0384 | 2058.7263 | 2017.3212 | 1975.916 | 1947.4725 | 2214.6044 | 1858.1185 | 2093.7136 | D,F,S
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 4.1 | 4.2 | 4.3 | 4.4 | 4.45 | 3.65 | 4.6 | 3.9 | 4.9 | G,I,L | 4, 5, 11, 12
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP ground-water,new single
Technology |  | Heat pump, Ground source - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 8 | 3 | 6 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 3.25 | 3.35 | 3.45 | 3.6 | 3.75 | 2.85 | 3.95 | 3.35 | 4.45 | G, I, K, L, Z | 4,5,6,7,8,9,10
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA | 2
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 18 | 40 | 18 | 40 | P | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 9.6644 | 9.1812 | 8.698 | 8.2631 | 7.8282 | 7.804 | 11.0174 | 5.8711 | 9.7852 | Q
| Nominal investment (equipment) [k€/unit, 2020] | 5.8389 | 5.547 | 5.255 | 4.9923 | 4.7295 | 4.7149 | 6.6564 | 3.5471 | 5.9119 | Q, R, B
| Nominal investment (installation) [k€/unit, 2020] | 3.8255 | 3.6342 | 3.443 | 3.2708 | 3.0987 | 3.0891 | 4.3611 | 2.324 | 3.8733 | Q, R, AB
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 274.7084 | 190.8903 | 187.6091 | 181.5201 | 175.4312 | 138.5115 | 236.7218 | 158.108 | 192.7543
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 274.7084 | 190.8903 | 187.6091 | 181.5201 | 175.4312 | 138.5115 | 236.7218 | 158.108 | 192.7543 | E,F,S
Annual O&M (time spent on manual maintenance) [hours/unit/y]
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 4.05 | 4.15 | 4.25 | 4.4 | 4.55 | 3.45 | 4.55 | 3.75 | 5.05 | G, I, L | 4,5,6,7,8,9,10
Notes:
A. This capacity is only for the heat pump itself, defined at -7/55 degrees. Additionally a direct electrical immersion heater is also included in the heat pump with a capacity of around 9 kW.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP ground-water,new apart
Technology |  | Heat pump, Ground source - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 | A
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 2.9 | 3 | 3.1 | 3.25 | 3.4 | 2.65 | 3.6 | 3.05 | 4.05 | G,I,K,L, Z | 4, 5, 11, 12
| Auxiliary Electricity consumption [kWh_e/y] | 350 | 325 | 300 | 250 | 250 | 250 | 500 | 200 | 400 | AA | 2
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 18 | 40 | 18 | 40 | P | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 117.047 | 108.2685 | 99.4899 | 92.0282 | 84.5664 | 92.0282 | 129.9221 | 63.4248 | 105.7081 | T
| Nominal investment (equipment) [k€/unit, 2020] | 59.0604 | 54.6309 | 50.2013 | 46.4362 | 42.6711 | 46.4362 | 65.557 | 32.0034 | 53.3389 | T, R, AC
| Nominal investment (installation) [k€/unit, 2020] | 57.9866 | 53.6376 | 49.2886 | 45.5919 | 41.8953 | 45.5919 | 64.3651 | 31.4215 | 52.3691 | T, R, AB
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 1543.2252 | 1524.388 | 1504.7509 | 1460.2958 | 1420.8906 | 1384.4471 | 1672.829 | 1297.2431 | 1556.2382
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 24.15 | 27.625 | 30.3 | 27.25 | 29.25 | 21.25 | 42.5 | 23.4 | 46.8 | J
| Fixed O&M (other) [€/unit/y, 2020] | 1519.0752 | 1496.763 | 1474.4509 | 1433.0458 | 1391.6406 | 1363.1971 | 1630.329 | 1273.8431 | 1509.4382 | D,F,S
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, floor heating) [p.u.] | 3.7 | 3.8 | 3.9 | 4.05 | 4.15 | 3.15 | 4.2 | 3.5 | 4.6 | G,I,L | 4, 5, 11, 12
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP air-air,ex single
Technology |  | Heat pump, Air-to-air - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 2.5 | 8.5 | 2.5 | 8.5 | U | 1,15
| Expected share of space heating demand covered by unit [p.u.] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.7 | 0.2 | 0.7 | V
| Expected share of hot tap water demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | W
| Heat efficiency (annual average, net) [p.u.] | 4.85 | 5.1 | 5.3 | 5.5 | 5.6 | 4 | 6 | 4.8 | 6.8 | G, I, L,Y, Z | 4, 14, 6, 13
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA
| Technical economic lifetime [years] | 12 | 12 | 12 | 12 | 12 | 10 | 15 | 10 | 15
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 1.698 | 1.6565 | 1.615 | 1.5379 | 1.4609 | 1.2571 | 2.1999 | 0.9496 | 3.3601 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 1.204 | 1.1746 | 1.1452 | 1.0905 | 1.0359 | 0.87996 | 1.5714 | 0.67335 | 2.3826 |  | 1
| Nominal investment (installation) [k€/unit, 2020] | 0.49396 | 0.48188 | 0.46981 | 0.4474 | 0.425 | 0.37713 | 0.62855 | 0.27625 | 0.97749 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 150.3356 | 102.1402 | 100.2535 | 96.7523 | 93.2511 | 79.2244 | 125.0559 | 83.2903 | 106.5322
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 150.3356 | 102.1402 | 100.2535 | 96.7523 | 93.2511 | 79.2244 | 125.0559 | 83.2903 | 106.5322 | E,F | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP air-air,new single
Technology |  | Heat pump, Air-to-air - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 6.5 | 2 | 6.5 | U | 1,15
| Expected share of space heating demand covered by unit [p.u.] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.7 | 0.2 | 0.7 | V
| Expected share of hot tap water demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | W
| Heat efficiency (annual average, net) [p.u.] | 4.6 | 4.85 | 5.05 | 5.25 | 5.3 | 4 | 5.3 | 4.5 | 6.3 | G, I, L,Y, Z | 4, 14, 6, 13
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA
| Technical economic lifetime [years] | 12 | 12 | 12 | 12 | 12 | 10 | 15 | 10 | 15
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 1.114 | 1.0868 | 1.0596 | 1.009 | 0.95851 | 0.83806 | 1.5714 | 0.62303 | 2.2046 |  | 1
| Nominal investment (equipment) [k€/unit, 2020] | 0.62009 | 0.60493 | 0.58977 | 0.56164 | 0.53351 | 0.46093 | 0.94282 | 0.34678 | 1.2271 |  | 1
| Nominal investment (installation) [k€/unit, 2020] | 0.49396 | 0.48188 | 0.46981 | 0.4474 | 0.425 | 0.37713 | 0.62855 | 0.27625 | 0.97749 | AB | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 150.3356 | 102.1402 | 100.2535 | 96.7523 | 93.2511 | 79.2244 | 125.0559 | 83.2903 | 106.5322
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | J
| Fixed O&M (other) [€/unit/y, 2020] | 150.3356 | 102.1402 | 100.2535 | 96.7523 | 93.2511 | 79.2244 | 125.0559 | 83.2903 | 106.5322 | E,F | 1
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP ventilation,new single
Technology |  | Heat pump, ventilation - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 2 | 3 |  | 16,17,19
| Expected share of space heating demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| Expected share of hot tap water demand covered by unit [p.u.] | 0.9 | 0.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | V | 16,20
| Heat efficiency (annual average, net) [p.u.] | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.2 | 3.5 | 3.2 | 4 | X, I | 16,17,20
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AA | 20
| Technical economic lifetime [years] | 15 | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 16,17,20
Electric regulation ability
| Primary regulation (per 30 seconds) [p.u.] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 16,17,20
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16,17,20
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16,17,20
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.307 | 2.2126 | 2.122 | 2.0436 | 1.9719 | 1.77 | 2.5444 | 1.5775 | 2.2677 |  | 18,21,22,23
| Nominal investment (equipment) [k€/unit, 2020] | 2.1059 | 2.0191 | 1.9393 | 1.8717 | 1.8107 | 1.6153 | 2.3408 | 1.47 | 1.8378 | J | 16,17,20
| Nominal investment (installation) [k€/unit, 2020] | 0.20112 | 0.19346 | 0.18271 | 0.17197 | 0.16122 | 0.15477 | 0.20364 | 0.10748 | 0.42991 | AB | 16,17,20
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 202.0589 | 191.8485 | 181.6381 | 172.5024 | 163.3668 | 153.0706 | 255.1177 | 161.2172 | 268.6954
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (other) [€/unit/y, 2020] | 202.0589 | 191.8485 | 181.6381 | 172.5024 | 163.3668 | 153.0706 | 255.1177 | 161.2172 | 268.6954 |  | 16,17,20
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 207 HP ventilation,new apart
Technology |  | Heat pump, ventilation - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 |  | 19,25
| Expected share of space heating demand covered by unit [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.7 | 1 | 0.7 | 1 | V
| Expected share of hot tap water demand covered by unit [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.7 | 1 | 0.7 | 1 | V
| Heat efficiency (annual average, net) [p.u.] | 5.4 | 5.45 | 5.5 | 5.6 | 5.7 | 5.3 | 5.6 | 5.3 | 6.2 | X, I | 24,26,27,28
| Auxiliary Electricity consumption [kWh_e/y] | 350 | 325 | 300 | 250 | 250 | 250 | 500 | 200 | 400 | AA | 24,20
| Technical economic lifetime [years] | 15 | 15 | 15 | 15 | 15 | 12 | 20 | 12 | 20 |  | 20,27
Electric regulation ability
| Primary regulation (per 30 seconds) [p.u.] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 20,26
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | H
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20,26
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20,26
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 76.3095 | 72.0104 | 67.7112 | 64.4869 | 61.2626 | 60.8538 | 101.4231 | 53.7391 | 107.4782 |  | 27,28
| Nominal investment (equipment) [k€/unit, 2020] | 53.4166 | 50.4073 | 47.3979 | 45.1408 | 42.8838 | 42.5977 | 70.9961 | 26.8695 | 91.3564 | J | 27
| Nominal investment (installation) [k€/unit, 2020] | 22.8928 | 21.6031 | 20.3134 | 19.3461 | 18.3788 | 18.2561 | 30.4269 | 8.0609 | 53.7391 | AB | 27
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 1034.4447 | 987.405 | 939.5652 | 890.837 | 847.1588 | 531.7713 | 2084.585 | 560.7908 | 2196.3632
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 24.15 | 27.625 | 30.3 | 27.25 | 29.25 | 21.25 | 42.5 | 23.4 | 46.8
| Fixed O&M (other) [€/unit/y, 2020] | 1010.2947 | 959.78 | 909.2652 | 863.587 | 817.9088 | 510.5213 | 2042.085 | 537.3908 | 2149.5632 |  | 27
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Notes:
A. This capacity does not include the capacity of the direct electrical heating also installed, but only the capacity of the heat pump itself. It is defined at -7/55 degrees.
B. Including domestic hot water storage tank with approximately 200L and auxiliary equipment. Not including buffer tank.
C. Typically cascade solution of smaller heat pumps.
D. A service requires the system must cycle fully, which takes time for larger systems. The service cost is not very dependent on the kW, but more on the specific installation and therefore the price is typically defined for a specific installation. Service is performed annually.
E. The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
F. Including spare parts.
G. Based on large samples of SCOP data (EN14825) which have been corrected for hot water consumption and correlated with field study measurements.
H. Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating.
I. Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
J. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K. Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
L. Projections are based on developments in SCOPs from 2015 to 2020 for the given product type and expected future development rates
M. Assuming 4% lower SCOP for cheaper heat pump models for buildings with radiators and 1% lower for buildings with floor heating.
N. Based on discussions with suppliers and the length of available insurance plans.
O. Data is very limited and therefore this value is highly uncertain.
P. Installation companies report very few issues with ground-source heat pumps. The higher temperature results in less strain on the unit compared to air-sourced heat pumps.
Q. Based on a ground source with horizontal collector
R. The ration between installation and equipment is maintained in the upper and lower boundaries
S. Assumed the same as corresponding air-sourced heat pumps
T. Based on a ground source with horizontal collector. A vertical collector would increase the investment by approximately 700.000 kr. for existing building and 450.000 for new buildings.
U. Based on a air-to-air heat pump with one indoor component.
V. The share of heating demand covered depends on how the heat pump is operated in the total heat energy system in the house. Therefore this value is highly uncertain.
W. There are air-to-air heat pumps capable of delivering domestic hot water, but these are not expected to have an considerable role in the heating sector. Most installed air-to-air heat pumps will only provide space heating and cooling.
X. Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
Y. Data shows a small dependency between capacity and SCOP efficiency for air-to-air heat pumps which is included
Z. The SCOP numbers is bases on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
AA. For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
AB. The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
AC. Including domestic hot water storage tank and auxiliary equipment.
References:
1. Interviews with various installation companies.
2. Teknologisk Institute.
3. Installation company
4. Dialogue with heat pump experts at Danish Technological Institute, 2020
5. SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
6. "Den Lille Blå om Varmepumper" published by elforsk.dk
7. "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
8. Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
9. "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
10. "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
11. Bosch 2020, conversation
12. DVI (Dansk Varmepumpe Industri) 2020, conversation
13. Ecodesign Review study "Air conditioners and comfort fans - task 6 Design Options" published May 2018
14. SCOP data for air-air heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
15. ENS heat pump sale statistics
16. Danfoss, 2015, information provided at workshop
17. Bosch, 2015 , information provided at workshop
18. Market and Statistics Report, EHPA 2014
19. Energistyrelsen, 2015, conversation
20. Teknologisk Institut, 2015, conversation
21. Nilan, 2015, conversation
22. Genvex, 2015, conversation
23. Heat implementation scenarios until 2030, Ecofys 2013
24. Sparenergi.dk, 2015
25. Energinet.dk, 2015, conversation
26. Cronborg, 2015, conversation
27. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
28. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
29. SCOP values from "Varmepumpelisten" and supplier websites.

## 208 HP hybrid,ex single
Technology |  | Heat pump, gas-hybrid - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 9 | 3 | 9 | I | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to -
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to -
| Heat efficiency (annual average, net) [p.u.] | 2.15 | 2.25 | 2.3 | 2.35 | 2.4 | 2.05 | 2.45 | 2.25 | 2.65 | N, O
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | V | 2
| Technical economic lifetime [years] | 18 | 18 | 18 | 18 | 18 | 14 | 20 | 14 | 20 | F
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to -
Secondary regulation (per minute) [p.u.] | bar: ctrl to -
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | W
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | G,H
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | G,H
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | G,H
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 11.2752 | 10.4385 | 9.6018 | 8.871 | 8.1402 | 8.3508 | 13.57 | 6.5122 | 10.5822 | D | 1
| Nominal investment (equipment) [k€/unit, 2020] | 6.706 | 6.4405 | 6.175 | 5.8725 | 5.5701 | 5.1524 | 8.3727 | 4.456 | 7.2411 | D, Y | 1
| Nominal investment (installation) [k€/unit, 2020] | 4.5691 | 3.998 | 3.4268 | 2.9985 | 2.5701 | 3.1984 | 5.1974 | 2.0561 | 3.3412 | D, X | 1
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | K
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 375.8389 | 271.0663 | 266.9648 | 259.3536 | 251.7423 | 205.5928 | 328.3556 | 230.0883 | 273.3963
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (other) [€/unit/y, 2020] | 375.8389 | 271.0663 | 266.9648 | 259.3536 | 251.7423 | 205.5928 | 328.3556 | 230.0883 | 273.3963 | B, C, E | 1
| Variable O&M (*total) [€/MWh_h, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, gas boiler heating) [p.u.] | 0.913 | 0.913 | 0.92241 | 0.93182 | 0.93182 | 0.89418 | 0.94124 | 0.92241 | 0.96006 | R | 4
| Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | 3.35 | 3.55 | 3.75 | 3.95 | 4.05 | 3 | 4.1 | 3.55 | 4.85 | Q, U, S, T | 5,6,7,8,9,10,11
| Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | 4.5 | 4.75 | 4.9 | 5.1 | 5.25 | 3.6 | 5.25 | 4.25 | 5.85 | Q, P, U, S, T | 5,6,7,8,9,10,11
| Heat efficiency (annual average, net, total system, floor heating) [p.u.] | 2.5 | 2.55 | 2.65 | 2.7 | 2.7 | 2.25 | 2.75 | 2.45 | 2.9 | P, N
Notes:
A | The heat pump delivers approximately 80% of the total heat demand while the gas boiler supplies the rest. The expected shares of heating demand and hot tap water demand delivered by each unit depends on the operation strategy.
B | The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
C | Including spare parts.
D | Based on a combination of interviews, market research and data from datasheets for air-to-water heat pumps and gas boilers.
E | 25% higher than the corresponing pure heat pump solution to account for the additional work for the gas furnace.
F | The liftetime for the heat pump is expected to be extended due to decreased strain compared to a pure heat pump solution. The heat pump is the most expensive component and therefore this is the deciding factor for the economic lifetime.
G | Data for emissions can be found at emission inventories envs.au.dk
H | Only for the gas usage. The gas boiler is assumed to deliver 20% of the heat demand.
I | The capacity shown only considers the heat pump calculated at -7/55 degrees. The size of the gas boiler can vary but does not significantly affect the price.
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K | Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L | Typically cascade solution of smaller heat pumps.
M | Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same is true for heat pumps.
N | Efficiency of the total system. Se technology specific data for the seperate efficiencies. Calculated as 1/(80%/COPVP + 20%/ƞgas) and afterwards rounded.
O | Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
P | Efficiency for a building with floor heating.
Q | Based on data from the datasheets for the corresponding air-to-water heat pump
R | Based on summer efficiency of gas boiler installations. The development is based on the gas boiler for corresponding building type.
S | Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
T | The SCOP numbers is based on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
U | Under the assumption that the gas boiler provides the hot tap water and a share of the coldest hours of the year.
V | For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
W | Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating. Same is true for the gas boiler.
X | The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
Y | Including domestic hot water storage tank and auxiliary equipment.
References:
1 | Interviews with various installation companies.
2 | Teknologisk Institute.
3 | Installation company
4 | DGC, ”Dokumentation for villagaskedlers faktiske virkningsgrad”, November 2020.
5 | Dialogue with heat pump experts at Danish Technological Institute, 2020
6 | SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
7 | "Den Lille Blå om Varmepumper" published by elforsk.dk
8 | "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
9 | Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
10 | "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
11 | "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
12 | Bosch 2020, conversation
13 | DVI (Dansk Varmepumpe Industri) 2020, conversation

## 208 HP hybrid,ex apart
Technology |  | Heat pump, gas-hybrid - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 150 | 250 | 150 | 250 | I, L | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to -
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to -
| Heat efficiency (annual average, net) [p.u.] | 2.15 | 2.2 | 2.3 | 2.35 | 2.45 | 2 | 2.4 | 2.25 | 2.65 | N, O
| Auxiliary Electricity consumption [kWh_e/y] | 600 | 550 | 500 | 450 | 400 | 400 | 1000 | 250 | 800 | V | 2
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to -
Secondary regulation (per minute) [p.u.] | bar: ctrl to -
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | W
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | G,H
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | G,H
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | G,H
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 193.2886 | 177.1347 | 160.9807 | 147.5275 | 134.0743 | 141.7077 | 230.2751 | 107.2594 | 174.2965 | D | 1
| Nominal investment (equipment) [k€/unit, 2020] | 147.1141 | 136.732 | 126.3499 | 117.2255 | 108.1011 | 109.3856 | 177.7516 | 86.4809 | 140.5314 | D, Y | 1
| Nominal investment (installation) [k€/unit, 2020] | 46.1745 | 40.4027 | 34.6309 | 30.302 | 25.9732 | 32.3221 | 52.5235 | 20.7785 | 33.7651 | D, X | 1
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | K
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 3743.0723 | 3720.5821 | 3696.3919 | 3643.2355 | 3589.1791 | 3540.8247 | 3925.7395 | 3424.4321 | 3783.2261
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 41.4 | 46.8 | 50.5 | 49.1 | 46.8 | 34 | 85 | 29.3 | 93.6 | J
| Fixed O&M (other) [€/unit/y, 2020] | 3701.6723 | 3673.7821 | 3645.8919 | 3594.1355 | 3542.3791 | 3506.8247 | 3840.7395 | 3395.1321 | 3689.6261
| Variable O&M (*total) [€/MWh_h, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, gas boiler heating) [p.u.] | 0.913 | 0.913 | 0.92204 | 0.92204 | 0.92204 | 0.89492 | 0.93108 | 0.90396 | 0.94012 | R | 4
| Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | 3.25 | 3.45 | 3.7 | 3.9 | 4.15 | 2.85 | 4 | 3.55 | 4.9 | Q, U, S, T | 5, 6, 12, 13
| Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | 4.45 | 4.65 | 4.8 | 5.05 | 5.25 | 3.6 | 5.35 | 4.3 | 5.95 | Q, P, U, S, T | 5, 6, 12, 13
| Heat efficiency (annual average, net, total system, floor heating) [p.u.] | 2.5 | 2.55 | 2.6 | 2.65 | 2.7 | 2.25 | 2.75 | 2.45 | 2.85 | P, N
Notes:
A | The heat pump delivers approximately 80% of the total heat demand while the gas boiler supplies the rest. The expected shares of heating demand and hot tap water demand delivered by each unit depends on the operation strategy.
B | The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
C | Including spare parts.
D | Based on a combination of interviews and data from datasheets for air-to-water heat pumps and gas boilers.
E | 25% higher than the corresponing pure heat pump solution to account for the additional work for the gas furnace.
F | The liftetime for the heat pump is expected to be extended due to decreased strain compared to a pure heat pump solution. The heat pump is the most expensive component and therefore this is the deciding factor for the economic lifetime.
G | Data for emissions can be found at emission inventories envs.au.dk
H | Only for the gas usage. The gas boiler is assumed to deliver 20% of the heat demand.
I | The capacity shown only considers the heat pump calculated at -7/55 degrees. The size of the gas boiler can vary but does not significantly affect the price.
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K | Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L | Typically cascade solution of smaller heat pumps.
M | Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same is true for heat pumps.
N | Efficiency of the total system. Se technology specific data for the seperate efficiencies. Calculated as 1/(80%/COPVP + 20%/ƞgas) and afterwards rounded.
O | Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
P | Efficiency for a building with floor heating.
Q | Based on data from the datasheets for the corresponding air-to-water heat pump
R | Based on summer efficiency of gas boiler installations. The development is based on the gas boiler for corresponding building type.
S | Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
T | The SCOP numbers is based on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
U | Under the assumption that the gas boiler provides the hot tap water and a share of the coldest hours of the year.
V | For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
W | Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating. Same is true for the gas boiler.
X | The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
Y | Including domestic hot water storage tank and auxiliary equipment.
References:
1 | Interviews with various installation companies.
2 | Teknologisk Institute.
3 | Installation company
4 | DGC, ”Dokumentation for villagaskedlers faktiske virkningsgrad”, November 2020.
5 | Dialogue with heat pump experts at Danish Technological Institute, 2020
6 | SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
7 | "Den Lille Blå om Varmepumper" published by elforsk.dk
8 | "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
9 | Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
10 | "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
11 | "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
12 | Bosch 2020, conversation
13 | DVI (Dansk Varmepumpe Industri) 2020, conversation

## 208 HP hybrid,new single
Technology |  | Heat pump, gas-hybrid - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 4 | 4 | 4 | 4 | 4 | 3 | 8 | 3 | 6 | I | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to -
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to -
| Heat efficiency (annual average, net) [p.u.] | 2.15 | 2.2 | 2.25 | 2.35 | 2.4 | 1.95 | 2.4 | 2.25 | 2.65 | N, O
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | V | 2
| Technical economic lifetime [years] | 18 | 18 | 18 | 18 | 18 | 14 | 20 | 14 | 20 | P
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to -
Secondary regulation (per minute) [p.u.] | bar: ctrl to -
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | W
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | G,H
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | G,H
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | G,H
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 7.302 | 6.953 | 6.604 | 6.2344 | 5.8649 | 5.551 | 9.043 | 4.6919 | 7.6243 | D | 1
| Nominal investment (equipment) [k€/unit, 2020] | 5.1544 | 4.9664 | 4.7785 | 4.5458 | 4.3132 | 3.6886 | 6.5598 | 3.4506 | 5.6072 | D, Y | 1
| Nominal investment (installation) [k€/unit, 2020] | 2.1477 | 1.9866 | 1.8255 | 1.6886 | 1.5517 | 1.8624 | 2.4832 | 1.2413 | 2.0172 | D, X | 1
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 358.1755 | 253.4028 | 249.3013 | 241.6901 | 234.0789 | 187.9293 | 310.6921 | 212.4249 | 255.7328
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (other) [€/unit/y, 2020] | 358.1755 | 253.4028 | 249.3013 | 241.6901 | 234.0789 | 187.9293 | 310.6921 | 212.4249 | 255.7328 | B, C, E | 1
| Variable O&M (*total) [€/MWh_h, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, gas boiler heating) [p.u.] | 0.913 | 0.913 | 0.92241 | 0.93182 | 0.93182 | 0.89418 | 0.94124 | 0.92241 | 0.96006 | R | 4
| Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | 3.2 | 3.4 | 3.6 | 3.8 | 3.95 | 2.81 | 3.85 | 3.45 | 4.7 | Q, U, S, T | 5,6,7,8,9,10,11
| Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | 4.3 | 4.55 | 4.8 | 4.95 | 5.1 | 3.6 | 4.9 | 4.3 | 5.9 | Q, P, U, S, T | 5,6,7,8,9,10,11
| Heat efficiency (annual average, net, total system, floor heating) [p.u.] | 2.45 | 2.5 | 2.6 | 2.65 | 2.7 | 2.25 | 2.65 | 2.45 | 2.9 | P, N
Notes:
A | The heat pump delivers approximately 80% of the total heat demand while the gas boiler supplies the rest. The expected shares of heating demand and hot tap water demand delivered by each unit depends on the operation strategy.
B | The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
C | Including spare parts.
D | Based on a combination of interviews and data from datasheets for air-to-water heat pumps and gas boilers.
E | 25% higher than the corresponing pure heat pump solution to account for the additional work for the gas furnace.
F | The liftetime for the heat pump is expected to be extended due to decreased strain compared to a pure heat pump solution. The heat pump is the most expensive component and therefore this is the deciding factor for the economic lifetime.
G | Data for emissions can be found at emission inventories envs.au.dk
H | Only for the gas usage. The gas boiler is assumed to deliver 20% of the heat demand.
I | The capacity shown only considers the heat pump calculated at -7/55 degrees. The size of the gas boiler can vary but does not significantly affect the price.
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K | Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L | Typically cascade solution of smaller heat pumps.
M | Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same is true for heat pumps.
N | Efficiency of the total system. Se technology specific data for the seperate efficiencies. Calculated as 1/(80%/COPVP + 20%/ƞgas) and afterwards rounded.
O | Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
P | Efficiency for a building with floor heating.
Q | Based on data from the datasheets for the corresponding air-to-water heat pump
R | Based on summer efficiency of gas boiler installations. The development is based on the gas boiler for corresponding building type.
S | Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
T | The SCOP numbers is based on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
U | Under the assumption that the gas boiler provides the hot tap water and a share of the coldest hours of the year.
V | For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
W | Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating. Same is true for the gas boiler.
X | The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
Y | Including domestic hot water storage tank and auxiliary equipment.
References:
1 | Interviews with various installation companies.
2 | Teknologisk Institute.
3 | Installation company
4 | DGC, ”Dokumentation for villagaskedlers faktiske virkningsgrad”, November 2020.
5 | Dialogue with heat pump experts at Danish Technological Institute, 2020
6 | SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
7 | "Den Lille Blå om Varmepumper" published by elforsk.dk
8 | "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
9 | Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
10 | "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
11 | "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
12 | Bosch 2020, conversation
13 | DVI (Dansk Varmepumpe Industri) 2020, conversation

## 208 HP hybrid,new apart
Technology |  | Heat pump, gas-hybrid - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 | I, L | 1
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to -
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to -
| Heat efficiency (annual average, net) [p.u.] | 2.15 | 2.25 | 2.3 | 2.4 | 2.45 | 1.95 | 2.4 | 2.2 | 2.75 | N, O
| Auxiliary Electricity consumption [kWh_e/y] | 350 | 325 | 300 | 250 | 250 | 250 | 500 | 200 | 400 | V | 2
| Technical economic lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to -
Secondary regulation (per minute) [p.u.] | bar: ctrl to -
| Minimum load (of full load) [p.u.] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.3 | 0.2 | 0.3 | W
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
Environment
| SO2 [g/GJ_i] | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0 | 1 | 0 | 1 | G,H
| PM2.5 [g/GJ_i] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.5 | 0 | 1 | G,H
| NOX [g/GJ_i] | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 15 | 25 | 15 | 25 | G,H
| CH4 [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | G,H
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 107.3826 | 98.2085 | 89.0344 | 81.3799 | 73.7253 | 68.7459 | 127.671 | 58.9802 | 95.8428 | D | 1
| Nominal investment (equipment) [k€/unit, 2020] | 71.9463 | 67.2018 | 62.4573 | 58.1248 | 53.7924 | 47.0412 | 87.3623 | 43.0339 | 69.9301 | D, Y | 1
| Nominal investment (installation) [k€/unit, 2020] | 35.4362 | 31.0067 | 26.5772 | 23.255 | 19.9329 | 21.7047 | 40.3087 | 15.9463 | 25.9128 | D, X | 1
| Nominal investment (additional) [k€/unit, 2020] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | K
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 2371.8311 | 2348.4566 | 2324.382 | 2271.6958 | 2224.0097 | 2181.8774 | 2523.6357 | 2076.7526 | 2382.8668
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 24.2 | 27.6 | 30.3 | 27.3 | 29.3 | 21.3 | 42.5 | 23.4 | 46.8 | J
| Fixed O&M (other) [€/unit/y, 2020] | 2347.6311 | 2320.8566 | 2294.082 | 2244.3958 | 2194.7097 | 2160.5774 | 2481.1357 | 2053.3526 | 2336.0668
| Variable O&M (*total) [€/MWh_h, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Heat efficiency (annual average, net, gas boiler heating) [p.u.] | 0.913 | 0.913 | 0.92204 | 0.92204 | 0.92204 | 0.89492 | 0.93108 | 0.90396 | 0.94012 | R | 4
| Heat efficiency (annual average, net, heat pump, radiator heating) [p.u.] | 3.35 | 3.5 | 3.7 | 4 | 4.2 | 2.75 | 4 | 3.5 | 5.25 | Q, U, S, T | 5, 6, 12, 13
| Heat efficiency (annual average, net, hear pump, floor heating) [p.u.] | 4.55 | 4.85 | 5.15 | 5.3 | 5.5 | 3.7 | 5.3 | 4.45 | 6.55 | Q, P, U, S, T | 5, 6, 12, 13
| Heat efficiency (annual average, net, total system, floor heating) [p.u.] | 2.55 | 2.6 | 2.65 | 2.7 | 2.75 | 2.25 | 2.75 | 2.5 | 3 | P, N
Notes:
A | The heat pump delivers approximately 80% of the total heat demand while the gas boiler supplies the rest. The expected shares of heating demand and hot tap water demand delivered by each unit depends on the operation strategy.
B | The follow-up agreement to the climate agreement of June 2020 detirmined that only bi-annual service is required for private households. Therefore it is assumed that only 25% of consumers will continue the annual service reducing fixed O&M allocated to service (not spare parts) by 38% after 2020.
C | Including spare parts.
D | Based on a combination of interviews and data from datasheets for air-to-water heat pumps and gas boilers.
E | 25% higher than the corresponing pure heat pump solution to account for the additional work for the gas furnace.
F | The liftetime for the heat pump is expected to be extended due to decreased strain compared to a pure heat pump solution. The heat pump is the most expensive component and therefore this is the deciding factor for the economic lifetime.
G | Data for emissions can be found at emission inventories envs.au.dk
H | Only for the gas usage. The gas boiler is assumed to deliver 20% of the heat demand.
I | The capacity shown only considers the heat pump calculated at -7/55 degrees. The size of the gas boiler can vary but does not significantly affect the price.
J | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
K | Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L | Typically cascade solution of smaller heat pumps.
M | Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same is true for heat pumps.
N | Efficiency of the total system. Se technology specific data for the seperate efficiencies. Calculated as 1/(80%/COPVP + 20%/ƞgas) and afterwards rounded.
O | Efficiency for a building with radiators. See technology specific data for efficiency regarding buildings with floor heating
P | Efficiency for a building with floor heating.
Q | Based on data from the datasheets for the corresponding air-to-water heat pump
R | Based on summer efficiency of gas boiler installations. The development is based on the gas boiler for corresponding building type.
S | Heat efficiency values refers to the SCOP of the heat pump and includes auxillary electricity consumption
T | The SCOP numbers is based on the assumption, that the heat pump is installed correctly and the controls are well-adjusted.
U | Under the assumption that the gas boiler provides the hot tap water and a share of the coldest hours of the year.
V | For small buildings (new and existing single-family homes) the necessary pumps and electrical equiment is built into the heat pump, and therefore also included in the SCOP. Hence the aux. electricity consumption is set to 0. For larger buldings it expected that external pumps are necessary to ensure sufficient circulation, where the auxilary electricity consumption is assumed equal to that of indirect heating.
W | Down to this value, the heat pump is frequency regulated. It can provide less heat, but does so by on and off regulating. Same is true for the gas boiler.
X | The split between equipment and installation is a average account of the collected data. The split can vary depending on the supplier, where some price-components can be defined as both equiment and installation, such as mark-up and piping/fittings/etc. needed for the specific installation. See uncertainty section.
Y | Including domestic hot water storage tank and auxiliary equipment.
References:
1 | Interviews with various installation companies.
2 | Teknologisk Institute.
3 | Installation company
4 | DGC, ”Dokumentation for villagaskedlers faktiske virkningsgrad”, November 2020.
5 | Dialogue with heat pump experts at Danish Technological Institute, 2020
6 | SCOP data for air-water heat pumps from the Danish positive list "Varmepumpelisten" hosted by the Danish Energy Agency
7 | "Den Lille Blå om Varmepumper" published by elforsk.dk
8 | "Wärmepumpen in Bestandsgebäuden" published by Fraunhofer July 2020
9 | Ecodesign Review study "Space & Combination heaters - task 4 Technologies" published july 2019
10 | "Den gode installation af varmepumper" published by Danish Technological Institute, January 2017
11 | "Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling", published by Danish Technological Institute, August 2011
12 | Bosch 2020, conversation
13 | DVI (Dansk Varmepumpe Industri) 2020, conversation

## 215 Solar heating,ex single
Technology |  | Solar heating system - single-family house - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 3 | 6 | 3 | 6 | A, I | 1
| Expected share of space heating demand covered by unit [p.u.] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.15 | 0 | 0.15 | B, I | 1
| Expected share of hot tap water demand covered by unit [p.u.] | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.7 | 0.4 | 0.7 | B, I | 1
Heat efficiency (annual average, net) [p.u.]
| Auxiliary Electricity consumption [kWh_e/y] | 50 | 50 | 50 | 50 | 50 | 25 | 75 | 25 | 75
| Technical economic lifetime [years] | 25 | 25 | 30 | 30 | 30 | 20 | 30 | 20 | 30 | C | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment | bar: -
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 4.14 | 4.0375 | 3.9376 | 3.7451 | 3.562 | 3.4319 | 4.845 | 3.0277 | 4.2744 | K, H
| Nominal investment (equipment) [k€/unit, 2020] | 2.898 | 2.8263 | 2.7563 | 2.6216 | 2.4934 | 2.4023 | 3.3915 | 2.1194 | 2.9921
| Nominal investment (installation) [k€/unit, 2020] | 1.242 | 1.2113 | 1.1813 | 1.1235 | 1.0686 | 1.0296 | 1.4535 | 0.90831 | 1.2823 | D
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 52.45 | 49.25 | 48.05 | 45.45 | 42.85 | 43.575 | 60.775 | 38.425 | 54.775 | E, H
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 3.45 | 4.25 | 5.05 | 5.45 | 5.85 | 2.125 | 6.375 | 2.925 | 8.775 | F
| Fixed O&M (other) [€/unit/y, 2020] | 49 | 45 | 43 | 40 | 37 | 41.45 | 54.4 | 35.5 | 46
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Solar collector area [m2] | 6 | 6 | 6 | 6 | 6 | 4 | 8 | 4 | 8 | I | 1, 6
| Performance (output per collector area) [kWh/m2/y] | 425 | 435 | 445 | 465 | 485 | 425 | 445 | 430 | 500 | J | 1
References:
1. Solvarme faktablade, www.altomsolvarme.dk.
6. Recommendation: Converting solar thermal collector area into installed capacity (m2 to kWth). Technical note, IEA SHC 2004.
Notes:
A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
C. Increase due to better materials/fluids.
D. Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
E. Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
F. Electricity for solar pump and control. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
G. Pollution associated with the small amount of electricity needed for operation is neglected.
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
K. Based on data from interviews with installers during creation of this data sheet

## 215 Solar heating,ex apart
Technology |  | Solar heating system - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 140 | 140 | 140 | 140 | 140 | 100 | 200 | 100 | 200 | A, I | 1
| Expected share of space heating demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B, I | 1
| Expected share of hot tap water demand covered by unit [p.u.] | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.7 | 0.4 | 0.7 | B, I | 1
Heat efficiency (annual average, net) [p.u.]
| Auxiliary Electricity consumption [kWh_e/y] | 3000 | 2800 | 2500 | 2250 | 2000 | 2000 | 4000 | 1500 | 3000
| Technical economic lifetime [years] | 20 | 25 | 30 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 81 | 77.5 | 74 | 70.5 | 67 | 65.875 | 93 | 56.95 | 80.4
| Nominal investment (equipment) [k€/unit, 2020] | 52.65 | 50.375 | 48.1 | 45.825 | 43.55 | 42.8188 | 60.45 | 37.0175 | 52.26
| Nominal investment (installation) [k€/unit, 2020] | 28.35 | 27.125 | 25.9 | 24.675 | 23.45 | 23.0562 | 32.55 | 19.9325 | 28.14 | D
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 417 | 442 | 451.5 | 439.25 | 417 | 310 | 609 | 261.5 | 566 | E, H
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 207 | 238 | 252.5 | 245.25 | 234 | 170 | 340 | 175.5 | 351
| Fixed O&M (other) [€/unit/y, 2020] | 210 | 204 | 199 | 194 | 183 | 140 | 269 | 86 | 215 | F
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Solar collector area [m2] | 200 | 200 | 200 | 200 | 200 | 140 | 290 | 140 | 290 | I | 1, 6
| Performance (output per collector area) [kWh/m2/y] | 425 | 435 | 450 | 475 | 500 | 300 | 450 | 400 | 550 |  | 1
References:
1. Solvarme faktablade, www.altomsolvarme.dk.
Notes:
A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
C. Increase due to better materials/fluids.
D. Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
E. Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
F. Electricity for solar pump and control. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.

## 215 Solar heating,new single
Technology |  | Solar heating system - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 3 | 6 | 3 | 6 | A, I | 1
| Expected share of space heating demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B, I | 1
| Expected share of hot tap water demand covered by unit [p.u.] | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.7 | 0.4 | 0.7 | B, I | 1
Heat efficiency (annual average, net) [p.u.] | bar: -
| Auxiliary Electricity consumption [kWh_e/y] | 50 | 50 | 50 | 50 | 50 | 25 | 75 | 25 | 75
| Technical economic lifetime [years] | 25 | 25 | 30 | 30 | 30 | 20 | 30 | 20 | 30 | C | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.4 | 2.25 | 2.1 | 2 | 1.9 | 1.9125 | 2.7 | 1.615 | 2.4 | K
| Nominal investment (equipment) [k€/unit, 2020] | 1.56 | 1.4625 | 1.365 | 1.3 | 1.235 | 1.2431 | 1.755 | 1.0497 | 1.56
| Nominal investment (installation) [k€/unit, 2020] | 0.84 | 0.7875 | 0.735 | 0.7 | 0.665 | 0.66937 | 0.945 | 0.56525 | 0.84 | D
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 66.45 | 65.25 | 65.05 | 62.45 | 59.85 | 45.125 | 92.375 | 34.925 | 83.775
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 3.45 | 4.25 | 5.05 | 5.45 | 5.85 | 2.125 | 6.375 | 2.925 | 8.775
| Fixed O&M (other) [€/unit/y, 2020] | 63 | 61 | 60 | 57 | 54 | 43 | 86 | 32 | 75
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Solar collector area [m2] | 6 | 6 | 6 | 6 | 6 | 4 | 8 | 4 | 8 | I | 1, 6
| Performance (output per collector area) [kWh/m2/y] | 425 | 435 | 445 | 465 | 485 | 425 | 445 | 430 | 500 | J | 1
References:
1. Solvarme faktablade, www.altomsolvarme.dk.
Notes:
A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
C. Increase due to better materials/fluids.
D. Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
J. In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.
K. Based on data from interviews with installers during creation of this data sheet

## 215 Solar heating,new apart
Technology |  | Solar heating system - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 140 | 140 | 140 | 140 | 140 | 100 | 200 | 100 | 200 | A, I | 1
| Expected share of space heating demand covered by unit [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B, I | 1
| Expected share of hot tap water demand covered by unit [p.u.] | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.7 | 0.4 | 70 | B, I | 1
Heat efficiency (annual average, net) [p.u.]
| Auxiliary Electricity consumption [kWh_e/y] | 3000 | 2800 | 2500 | 2250 | 2000 | 2000 | 4000 | 1500 | 3000
| Technical economic lifetime [years] | 20 | 25 | 30 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 81 | 77.5 | 74 | 70.5 | 67 | 65.875 | 93 | 56.95 | 80.4 | K
| Nominal investment (equipment) [k€/unit, 2020] | 52.65 | 50.375 | 48.1 | 45.825 | 43.55 | 42.8188 | 60.45 | 37.0175 | 52.26
| Nominal investment (installation) [k€/unit, 2020] | 28.35 | 27.125 | 25.9 | 24.675 | 23.45 | 23.0562 | 32.55 | 19.9325 | 28.14
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 414 | 480 | 524.5 | 503.25 | 486 | 318 | 637 | 364.5 | 728 | E, H
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 207 | 238 | 252.5 | 245.25 | 234 | 170 | 340 | 175.5 | 351
| Fixed O&M (other) [€/unit/y, 2020] | 207 | 242 | 272 | 258 | 252 | 148 | 297 | 189 | 377
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Technology specific data
| Solar collector area [m2] | 200 | 200 | 200 | 200 | 200 | 140 | 290 | 140 | 290 | I | 1, 6
| Performance (output per collector area) [kWh/m2/y] | 425 | 435 | 450 | 475 | 500 | 300 | 450 | 400 | 550 | J | 1
References:
1. Solvarme faktablade, www.altomsolvarme.dk.
Notes:
A. Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
B. Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
C. Increase due to better materials/fluids.
E. Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
H. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
I. The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
K. Based on data from interviews with installers during creation of this data sheet

## 216 Electric heating,new single
Technology |  | Electric heating - single-family house - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 3 | 3 | 3 | 3 | 3 | 2 | 7 | 2 | 7
| Expected share of space heating demand covered by unit [p.u.] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100
| Expected share of hot tap water demand covered by unit [p.u.] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | A
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical economic lifetime [years] | 30 | 30 | 30 | 30 | 30 | 25 | 30 | 25 | 30
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 2.691 | 2.6244 | 2.5594 | 2.4343 | 2.3153 | 2.2307 | 3.1493 | 1.968 | 2.7784 | D, E, F | 4, 5
| Nominal investment (equipment) [k€/unit, 2020] | 1.8837 | 1.8371 | 1.7916 | 1.704 | 1.6207 | 1.5615 | 2.2045 | 1.3776 | 1.9448
| Nominal investment (installation) [k€/unit, 2020] | 0.8073 | 0.78732 | 0.76783 | 0.73029 | 0.69459 | 0.66922 | 0.94478 | 0.5904 | 0.83351
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 24 | 24 | 23 | 22 | 21 | 20.4 | 28.8 | 17.85 | 25.2 | C, E
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (other) [€/unit/y, 2020] | 24 | 24 | 23 | 22 | 21 | 20.4 | 28.8 | 17.85 | 25.2
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
4. Peter Strøm from “EL-Strøm A/S”, personnaly communication.
5. Based on data from interviews with installers during creation of this data sheet
Notes:
A. Annual efficiency based on 100 % space heating efficiency and hot water efficiency. In addition, distribution heat losses compared to water based heating systems are saved, typically in the range of 5-10 %.
C. Assuming change of heating elements in the hot water tank every 10 years.
D. The price includes the complete system including room heaters and hot tap water preparation.
E. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
F. Including costs of wiring and procurement and installation of radiators

## 216 Electric heating,new apart
Technology |  | Electric heating - apartment complex - new building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 160 | 160 | 160 | 160 | 160 | 100 | 250 | 100 | 250 | B
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
Heat efficiency (annual average, net) [p.u.] | bar: ctrl to -
| Auxiliary Electricity consumption [kWh_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical economic lifetime [years] | 30 | 30 | 30 | 30 | 30 | 25 | 30 | 25 | 30
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.] | bar: ctrl to upper
Secondary regulation (per minute) [p.u.] | bar: ctrl to upper
| Minimum load (of full load) [p.u.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 109.71 | 106.9945 | 104.3463 | 99.2448 | 94.3927 | 90.9454 | 128.3934 | 80.2338 | 113.2713 | D, E, F | 4, 5
| Nominal investment (equipment) [k€/unit, 2020] | 76.797 | 74.8962 | 73.0424 | 69.4714 | 66.0749 | 63.6618 | 89.8754 | 56.1637 | 79.2899
| Nominal investment (installation) [k€/unit, 2020] | 32.913 | 32.0984 | 31.3039 | 29.7734 | 28.3178 | 27.2836 | 38.518 | 24.0702 | 33.9814
| Nominal investment (additional) [k€/unit, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [€/kWh, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [€/unit/y, 2020] | 49 | 47 | 46 | 44 | 42 | 39.95 | 56.4 | 35.7 | 50.4 | C, E
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (other) [€/unit/y, 2020] | 49 | 47 | 46 | 44 | 42 | 39.95 | 56.4 | 35.7 | 50.4
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
4. Peter Strøm from “EL-Strøm A/S”, personnaly communication.
5. Based on data from interviews with installers during creation of this data sheet
Notes:
A. Annual efficiency based on 100 % space heating efficiency and hot water efficiency. In addition, distribution heat losses compared to water based heating systems are saved, typically in the range of 5-10 %.
B. Assuming 150 apartments.
C. Assuming change of heating elements in the hot water tank every 10 years.
D. The price includes the complete system including room heaters and hot tap water preparation.
E. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
F. Including costs of wiring and procurement and installation of radiators