## Index
INDEX | Technology Data for Energy Carrier Generation and Conversion June 2017
81 Biogas Plant, Basic conf.
81 Biogas Plant, Add. Straw
81 Biogas Plant, Add. Org Waste
82 Biogas, upgrading
83 Gasif. Fixed Bed, Producer
84 Gasif. CFB, Bio-SNG
85 Gasif. Ent. Flow FT, liq fu
86 AEC 1MW
86 AEC 100MW
86 PEMEC 1MW
86 PEMEC 100MW
86 SOEC 1MW
89 Vegetable oil FAME
90 UCO & animal fat FAME
91 Hydrogenated veg oil
92 HVO jet fuel
93 1st generation ethanol
94 Pyrolysis oils
95 Cellulosic ethanol | Version 0007
97 Methanol from biomass gasif.
98 Methanol from power
99 SNG from methan. of biogas
100 Hydrothermal liquifaction
101 Catalytic Hydropyrolysis 2
101 Catalytic Hydropyrolysis 1
102 Hydrogen to Jet
102 Power to Jet
103 Hydrogen to Ammonia
104 Methane pyrolysis, MBR
104 Methane pyrolysis, Plasma
The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. The date for the latest update is listed in the index below and also indicated in the specific datasheets.
INDEX:
85 Gasification of biomass for bio diesel has been overwritten with data from previous chapter 96. Chapter 96 has been removed. (update Feb 2019)
101 Catalytic hydropyrolysis configuration 1 - financial data added. (update Feb 2019)
89-100 datasheets have been revised (update Dec 2018)
101 Catalytic hydropyrolysis in two configurations (added Dec 2018)
83-88 Gasification and electrolysis (added Dec 2018)
102 Power to Jet (added May 2020) - minor adjustment (july 2020)
103 Hydrogen to Ammonia (added February 2021 - adjustet April 2021)
86-88 have been replaced with chapter 86 on electrolysis (added April 2021)
104 Methane pyrolysis (added April 2021)

## 81 Biogas Plant, Basic conf.
| Technology | Biogas plant, basic configuration
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Typical capacity (tons/year input)
| Typical total plant size (MW output) | 9.2417 | 8.6829 | 8.6829 | 8.6829 | 8.3176 | 9.5512 | 8.3176 | 9.5512 | A
- Inputs
| Biomass (tons/year) | 365000 | 365000 | 365000 | 365000 | 365000 | 365000 | 365000 | 365000 | A B | 5/8/9
| Aux. electricity (% of output energy) | 3.6969 | 3.8196 | 3.8196 | 3.8196 | 1.9195 | 6.7182 | 1.9195 | 6.7182 | A | 5/8/9
| Aux. electricity (kWh/ton input) | 8.1999 | 7.9596 | 7.9596 | 7.9596 | 4.2574 | 14 | 4 | 14
| Aux. process heat (% of output energy) | 8.3859 | 8.9256 | 8.9256 | 8.9256 | 7.198 | 11.9967 | 7.198 | 11.9967 | A | 5/8/9
| Aux. process heat (kWh/ton input)) | 18.6 | 18.6 | 18.6 | 18.6 | 15.9654 | 25 | 15 | 25
- Outputs
| Biogas (%) | 100 | 100 | 100 | 100 | 95.7922 | 110 | 95.7922 | 110 | F
| Biogas (GJ/ton input) | 0.79849 | 0.7502 | 0.7502 | 0.7502 | 0.71864 | 0.82523 | 0.71864 | 0.82523 | G | 9
| Biogas production, (MJ/S heating value) | [8 empty] | J
| Forced outage (%) | 0 | 0 | 0 | 0
| Planned outage (days per year) | 10 | 10 | 10 | 10
| Technical lifetime (years) | 20 | 20 | 20 | 20
| Construction time (years) | 1 | 1 | 1 | 1
Financial data
| Specific investment (mio €/MW output) | 1.8141 | 1.7107 | 1.5396 | 1.3857 | 1.5396 | 1.9008 | 1.2471 | 1.5396 | A H C | 8/5
| - of which equipment | - | -
| - of which installation | - | -
| Total O&M (€/MW/year) | 198785.1794 | 194715.0214 | 197702.4392 | 195722.307 | 154397.5872 | 245575.0367 | 150000.9903 | 252438.887
| Total O&M (€/(ton input/year)) | 5.0332 | 4.632 | 4.7031 | 4.656 | 3.5184 | 6.4261 | 3.4182 | 6.6058 | A D I | 8/5
| - of which O&M, excl el. and heat (€/(ton input/year)) | 4.1066 | 3.6728 | 3.4892 | 3.3147 | 2.8146 | 5.0501 | 2.5402 | 4.5578 | A D I | 8/5
| - of which electricity (€/(ton input/year)) | 0.51659 | 0.54922 | 0.80392 | 0.93128 | 0.29376 | 0.966 | 0.468 | 1.638 | K
| - of which heat (€/(ton input/year)) | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41
Technology Specific data
| Methane emission (Nm3 CH4/ton input/year) | 0.44 | 0.42 | 0.42 | 0.42 | 0.17 | 0.88 | 0.17 | 0.88 | J | 12
Notes:
A
B
C
D
| Biomass | Share, 2015 | Share, 2020 | Price per ton (€), incl transport
| Manure (pig and cattle) | 79.8% | 83.79% | 3.3557
| Deep bed material | 8% | 8.464% | 6.7114
| Manure, stable | 6.1% | 0.2439% | 6.7114
| Straw | 0% | 0% | 67.3826
| Industrial organic waste | 1% | 1.201% | 40.2685
| Household waste | 1.6% | 1.246% | 18.8591
| Energy crops | 0% | 0% | 34.8993
| Other | 3.5% | 5.056% | 27.9195
F
G
H
I
J
K
References:
5 | "Udvikling og effektivisering af biogasproduktionen I Danmark – Delrapport 1 og 2”, Danish Energy Agency Biogas Taskforce 2015.
8 | ”Anvendelse af biogas til el- og varmeproduktion, analyser for Biogas Taskforce”, Ea Energianalyse, 2014
9 | "Biomasse til biogasanlæg i Danmark - på kort og langt sigt", Agrotech, November 2013
12 | ”Miljøeffekter af metanlækage på biogasanlæg”, Agrotek, 2015

## 81 Biogas Plant, Add. Straw
| Technology | Biogas plant, additional straw input in the feedstock mix
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Biogas from additional straw (MW output) | 1 | [7 empty] | A B
- Inputs
| Straw input (% of additional output) | 199.4% | 181.9% | 181.9% | 181.9% |  |  |  |  | A B | 5/8/9
| Straw input (tons per year) | 4336.9805 | 3956.7055 | 3956.7055 | 3956.7055
| Auxilliary electricity input (% of additional output) | 3.124% | 2.85% | 2.85% | 2.85% | [5 empty] | 5/8/9
| Auxilliary electricity input (kWh/ton straw) | 63 | 63 | 63 | 63 |  |  |  |  | A
| Additional process heat (% of additional output) | 0.9209% | 0.8401% | 0.8401% | 0.8401% | [5 empty] | 5/8/9
| Auxilliary process heat (kWh/ton straw input) | 18.6 | 18.6 | 18.6 | 18.6 |  |  |  |  | A
- Outputs
| Biogas (%) | 100% | 100% | 100% | 100% |  |  |  |  | A C
| Biogas (GJ/ton straw input) | 7.27 | 7.97 | 7.97 | 7.97 |  |  |  |  | A C | 9
| Residual organic material | [8 empty] | D
| Forced outage (%) | 0 | 0 | 0 | 0
| Planned outage (days per year) | 10 | 10 | 10 | 10
| Technical lifetime (years) | 20 | 20 | 20 | 20
| Construction time (years) | 1 | 1 | 1 | 1
Financial data
| Investment (€/MW) | 407676.1694 | 371930.3139 | 371930.3139 | 371930.3139 |  |  |  |  | AEG | 8/5
| Investment (€/ton straw input/year) | 94 | 94 | 94 | 94 |  |  |  |  | AEG
| Total O&M (€/MW/year) | 47386.6211 | 44727.3028 | 52704.021 | 56692.3802 |  |  |  |  | AFG | 8/5
| Total O&M (€/ton straw input/year) | 10.9262 | 11.3042 | 13.3202 | 14.3282 |  |  |  |  | AFG
| - of which O&M, excl el. and heat (€/(ton input/year)) | 6.5472 | 6.5472 | 6.5472 | 6.5472
| - of which electricity (€/(ton input/year)) | 3.969 | 4.347 | 6.363 | 7.371 |  |  |  |  | K
| - of which heat (€/(ton input/year)) | 0.41 | 0.41 | 0.41 | 0.41
Technology Specific data
| Methane emission (Nm3 CH4 input/year) | 4 | 4.4 | 4.4 | 4.4 | 1.8 | 9.2 | 1.8 | 9.2 | H | 12
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | The data sheet shows the expected energy output and values for the input of industrial organic waste specifically. The values refer to a virtual part of a total plant processing the straw. A plant including increased share of straw may be composed by adding a basic plant part and straw processing part.
B | Values are assumed valid for adding a smaller part of straw to a total plant. Maximum share not assessed.
C | For compatibility with the template the energy of the biogas output is assumed to be 100%. (For the input material a calorific value is not relevant)
D | The energy content of residual organic material has not been evaluated due to lack of sources.
E | Investment in straw preparation equipment (57 Eur/ton/year) and proportional share of basic plant included. Biogas processing time is 25 days
F | All O&M considered fixed, assuming 8760 hours operation per year. Does not include fuel for process heat, electricity, biomass purchase and transport, see e.g. [5] and [8].
G | The value will vary with the quality of the input. Assumed average value used corresponding to 320 Nm3 CH4 / ton VS, TS 42%, vs/ts 90%. [8].
H | Learning curve effects have not been considered. Will depend on actrual deployment of technology.
J | Corresponding to 2% of the produced biogas, wit lower value 0.8% and upper value 4.2%. This will vary and can be reduced.
K | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
References:
5 | "Udvikling og effektivisering af biogasproduktionen I Danmark – Delrapport 1 og 2”, Danish Energy Agency Biogas Taskforce 2015.
8 | ”Anvendelse af biogas til el- og varmeproduktion, analyser for Biogas Taskforce”, Ea Energianalyse, 2014
9 | "Biomasse til biogasanlæg i Danmark - på kort og langt sigt", Agrotech, November 2013
12 | ”Miljøeffekter af metanlækage på biogasanlæg”, Agrotek, 2015

## 81 Biogas Plant, Add. Org Waste
| Technology | Biogas plant, additional industrial organic waste in the feedstock mix
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Biogas from additional ind. organic waste (MW output) | 100% | [7 empty] | A B
- Inputs
| Ind. organic waste input (% of additional output) | 125-200% | 125-200% | 125-200% | 125-200% |  |  |  |  | L
| Ind. organic waste input (tons per year) | 6529.1925 | 6529.1925 | 6529.1925 | 6529.1925 | [5 empty] | 5
| Aux. electricity (% of additional output) | 0.7677% | 0.7677% | 0.7677% | 0.7677% | [5 empty] | 5
| Aux. electricity (kWh/ton waste input) | 10.3 | 10.3 | 10.3 | 10.3 |  |  |  |  | A
| Aux. process heat (% of additional output) | 1.386% | 1.386% | 1.386% | 1.386% | [5 empty] | 5
| Aux. process heat (kWh/ton waste input)) | 18.6 | 18.6 | 18.6 | 18.6 |  |  |  |  | A
- Outputs
| Biogas (% of total input) | 100% | 100% | 100% | 100% |  |  |  |  | A C
| Biogas (GJ/ton ind. org. waste input) | 4.83 | 4.83 | 4.83 | 4.83 |  |  |  |  | ACG | 5/9
| Residual organic material | [8 empty] | D
| Forced outage (%) | 0 | 0 | 0 | 0
| Planned outage (days per year) | 10 | 10 | 10 | 10
| Technical lifetime (years) | 20 | 20 | 20 | 20
| Construction time (years) | 1 | 1 | 1 | 1
Financial data
| Investment (€/MW output) | 276050.4202 | 276050.4202 | 276050.4202 | 276050.4202 |  |  |  |  | AEH | 8/5
| Investment (€/ton waste input / year) | 42.2794 | 42.2794 | 42.2794 | 42.2794 |  |  |  |  | AEH
| Total O&M (€/MW/year) | 49500.2802 | 49903.7843 | 52055.8062 | 53131.8171 |  |  |  |  | AFH | 8/5
| Total O&M (€/ton waste input/year) | 7.5814 | 7.6432 | 7.9728 | 8.1376 |  |  |  |  | AFH
| - of which O&M, excl el. and heat (€/(ton input/year)) | 6.5225 | 6.5225 | 6.5225 | 6.5225
| - of which electricity (€/(ton input/year)) | 0.6489 | 0.7107 | 1.0403 | 1.2051 |  |  |  |  | K
| - of which heat (€/(ton input/year)) | 0.41 | 0.41 | 0.41 | 0.41
Technology Specific data
| Methane emission (Nm3 CH4 input/year) | 4 | 4.4 | 4.4 | 4.4 | 1.8 | 9.2 | 1.8 | 9.2 | H | 12
Notes:
A | The data sheet shows the expected energy output and values for the input of industrial organic waste specifically. The values refer to a virtual part of a total plant processing the industrial organic waste. A plant including including increased share of industrial organic waste may be composed by adding a basic plant part and an ind. org. waste processing part.
B | Values are assumed valid for adding a smaller part of straw to a total plant. Maximum share not assessed.
C | For compatibility with the template the energy of the biogas output is assumed to be 100%. (For the input material a calorific value is not relevant)
D | The energy content of residual organic material has not been evaluated due to lack of sources.
E | Investment in straw preparation equipment (57 Eur/ton/year) and proportional share of basic plant included. Biogas processing time is 25 days
F | All O&M considered fixed, assuming 8760 hours operation per year. Does not include fuel for process heat, electricity, biomass purchase and transport, see e.g. [5] and [8]. O&M costs for straw processing equipment, 10 Eur/ton/year, and proportional share of basic plant included.
G | The value will vary with the quality of the input. Assumed average value used corresponding to 320 Nm3 CH4 / ton VS, TS 42%, vs/ts 90%. [8].
H | Learning curve effects have not been considered. Will depend on actrual deployment of technology.
J | Calculated with a constant production 8760 hours per year
K | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
L | The conversion efficiency depends on the specific types of industrial waste used at the biogas plants.
Fatty biomasses may be converted with high efficiences (>70 %) whereas for example the conversion of protein rich biomasses is closer to 50 %.
References:
5 | "Udvikling og effektivisering af biogasproduktionen I Danmark – Delrapport 1 og 2”, Danish Energy Agency Biogas Taskforce 2015.
8 | ”Anvendelse af biogas til el- og varmeproduktion, analyser for Biogas Taskforce”, Ea Energianalyse, 2014
9 | "Biomasse til biogasanlæg i Danmark - på kort og langt sigt", Agrotech, November 2013
12 | ”Miljøeffekter af metanlækage på biogasanlæg”, Agrotek, 2015

## 82 Biogas, upgrading
| Technology | Biogas upgrading
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total size (MJ output/s) | 5.9222 | 5.9222 | 5.9222 | 5.9222 |  |  |  |  | A G
| Typical total size (Nm3 biogas/h) | 1000 | 1000 | 1000 | 1000 |  |  |  |  | A B | 1/4
| Capacity (Nm3 biomethane/h) | 594 | 594 | 594 | 594 |  |  |  |  | A B
- Inputs
| Biogas (% of biogas input) | 100% | 100 | 100 | 100
| Auxilliary electricity for upgrading (% of biogas input) | 4.313% | 4.313% | 2.156% | 2.156% | 3.235% | 4.313% | 1.617% | 3.235% | A D J | 1/2/4/7
| Auxilliary electricity for compression (% of biogas input) | 1.003% | 1.003% | 1.003% | 1.003% |  |  |  |  | A F | 2/4
| Heat (% of biogas input) | 0% | 0% | 0% | 0% | [5 empty] | 2/4
- Outputs
| Biomethane (% of biogas input) | 99% | 99% | 100% | 100% |  |  |  |  | I | 2
| Waste gas (% of biogas input) | 1% | 1% | 0.1% | 0.1% |  |  |  |  | I
| Waste heat (% of biogas input) | 5.3% | 5.3% | 3.2% | 3.2%
| Forced outage (weeks per year) | 1 | 1 | 1 | 1
| Planned outage (weeks per year) | 1 | 1 | 1 | 1
| Technical lifetime (years) | 15 | 15 | 15 | 15
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5
Financial data
| Specific investment, upgrading and methane reduction (€/MJ/s input) | 335000 | 302000 | 272000 | 245000 | 268000 | 318000 | 172000 | 287000 | C D | 1/2/5/7
| Specific investment, grid injection at 40bar (€/MJ/s input) | 134000 | 121000 | 109000 | 98000 | 107000 | 127000 | 69000 | 115000 | F | 5
| Fixed O&M (€/MJ/s input / year) | 11800 | 10600 | 9500 | 8600 | 9400 | 11200 | 6000 | 10100 |  | 2
| - of which fixed O&M costs upgrading and methane reduction, excl. el. (€/MJ/s input / year) | 8400 | 7600 | 6800 | 6100 | 6700 | 8000 | 4300 | 7200 |  | 2
| - of which fixed O&M costs grid injection, excl. el. (€/MJ/s input / year) | 3400 | 3000 | 2700 | 2500 | 2700 | 3200 | 1700 | 2900 | H | 2
| Variable O&M ((€/GJ input) | 0.93 | 1.0252 | 0.88439 | 1.023 |  |  |  |  | H
| - of which electricity (€/GJ input) | 0.93 | 1.0252 | 0.88439 | 1.023 |  |  |  |  | E | 2/4/7
Technology specific data
| Methane slip / emission (%) | 1% | 1% | 0.1% | 0.1% |  |  |  |  | I | 2
| Minimum load (% of full load) | 50 | [8 empty] | 7
| CO2 removal, % | 98.5 | [8 empty] | 1
References:
1 | "Technology Data for Energy Plants – Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion.", certain updates in October 2013, and January 2014, Danish Energy Agency, May 2012.
2 | Biogas upgrading – Review of commercial technologies. SGC Rapport 2013:270. SGC, 2013 |  |  |  | "Biogas upgrading – Review of commercial technologies", SGC Rapport 2013:270, SGC, 2013 .
4 | "Biogas upgrading technologies – developments and innovations, Task 37 – Energy from biogas and landfill gas". IEA Bioenergy, 2009.
5 | ”Anvendelse af biogas til el- og varmeproduktion”, Ea Energianalyse, 2014.
7 | ”Introduktion til produktion af biometan fra biogas”, Biometan Regioner, 2013.
Notes:
A | Corresponding to 1.000 Nm3 biogas input, assuming a methane content of the raw biogas of 60% and an average gross conversion efficiency of approx. 98,5%.
B | Values are assumed valid for a range 500-1,500 Nm3 biomethane per hour
C | Values include upgrading, methane reduction and grid injection facilities
D | Based on a water-scrubber technology based plant, alternative technologies have comparable values in terms of total upgrading costs. For a plant of double capacity (2000 Nm3/h) the realtive price is expected to be 20-25% lower [1,3]
E | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
F | Injection in natural gas grid at 40 bar
G | Based on a lower calorfic value of 36 MJ/Nm3 and 8760 hours per year
H | O&M costs are estimated to 2.5% of investment per year, in accodance with [2]
I | Assuming that, by 2030, methane slip can be reduced to levels seen today for amin scrubbing technology. Methane slip is assumed to be the same as waste gas assuming that the plant is not equipped with a regenerative thermal oxidation (RTO) plant. If the the off-gas from the upgrading plant is treated with a regenerative thermal oxidation (RTO) plant the methane slip can be eliminated.
J | Assuming that, by 2030, one or more of the newer and currently less developled technologies (e.g. cryogenic and membrane technologies) will take over.
This can lead to a 50% reduction of the electricity consumption, which is already achievable today with the amine scrubbing technology.
References:
1 | “Biogas upgrading – Technical review, Energiforsk report 2016:275, Energiforsk AB, 2016.
2 | “Biogas upgrading – Review of commercial technologies”, SGC Rapport 2013:270, SGC, 2013.
4 | “Biogas upgrading technologies – developments and innovations. Task 37 – Energy from biogas and landfill gas”, Petersson & Wellinger, IEA Bioenergy, 2009.
5 | ”Anvendelse af biogas til el- og varmeproduktion”, Ea Energianalyse, 2014.
7 | ”Introduktion til produktion af biometan fra biogas”, Biometan Regioner, 2013.

## 83 Gasif. Fixed Bed, Producer
| Technology | Gasifier, biomass, producer gas, small - medium scale
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref.
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical fuel input capacity, one unit (MWth) | 20 | 20 | 20 | 20 |  |  |  |  | A | 1,2,8
- Input
| Biomass (% of input capacity) | 98 | 98 | 98 | 98
| Electricity (% of input capacity) | 2 | 2 | 2 | 2
- Output
| Producer gas (% of fuel input) | 74 | 75 | 77 | 83 | 60 | 80 | 80 | 90 | C | 3,4,5,8,11
| Heat (% of input) | 10 | 10 | 9 | 5 |  |  |  |  | B | 3,4,5,8,11
| Unplanned outage (%) | 5 | 5 | 5 | 5 | [5 empty] | 1,2,8
| Planned outage (weeks per year) | 3 | 3 | 3 | 3 | [5 empty] | 1,2,8
| Technical lifetime (years) | 20 | 20 | 20 | 20 | [5 empty] | 1,2,8
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | [5 empty] | 1,2,8
Financial data
| Specific investment (M€/MWth) | 1.4 | 1.3 | 1.2 | 1.1 | 0.9 | 1.8 | 0.7 | 1.4 | D | 1,3,4,5
| - of which equipment | -
| - of which installation | -
| Fixed O&M (€/MWth/year) | 21000 | 20000 | 18000 | 16200 | 15000 | 24900 | 12100 | 20200 | D | 1,3,4,5
| Variable O&M (€/MWhth) | 2.6 | 2.5 | 2.2 | 2 | 1.7 | 3.3 | 1.4 | 2.7 | D | 1,3,4,5
Technology specific data
| Minimum load (% of full load) | 20 | 20 | 20 | 20 | [5 empty] | 8
References:
[18] | “Handbook Biomass Gasification”, Edited by H.A.M. Knoef, BTG biomass technology group, 2005.
3 | IEA Task 32, Workshop State of the art technologies for small biomass co-generation, 2010
4 | http://www.volund.dk/Biomass_energy/Technologies/Gasification_of_biomass
5 | BioSynergi, telefonkontakt Henrik Houman
Notes:
A | The stated capacity is the upper range, down scaling is possible.
B | With flue gas condensation, considering lower heating value of biomass fuel.
C | Producer gas primarily consists of the components N2, H2, CO, CO2, CH4, and water. Calorific value 5 - 6 MJ/Nm3. For some references ([3], [4]) the electric efficincy has been used to calculate gasifier efficiencies, assuming an engine efficiency of 42%.
D | Fixed bed gasifiers are usually integrated with an internal combustion gas engine gen-set. Sources are for total project including gas engine and the engine part has been deducted at 1.33 M€/Mwe and 42% efficiency. It is assumed that the accumulated production capacity will increase by 40 % between 2015 and 2020, double between 2020 and 2030 and between 2030 and 2050. A learning curve progress rate of 90 % is assumed this yields a 5 % decrease in investment costs between 2015 and 2020, 10 % reduction between 2020 and 2030 and between 2030 and 2050. Similar progress ratios have been used for O&M costs.
E | The values in [9] have been used (sh. 85) but adjusted to keep overall yearly O&M costs at 3% of investment
F | The values in [9] have been used. Variable O&M for a Staged down draft gasifier (sh. 85) have been subtracted O&M of a gas engine (sh. 06).
G | Efficiencies are expected to improve gradually from presently demonstrated levels, to cold gas efficiencies of 85% in 2050. It is assumed that a total efficiency of 90% can be obtained in 2050.

## 84 Gasif. CFB, Bio-SNG
| Technology | Gasifier, biomass, bio-SNG, medium - large scale
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical fuel input capacity, one unit (MWth) | 32 | 154 | 400 | 400 | [5 empty] | 12;13
| - Input | [8 empty] | B
| Biomass (% of input capacity) | 91 | 100 | 100 | 100
| Electricity (% of input capacity) | 9 | 0 | 0 | 0 |  |  |  |  | B
| - Output | [8 empty] | B
| Bio SNG (% of fuel input) | 56 | 60 | 63 | 70 | 58 | 65 | 65 | 75 | G | 21;19;13/17/19;
| Heat (% of input) | 15 | 20 | 22 | 20 |  |  |  |  | H | 21;19;13/17/19;
| Unplanned outage (%) | 3 | 3 | 3 | 3
| Planned outage (weeks per year) | 3 | 3 | 3 | 3
| Technical lifetime (years) | 15 | 20 | 20 | 20
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5
Financial data
| Specific investment (M€/MWth) | 4 | 2.5 | 1.6 | 1.5 | 1.8 | 3 | 1.4 | 2.6 | E | 12+21;12+19+13;15/17
| - of which equipment | -
| - of which installation | -
| Fixed O&M (€/MWth/year) | 80500 | 40200 | 26200 | 24100 | 30200 | 50300 | 18100 | 30200 | F | 12/21;12/21+13/17/19
| Variable O&M (€/MWhth) | 5.3 | 2.7 | 1.7 | 1.6 | 1.8 | 3.5 | 1.1 | 2.1 | F | 12/21;12/21+13/17/19
Technology specific data
| Warm start-up time (hours) | 6 | 6 | 6 | 6 |  |  |  |  | C
| Cold start-up time (hours) | 12 | 12 | 12 | 12 |  |  |  |  | C
Environment
| NOX (g per GJ fuel) | 16 | 20 | 20 | 20 |  |  |  |  | D | 23, 29
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 |  |  |  |  | D | 29
| N2O (g per GJ fuel) | 0.3 | 1 | 1 | 0 |  |  |  |  | D | 23, 29
References:
1 | Commissioning of the GoBiGas 20 MW biomethane plant. Thuman 2015
2 | Forgasning – Fase 2. Økonomi, videnindhentning og samarbejde. DGC Februar 2012.
3 | Gassner & Marechal, 2012
4 | Bio2G - A full scale reference plant in Sweden for production of bio-SNG, E.ON (Möller) 2013.
5 | Tunå & Hulteberg, 2014.
6 | Force, Technology data for advanced bioenergy fuels, 2013
Notes:
A | With flue gas condensation
B | Generally the plants' electricity generation is assumed to balance the consumption
C | Assumed to be in the same magnitude as a coal fired power plant
D | 2015 data for NOX and N2O origin from [23]. Other values are assumed to be in the same magnitude as a biomass fired PF power plant (pellets)
E | For 2015, values reflect the 20 MWgas Swedish GoBiGas Phase 1 demonstration project. A proportionality factor of 0.7 is assumed to apply when going from 2015 to 2020 based on the anticipated upscaling from 20 MWgas to 100 MWgas [21]. For 2030, the figure is an average of a value from theoretical studies [17] multiplied by 1.4 and a value from feasibility studies [19] multiplied by 1.15. From 2030 to 2050 simply a reduction of 10% has been assumed to reflect a learning curve.
F | Assumed that the total O&M costs splits in 1/3 variable, 2/3 fixed costs, 8000 h/year
G | Efficiencies are expected to improve gradually from presently demonstrated level, to values corresponding to various studies for large plants in 2030, and gradual increase to 2050. It is assumed that a total efficiency of 90% can be obtained.
H | Heat at normal district heating temprature set 80/50 deg. Additional low temperature heat for heat pumps is possible. For uncertainty values, a higher heat output can be expected at low gas output and vice versa.

## 85 Gasif. Ent. Flow FT, liq fu
Technology | Gasifier, biomass, Fischer Tropsch liquid fuels, large scale
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t FT Liquids/year | 50 | 50 | 100 | 125 | 150 | 100% | 150% | 50% | 150% | A, B | 1, 6
Typical total plant size, MW | 75 | 75 | 150 | 190 | 225 | 100% | 150% | 50% | 150% | A, A1, B | 1, 6
Inputs
Feedstock Consumption, MWh/MWh Total Input | 1 | 1 | 1 | 1 | 1 | 80% | 100% | 80% | 100% | C | 1
Outputs
Naphta Output, MWh/MWh Total Input | 0.1376 | 0.1376 | 0.14484 | 0.15389 | 0.16295 | 80% | 110% | 80% | 110% | D | 1
Jet Fuel Output, MWh/MWh Total Input | 0.0147 | 0.0147 | 0.015474 | 0.016441 | 0.017408 | 80% | 110% | 80% | 110% | D | 1
Diesel Output, MWh/MWh Total Input | 0.0998 | 0.0998 | 0.10505 | 0.11162 | 0.11818 | 80% | 110% | 80% | 110% | D | 1
Electricity Output, MWh/MWh Total Input | 0.0117 | 0.0117 | 0.016 | 0.018 | 0.02 | 80% | 110% | 80% | 110% | D | 1
Forced outage (%) | 4 | 4 | 0 | 0 | 0
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 20 | 25 | 25 | 25 | 25
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ /MW Liquids/year) | 4.329 | 4.329 | 3.8961 | 3.6184 | 3.4632 | 75% | 120% | 75% | 120% | E, L | 1, 6, 7, 8, 9
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW /year FT Liquids/year) | 0.1039 | 0.1039 | 0.1039 | 0.10263 | 0.1039 | 75% | 120% | 75% | 120% | L | 1
Variable O&M (€ /MWh FT Liquids/year) | 1.0626 | 1.0626 | 1.0626 | 1.0636 | 1.0626 | 75% | 120% | 75% | 120% | L | 1
Start up (M€ /1,000 t FT Liquids/year) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | F
Technology specific data
Specific energy content (GJ/ton) FT Diesel) | 44 | 44 | 44 | 44 | 44
Specific density (kg/l) or (ton/m3) | 0.77 | 0.77 | 0.77 | 0.77 | 0.77
Specific investment (M€ /1,000 t FT Liquids/year) | 6.4935 | 6.4935 | 5.8442 | 5.5 | 5.1948 | 75% | 120% | 75% | 120% | E, L | 1, 6, 7, 8, 9
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t FT Liquids/year) | 0.15584 | 0.15584 | 0.15584 | 0.156 | 0.15584 | 75% | 120% | 75% | 120% | L | 1
Variable O&M (M€ /1,000 t FT Liquids/year) | 0.012987 | 0.012987 | 0.012987 | 0.013 | 0.012987 | 75% | 120% | 75% | 120% | L | 1
Start up (M€ /1,000 t FT Liquids/year) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | F
Notes:
A. The plant size is assumed based on the proposed Velocys plant and the NREL nth plant.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year
B. Feedstock availability is likely to determine the maximum plant size.
C. The feedstock requirements could vary with efforts to improve the desired product selectivity.
D. Over time the power available for export may increase due to improve thermal management in the plant.
E. There is a wide range of reported capital costs for the existing plants and a wide range in the cost of future plants.
F. Start-up costs are included in the operating costs.
M €/k tonne is million euro per 1,000 tonnes
References
[1] Tan, E. C. D., Snowden-Swan, L. J., Talmadge, M., Dutta, A., Jones, S., Ramasamy, K. K., Gray, M., Dagle, R., Padmaperuma, A., Gerber, M., Sahir, A. H., Tao, L. and Zhang, Y. 2017. Comparative techno-economic analysis and process design for indirect liquefaction pathways to distillate-range fuels via biomass-derived oxygenated intermediates upgrading. Biofuels, Bioprod. Bioref., 11: 41–66. https://www.doi.org/10.1002/bbb.1710
[2] Kreutz, T., Larson, E., Liu, G., Williams, R. 2008. Fischer-Tropsch Fuels from Coal and Biomass. 25th Annual International Pittsburgh Coal Conference. http://acee.princeton.edu/wp-content/uploads/2016/10/Kreutz-et-al-PCC-2008-10-7-08.pdf
[3] Baliban, R., Elia, J., Floudas, C., Gurau, B., Weingarten, M., and Klotz, S. 2013. Hardwood Biomass to Gasoline, Diesel, and Jet Fuel: 1. Process Synthesis and Global Optimization of a Thermochemical Refinery. Energy & Fuels 2013 27 (8), 4302-4324. https://www.doi.org/10.1021/ef302003f
[4] Sikarwar, V., Zhao, M., Clough, P., Yao, J., Zhong, X., Memon, Shah, M., Anthony, E., and Fennell, P. 2016. An overview of advances in biomass gasification. Energy Environ. Sci. 2016, 9, 2939. https://doi.org/10.1039/C6EE00935B
[5] Molino, A., Chianese, S., Musmarra, D. 2016. Biomass gasification technology: The state of the art overview, In Journal of Energy Chemistry, Volume 25, Issue 1, 2016, Pages 10-25, ISSN 2095-4956, https://doi.org/10.1016/j.jechem.2015.11.005
[6] Velocys. 2017. The biomass-to-liquids process. http://www.velocys.com/our-biorefineries/
[7] Chandra, P.K. & Payne, Fred. 1986. Turndown Ratio of a Gasifier-Combustor Predicted by a Simulation Model. Transactions of the ASAE. 29. 1748-1753. https://doi.org/10.13031/2013.30383.
[8] Danish Energy Agency. 2017. Energy Statistics 2015. https://ens.dk/sites/ens.dk/files/Statistik/energy_statistics_2015.pdf
[9] Li X, Rubæk GH, Müller-Stöver DS, Thomsen TP, Ahrenfeldt J and Sørensen P. 2017. Plant Availability of Phosphorus in Five Gasification Biochars. Front. Sustain. Food Syst. 1:2. https://www.doi.org/10.3389/fsufs.2017.00002
[10] Velocys. 2017. Establishment of a strategic alliance with TRI. http://www.velocys.com/establishment-of-a-strategic-alliance-with-tri/
[11] Velocys. 2017. Velocys plans for the construction of a commercial BTL plant move forward. https://biorrefineria.blogspot.ca/2017/06/velocys-plans-for-construction-of-commercial-BTL-plant-move-forward.html
[12] Tijm, P. 1994. Shell Middle Distillate Synthesis: The Process, The Plant, The Products. http://web.anl.gov/PCS/acsfuel/preprint%20archive/Files/39_4_WASHINGTON%20DC_08-94_1146.pdf
[13] van der Laan, P. 1999. Kinetics, Selectivity and Scale Up of the Fischer-Tropsch Synthesis. http://www.adktroutguide.com/files/1999_Phd_Thesis_-_Kinetics_Selectivity_and_Scaleup_of_FT_Synthesis.pdf
[14] Industrial Equipment News. 2017. Mississippi Lands Biofuel Refinery. https://www.ien.com/operations/news/20980331/mississippi-lands-biofuel-refinery
[15] Irena. 2016. Innovation Outlook. Advanced Liquid Biofuels. http://www.irena.org/DocumentDownloads/Publications/IRENA_Innovation_Outlook_Advanced_Liquid_Biofuels_2016.pdf
[16] Sub Group on Advanced Biofuels. 2017. Cost of Biofuel. http://platformduurzamebiobrandstoffen.nl/wp-content/uploads/2017/07/2017_SGAB_Cost-of-Biofuels.pdf
[17] de Jong, S., Hoefnagels, R., Faaij, A., Slade, R., Mawhood, R. and Junginger, M. 2015. The feasibility of short-term production strategies for renewable jet fuels – a comprehensive techno-economic comparison. Biofuels, Bioprod. Bioref., 9: 778–800. https://www.doi.org/10.1002/bbb.1613

## 86 AEC 1MW
| Technology | Hydrogen production via alkaline electrolysis (AEC) for 1MW plant
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input_e) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Typical total plant size (kgH2 / day of max output) | 478.8 | 489.6 | 514.8 | 540 | 453.6 | 504 | 504 | 576 | L, E
- Inputs
| Electricity (% total input (MWh / MWh)) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Water for electrolysis (kg / MWh input_e) | 179.568 | 183.6184 | 193.0693 | 202.5203 | 170.117 | 189.0189 | 189.0189 | 216.0216
- Outputs
| Hydrogen (% total input_e (MWh / MWh)) | 66.5 | 68 | 71.5 | 75 | 63 | 70 | 70 | 80 | B | [24]
| ΔE from HHV to LHV (% total input_e (MWh / MWh)) | 12.1109 | 12.384 | 13.0215 | 13.6589 | 11.4734 | 12.7483 | 12.7483 | 14.5695 | N
| Heat loss (% total input_e (MWh / MWh)) | 21.3891 | 19.616 | 15.4785 | 11.3411 | 25.5266 | 17.2517 | 17.2517 | 5.4305
| - hereof unrecoverable heat loss (%-points of heat loss) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | A
| - hereof recoverable for district heating (%-points of heat loss) | 16.3891 | 14.616 | 10.4785 | 6.3411 | 20.5266 | 12.2517 | 12.2517 | 0.43054 | K
| Hydrogen (kg / MWh input_e) | 19.952 | 20.402 | 21.4521 | 22.5023 | 18.9019 | 21.0021 | 21.0021 | 24.0024 | B | [24]
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Planned outage (days per year) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Technical lifetime (years) | 25 | 30 | 32 | 35 | 25 | 25 | 30 | 35 | C, J | [27]
| Construction time (years) | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | C, O
Financial data (2020 price level)
| Specific investment (€ / kW of total input_e) | 750 | 570 | 450 | 350 | 500 | 1400 | 200 | 700 | D, I
| Specific investment (€ / kgH2 / day of max output) | 1566.416 | 1164.2157 | 874.1259 | 648.1481 | 1102.2928 | 2777.7778 | 396.8254 | 1215.2778 | E, I, L
| - hereof equipment (%) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | F
| - hereof installation (%) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | F
| Fixed O&M (% of specific investment / year) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | G, I, J | [26]
| Variable O&M (€ / kWh of total input) | - | - | - | - |  |  |  |  | M
| Startup cost (€ / kW of total input per startup) | - | - | - | -
Technology specific data
| Current Density (A / cm2) | 0.6 | 1 | 1.2 | 1.5 | 0.4 | 0.6 | 1.2 | 1.5 | H | [21]
| Footprint (m2 / MW input_e) | 12.5 | 10 | 8 | 7.5 | 10 | 15 | 5 | 10 | H | [21]
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | 5% of the energy is estimated to be unrecoverable for small plants.
B | Values are from Table 5 in IEA [24], Today is understood as 2020, Long-term is understood as 2050 and the value selected is the mid of the range given.
C | According to the Green Hydrogen Systems (GHS).
D | The price estimates are from Green Hydrogen Systems.
E | For the unit regarding "day" a 100% load factor is assummed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily fullload hours may vary and should therefore be adjusted for.
F | These are rough estimates based on operational AEC systems as provided by GHS.
G | O&M is estimated as 5% of CAPEX for small systems. According to the 2-5% given for large to small scale systems from [26].
H | The values are predicted until 2050 with a high margin of uncertainty. For 2030, the values are quite reasonable according to GHS.
I | The CAPEX includes all components required for converting 400VAC electricity and purified water into H2 gas at 35 bar and a waste heat stream at 50 °C. CAPEX does not include transformer, water purifier, heat pumps for increasing the temperature of waste heat stream or compressors for increasing the pressure of H2 further than 35 bar. The tariffs, capacity payments and network connection fees to DSO / TSO are not contained in CAPEX nor in O&M
J | The lifetime of current AEC stacks is more than 100 000 hours according to Green Hydrogen Systems. Assuming that the facility is run for 4000h pr year, the stacks do not need replacement in the technical lifetime. If the full load hours exceed the 100 000h lifetime, then the stack replacement cost will be 30% of the CAPEX cost of a new system in the year of replacement. Everfuel gives a stack replacement of 30% of CAPEX and GHS informs that 30% of current CAPEX is stack cost. The cost of replacing the stack is not included in fixed O&M.
K | 50 °C (expected to increase to 70°C, by 2024)
L | Maximum hydrogen output per day, assuming 24 hours of full load operation in a day.
M | The price of the input streams (water and electric energy), has not been estimated.
N | The HHV electorlyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
O | From the time of purchase to finished construction
References:
21 | H. Europe, “Strategic research and innovation agenda for lightweight,” no. July, p. 157, 2020.
16 | Green Hydrogen Systems, “HyProvide TM A-Series.”
24 | “The Future of Hydrogen,” Futur. Hydrog., no. June, 2019, doi: 10.1787/1e0514c4-en.
26 | “Development of Water Electrolysis in the European Union ¦ www.fch.europa.eu.” https://www.fch.europa.eu/node/783 (accessed Dec. 17, 2020).
27 | J. Ivy, “Summary of electrolytic hydrogen production,” Small, no. September, p. 27, 2004, [Online]. Available: http://www.nrel.gov/docs/fy04osti/35948.pdf.

## 86 AEC 100MW
| Technology | Hydrogen production via alkaline electrolysis (AEC) for 100MW plant
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input_e) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Typical total plant size (kgH2 / day of max output) | 47880 | 48960 | 51480 | 54000 | 45360 | 50400 | 50400 | 57600 | L, E
- Inputs
| Electricity (% total input (MWh / MWh)) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Water for electrolysis (kg / MWh input_e) | 179.568 | 183.6184 | 193.0693 | 202.5203 | 170.117 | 189.0189 | 189.0189 | 216.0216
- Outputs
| Hydrogen (% total input_e (MWh / MWh)) | 66.5 | 68 | 71.5 | 75 | 63 | 70 | 70 | 80 | B | [24]
| ΔE from HHV to LHV (% total input_e (MWh / MWh)) | 12.1109 | 12.384 | 13.0215 | 13.6589 | 11.4734 | 12.7483 | 12.7483 | 14.5695 | N
| Heat loss (% total input_e (MWh / MWh)) | 21.3891 | 19.616 | 15.4785 | 11.3411 | 25.5266 | 17.2517 | 17.2517 | 5.4305
| - hereof unrecoverable heat loss (%-points of heat loss) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | A
| - hereof recoverable for district heating (%-points of heat loss) | 18.3891 | 16.616 | 12.4785 | 8.3411 | 22.5266 | 14.2517 | 14.2517 | 2.4305 | K
| Hydrogen (kg / MWh input_e) | 19.952 | 20.402 | 21.4521 | 22.5023 | 18.9019 | 21.0021 | 21.0021 | 24.0024 | B | [24]
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Planned outage (days per year) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Technical lifetime (years) | 25 | 30 | 32 | 35 | 25 | 25 | 30 | 35 | C, J | [27]
| Construction time (years) | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | C, O
Financial data (2020 price level)
| Specific investment (€ / kW of total input_e) | 650 | 450 | 300 | 250 | 400 | 800 | 150 | 400 | D, I
| Specific investment (€ / kgH2 / day of max output) | 1357.5606 | 919.1176 | 582.7506 | 462.963 | 881.8342 | 1587.3016 | 297.619 | 694.4444 | E, I, L
| - hereof equipment (%) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | F
| - hereof installation (%) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | F
| Fixed O&M (% of specific investment / year) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G, I, J | [26]
| Variable O&M (€ / kWh of total input) | - | - | - | - |  |  |  |  | M
| Startup cost (€ / kW of total input per startup) | - | - | - | -
Technology specific data
| Current Density (A / cm2) | 0.6 | 1 | 1.2 | 1.5 | 0.4 | 0.6 | 1.2 | 1.5 | H | [21]
| Footprint (m2 / MW input_e) | 12.5 | 10 | 8 | 7.5 | 10 | 15 | 5 | 10 | H | [21]
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | 3% of the energy is estimated to be unrecoverable for large plants.
B | Values are from Table 5 in IEA [24], Today is understood as 2020, Long-term is understood as 2050 and the value selected is the mid of the range given.
C | According to the Green Hydrogen Systems.
D | CAPEX values from interviews with GHS, Everfuel and NEL and reports from IEA [24], HyEurope [21] and IRENA [24]. The values in the datasheet correspond to a fitted curve see figure 6 in the catalogue. For IEA today is taken to be 2020, Long term is taken to be 2050 and values is the middle of the range given.
E | For the unit regarding "day" a 100% load factor is assummed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily fullload hours may vary and should therefor be adjusted for.
F | These are rough estimates based on operational AEC systems as provided by the Green Hydrogen Systems.
G | O&M is estimated as 2% of CAPEX for large systems. According to the 2-5% given for large to small scale systems from [26].
H | The values are predicted until 2050 with a high margin of uncertainty.
I | The CAPEX includes all components required for converting 400VAC electricity and purified water into H2 gas at 35 bar and a waste heat stream at 50 °C. CAPEX does not include transformer, water purifier, heat pumps for increasing the temperature of waste heat stream or compressors for increasing the pressure of H2 further than 35 bar. The tariffs, capacity payments and network connection fees to DSO / TSO are not contained in CAPEX nor in O&M
J | The lifetime of current AEC stacks is more than 100 000 hours according to Green Hydrogen Systems. Assuming that the facility is run for 4000h pr year, the stacks do not need replacement in the technical lifetime. If the full load hours exceed the 100 000h lifetime, then the stack replacement cost will be 30% of the CAPEX cost of a new system in the year of replacement. Everfuel gives a stack replacement of 30% of CAPEX and GHS informs that 30% of current CAPEX is stack cost. The cost of replacing the stack is not included in fixed O&M.
K | 50 °C (expected to increase to 70°C, by 2024)
L | Maximum hydrogen output per day, assuming 24 hours of full load operation in a day.
M | The price of the input streams (water and electric energy), has not been estimated.
N | The HHV electorlyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
O | From the time of purchase to finished construction
References:
21 | H. Europe, “Strategic research and innovation agenda for lightweight,” no. July, p. 157, 2020.
24 | “The Future of Hydrogen,” Futur. Hydrog., no. June, 2019, doi: 10.1787/1e0514c4-en.
26 | “Development of Water Electrolysis in the European Union ¦ www.fch.europa.eu.” https://www.fch.europa.eu/node/783 (accessed Dec. 17, 2020).
27 | J. Ivy, “Summary of electrolytic hydrogen production,” Small, no. September, p. 27, 2004, [Online]. Available: http://www.nrel.gov/docs/fy04osti/35948.pdf.

## 86 PEMEC 1MW
| Technology | Hydrogen production via PEM electrolysis for 1MW plant
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input_e) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Typical total plant size (kgH2 / day of max output) | 417.6 | 471.6 | 489.6 | 507.6 | 432 | 460.8 | 489.6 | 504 | L, E
- Inputs
| Electricity (% total input (MWh / MWh)) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Water for electrolysis (kg / MWh input_e) | 156.6157 | 176.8677 | 183.6184 | 190.369 | 162.0162 | 172.8173 | 183.6184 | 189.0189
- Outputs
| Hydrogen (% total input_e (MWh / MWh)) | 58 | 65.5 | 68 | 70.5 | 60 | 64 | 68 | 70 | B | [24]
| ΔE from HHV to LHV (% total input_e (MWh / MWh)) | 10.5629 | 11.9287 | 12.384 | 12.8393 | 10.9271 | 11.6556 | 12.384 | 12.7483 | N
| Heat loss (% total input_e (MWh / MWh)) | 31.4371 | 22.5713 | 19.616 | 16.6607 | 29.0729 | 24.3444 | 19.616 | 17.2517
| - hereof unrecoverable heat loss (%-points of heat loss) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | A
| - hereof recoverable for district heating (%-points of heat loss) | 26.4371 | 17.5713 | 14.616 | 11.6607 | 24.0729 | 19.3444 | 14.616 | 12.2517 | K
| Hydrogen (kg / MWh input_e) | 17.4017 | 19.652 | 20.402 | 21.1521 | 18.0018 | 19.2019 | 20.402 | 21.0021 | B | [24]
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Planned outage (days per year) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Technical lifetime (years) | 20 | 25 | 28 | 30 | 20 | 20 | 25 | 30 | C, J | [27]
| Construction time (years) | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | C, O
Financial data (2020 price level)
| Specific investment (€ / kW of total input_e) | 925 | 650 | 450 | 400 | 700 | 1250 | 300 | 500 | D, I
| Specific investment (€ / kgH2 / day of max output) | 2214.8168 | 1378.1489 | 919.0257 | 787.9433 | 1620.2083 | 2712.4023 | 612.6838 | 991.9643 | E, I, L
| - hereof equipment (%) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | F
| - hereof installation (%) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | F
| Fixed O&M (% of specific investment / year) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | G, I, J
| Variable O&M (€ / kWh of total input) | - | - | - | - |  |  |  |  | M
| Startup cost (€ / kW of total input per startup) | - | - | - | -
Technology specific data
| Current Density (A / cm2) | 2.2 | 3.5 | 3.8 | 4 | 2.2 | 2.2 | 3.2 | 4 |  | [21]
| Footprint (m2 / MW input_e) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | 5% of the energy is estimated to be unrecoverable for small plants.
B | Values are from Table 5 in IEA [24], Today is understood as 2020, Long-term is understood as 2050 and the value selected is the mid of the range given.
C | According to the Green Hydrogen Systems (GHS).
D | CAPEX values from interviews with GHS and Siemens and reports from IEA [24], HyEurope [21] and IRENA [24]. The values in the datasheet correspond to a fitted curve see figure 6 in the catalogue. For IEA today is taken to be 2020, Long term is taken to be 2050 and values is the middle of the range given.
E | For the unit regarding "day" a 100% load factor is assummed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily fullload hours may vary and should therefor be adjusted for.
F | These are rough estimates based on existing systems according to GHS.
G | O&M is estimated as 7% of CAPEX. 5%-point is for small systems, according to the 2-5% given for large to small scale systems from [26]. 2%-points is the estimated stack replacement cost. Everfuel and GHS reports that the 30% of CAPEX is stack cost. At about 4000 full load hours per year, stacks are likely to be replaced twice during the technical lifetime.
H | This value is fixed due to no increase in research in increasing the pressure of PEMEC systems.
I | The CAPEX includes all components required for converting 400VAC electricity and purified water into H2 gas at 35 bar and a waste heat stream at 50 °C. CAPEX does not include transformer, water purifier, heat pumps for increasing the temperature of waste heat stream or compressors for increasing the pressure of H2 further than 35 bar. The tariffs, capacity payments and network connection fees to DSO / TSO are not contained in CAPEX nor in O&M
J | The lifetime of current PEMEC stacks is more than 25000 hours and in the future it could be more than 50000 hours according to Green Hydrogen Systems.
K | 50 °C (expected to increase to 70°C, by 2024)
L | Maximum hydrogen output per day, assuming 24 hours of full load operation in a day.
M | The price of the input streams (water and electric energy), has not been estimated.
N | The HHV electorlyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
O | From the time of purchase to finished construction
References:
21 | H. Europe, “Strategic research and innovation agenda for lightweight,” no. July, p. 157, 2020.
24 | “The Future of Hydrogen,” Futur. Hydrog., no. June, 2019, doi: 10.1787/1e0514c4-en.
26 | “Development of Water Electrolysis in the European Union ¦ www.fch.europa.eu.” https://www.fch.europa.eu/node/783 (accessed Dec. 17, 2020).
27 | J. Ivy, “Summary of electrolytic hydrogen production,” Small, no. September, p. 27, 2004, [Online]. Available: http://www.nrel.gov/docs/fy04osti/35948.pdf.

## 86 PEMEC 100MW
| Technology | Hydrogen production via PEM electrolysis for 100MW plant
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input_e) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Typical total plant size (kgH2 / day of max output) | 41760 | 47160 | 48960 | 50760 | 43200 | 46080 | 48960 | 50400 | L, E
- Inputs
| Electricity (% total input (MWh / MWh)) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Water for electrolysis (kg / MWh input_e) | 156.6157 | 176.8677 | 183.6184 | 190.369 | 162.0162 | 172.8173 | 183.6184 | 189.0189
- Outputs
| Hydrogen (% total input_e (MWh / MWh)) | 58 | 65.5 | 68 | 70.5 | 60 | 64 | 68 | 70 | B | [24]
| ΔE from HHV to LHV (% total input_e (MWh / MWh)) | 10.5629 | 11.9287 | 12.384 | 12.8393 | 10.9271 | 11.6556 | 12.384 | 12.7483 | N
| Heat loss (% total input_e (MWh / MWh)) | 31.4371 | 22.5713 | 19.616 | 16.6607 | 29.0729 | 24.3444 | 19.616 | 17.2517
| - hereof unrecoverable heat loss (%-points of heat loss) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | A
| - hereof recoverable for district heating (%-points of heat loss) | 28.4371 | 19.5713 | 16.616 | 13.6607 | 26.0729 | 21.3444 | 16.616 | 14.2517 | K
| Hydrogen (kg / MWh input_e) | 17.4017 | 19.652 | 20.402 | 21.1521 | 18.0018 | 19.2019 | 20.402 | 21.0021 |  | [24]
| Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Planned outage (days per year) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | C
| Technical lifetime (years) | 20 | 25 | 28 | 30 | 20 | 20 | 25 | 30 | C, J | [27]
| Construction time (years) | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | C, O
Financial data (2020 price level)
| Specific investment (€ / kW of total input_e) | 925 | 650 | 450 | 400 | 700 | 1250 | 300 | 500 | D, I
| Specific investment (€ / kgH2 / day of max output) | 2214.8168 | 1378.1489 | 919.0257 | 787.9433 | 1620.2083 | 2712.4023 | 612.6838 | 991.9643 | E, I, L
| - hereof equipment (%) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | F
| - hereof installation (%) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | F
| Fixed O&M (% of specific investment / year) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | G, I, J
| Variable O&M (€ / kWh of total input) | - | - | - | - |  |  |  |  | M
| Startup cost (€ / kW of total input per startup) | - | - | - | -
Technology specific data
| Current Density (A / cm2) | 2.2 | 3.5 | 3.8 | 4 | 2.2 | 2.2 | 3.2 | 4 |  | [21]
| Footprint (m2 / MW input_e) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | H
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | 3% of the energy is estimated to be unrecoverable for large plants.
B | Values are from Table 5 in IEA [24], Today is understood as 2020, Long-term is understood as 2050 and the value selected is the mid of the range given.
C | According to the Green Hydrogen Systems (GHS).
D | CAPEX values from interviews with GHS and Siemens and reports from IEA [24], HyEurope [21] and IRENA [24]. The values in the datasheet correspond to a fitted curve see figure 6 in the catalogue. For IEA today is taken to be 2020, Long term is taken to be 2050 and values is the middle of the range given.
E | For the unit regarding "day" a 100% load factor is assummed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily fullload hours may vary and should therefor be adjusted for.
F | These are rough estimates based on existing systems according to GHS.
G | O&M is estimated as 4% of CAPEX. 2%-point is for small systems, according to the 2-5% given for large to small scale systems from [26]. 2%-points is the estimated stack replacement cost. Everfuel and GHS reports that the 30% of CAPEX is stack cost. At about 4000 full load hours per year, stacks are likely to be replaced twice during the technical lifetime.
H | This value is fixed due to no increase in research in increasing the pressure of PEMEC systems.
I | The CAPEX includes all components required for converting 400VAC electricity and purified water into H2 gas at 35 bar and a waste heat stream at 50 °C. CAPEX does not include transformer, water purifier, heat pumps for increasing the temperature of waste heat stream or compressors for increasing the pressure of H2 further than 35 bar. The tariffs, capacity payments and network connection fees to DSO / TSO are not contained in CAPEX nor in O&M
J | The lifetime of current PEMEC stacks is more than 25000 hours and in the future it could be more than 50000 hours according to Green Hydrogen Systems.
K | 50 °C (expected to increase to 70°C, by 2024)
L | Maximum hydrogen output per day, assuming 24 hours of full load operation in a day.
M | The price of the input streams (water and electric energy), has not been estimated.
N | The HHV electorlyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
O | From the time of purchase to finished construction
References:
21 | H. Europe, “Strategic research and innovation agenda for lightweight,” no. July, p. 157, 2020.
24 | “The Future of Hydrogen,” Futur. Hydrog., no. June, 2019, doi: 10.1787/1e0514c4-en.
26 | “Development of Water Electrolysis in the European Union ¦ www.fch.europa.eu.” https://www.fch.europa.eu/node/783 (accessed Dec. 17, 2020).
27 | J. Ivy, “Summary of electrolytic hydrogen production,” Small, no. September, p. 27, 2004, [Online]. Available: http://www.nrel.gov/docs/fy04osti/35948.pdf.

## 86 SOEC 1MW
| Technology | Hydrogen production via solid oxide electrolysis (SOEC) for 1MW plant
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A
| Typical total plant size (kgH2 / day of max output) | 558 | 579.6 | 590.4 | 601.2 | 532.8 | 583.2 | 554.4 | 609.12 | E
- Inputs
| Electricity (% total input (MWh / MWh)) | 79.5 | 80.5 | 81.4 | 81.4 | 79 | 82 | 81 | 83 | A
| Heat (% total input (MWh / MWh)) | 20.5 | 19.5 | 18.6 | 18.6 | 21 | 18 | 19 | 17
| Water for electrolysis (kg / MWh input) | 209.2709 | 217.3717 | 221.4221 | 225.4725 | 199.82 | 218.7219 | 207.9208 | 228.4428
- Outputs
| Hydrogen (% total input (MWh / MWh)) | 77.5 | 80.5 | 82 | 83.5 | 74 | 81 | 77 | 84.6 | B, D | [24]
| ΔE from HHV to LHV (% total input (MWh / MWh)) | 14.1142 | 14.6605 | 14.9337 | 15.2069 | 13.4767 | 14.7516 | 14.0231 | 15.4072 | H
| Heat loss (% total input (MWh / MWh)) | 8.3858 | 4.8395 | 3.0663 | 1.2931 | 12.5233 | 4.2484 | 8.9769 | -0.0072007
| Hydrogen (kg / MWh input) | 23.2523 | 24.1524 | 24.6025 | 25.0525 | 22.2022 | 24.3024 | 23.1023 | 25.3825
| Forced outage (%) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | A
| Planned outage (days per year) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | A
| Technical lifetime (years) | 10 | 20 | 20 | 20 | 10 | 10 | 15 | 20 | A
| Construction time (months) | 4 | 0.5 | 0.5 | 0.5 | 4 | 4 | 0.5 | 1 | A
Financial data (2020 price level)
| Specific investment (€ / kW of total input) | 4490.566 | 1900.6211 | 1341.8953 | 783.1695 | 3012.6582 | 5804.878 | 524.6914 | 1024.0964 | D, G | [24]
| Specific investment (€ / kgH2 / day of max output) | 8046.8046 | 3278.8666 | 2272.6307 | 1302.5469 | 5653.8231 | 9952.4992 | 946.3183 | 1681.1038 | D, G, E | [24]
| - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | A
| - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | A
| Fixed O&M (% of specific investment / year) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E, G, I | [21]
| Variable O&M (€ / kWh of total input) | - | - | - | - |  |  |  |  | F
| Startup cost (€ / kW of total input per startup) | - | - | - | -
Technology specific data
| Current Density (A / cm2) | 0.65 | 1 | 1.5 | 1.5 | 0.5 | 0.65 | 1.5 | 1.8 |  | [21]
| Footprint (m2 / MW input_e) | 35 | 20 | 15 | 10 | 35 | 35 | 10 | 20 |  | [21]
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | Input from Haldor Topsoe
B | The efficiencies are assumed to be system efficiencies. IEA gives the values as electric efficiencies, however the references of IEA gives both system efficiencies and electric efficiencies. See for instance Buttler and Spliethoff (2018), "Current status of water electrolysis for energy storage, grid balancing and sector coupling via power-to-gas and power-to-liquids: A review". This assumption adds significant uncertainty to these values. However no good alternative was found.
C | For the unit regarding "day" a 100% load factor is assummed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily fullload hours may vary and should therefor be adjusted for.
D | Values are from Table 5 in IEA [24], Today is understood as 2020, Long-term is understood as 2050 and the value selected is the mid of the range given. For conversion a conversion of 0.85€/$ was used.
E | O&M is estimated as 12% of CAPEX. 5%-point is for small systems, according to the 2-5% given for large to small scale systems from [26]. 7%-points is the estimated stack replacement cost. Ceres Power gives a stack replacement cost of 20% of CAPEX. At about 6000 full load hours per year, stacks are likely to be replaced every three and a third years.
F | The price of the input streams (steam and electric energy), has not been estimated.
G | The CAPEX includes all components required for converting 400VAC electricity and purified water into H2 gas at 35 bar. CAPEX does not include transformer, water purifier or compressors for increasing the pressure of H2 further than 35 bar. The tariffs, capacity payments and network connection fees to DSO / TSO are not contained in CAPEX nor in O&M
H | The HHV electorlyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
I | The lifetime of current SOEC stacks is about 20000 hours and is expected to increase in the future [24], and is expected to increase in the future
References:
21 | H. Europe, “Strategic research and innovation agenda for lightweight,” no. July, p. 157, 2020.
24 | “The Future of Hydrogen,” Futur. Hydrog., no. June, 2019, doi: 10.1787/1e0514c4-en.
26 | “Development of Water Electrolysis in the European Union ¦ www.fch.europa.eu.” https://www.fch.europa.eu/node/783 (accessed Dec. 17, 2020).

## 89 Vegetable oil FAME
Technology | Vegetable Oil FAME
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t biodiesel/year | 100 | 100 | 100 | 100 | 100 | 50% | 200% | 50% | 200% | A | 1
Typical total plant size MW biodiesel | 125 | 125 | 125 | 125 | 125 | 50% | 200% | 50% | 200% | A1
Inputs
Veg Oil Consumption, MWh/MWh Total Input | 0.925 | 0.926 | 0.929 | 0.931 | 0.933 | 99% | 101% | 99% | 101% | E,I | 4
Methanol Consumption, MWh/MWh Total Input | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 93% | 107% | 93% | 107% | B,E,I | 4
Electricity Consumption, MWh/MWh Total Input | 0.004 | 0.004 | 0.003 | 0.0025 | 0.002 | 50% | 150% | 75% | 125% | E,I | 4
Natural Gas Consumption, MWh/MWh Total Input | 0.025 | 0.024 | 0.022 | 0.02 | 0.018 | 50% | 150% | 75% | 125% | E,I | 4
Outputs
Biodiesel Output, MWh/MWh Total Input | 0.903 | 0.903 | 0.903 | 0.903 | 0.903 | 99% | 101% | 99% | 101% | F | 4
Glycerine Output, MWh/MWh Total Input | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 99% | 101% | 99% | 101% | F | 4
Forced outage (%) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | H
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Financial data
Specific investment (M € /MW) | 0.512 | 0.504 | 0.496 | 0.49 | 0.48 | 90% | 110% | 90% | 110% | C, J, L
- equipment (%) | 75 | 75 | 75 | 75 | 75 |  |  |  |  | G
- installation (%) | 25 | 25 | 25 | 25 | 25 |  |  |  |  | G
Fixed O&M (M € /MW/year) | 0.0176 | 0.0176 | 0.0176 | 0.0176 | 0.0176 | 90% | 110% | 90% | 110% | D, K, L
Variable O&M (€ /MWh) | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 90% | 110% | 90% | 110% | D, K, L
Start-up (M € /MW) | 0 | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) biodiesel) | 37.2 | 37.2 | 37.2 | 37.2 | 37.2
Specific density (kg/l) or (ton/m3) | 0.885 | 0.885 | 0.885 | 0.885 | 0.885
Specific investment (M € /1,000 t biodiesel/year) | 0.64 | 0.63 | 0.62 | 0.61 | 0.6 | 90% | 110% | 90% | 110% | C, J
- equipment (%) | 75 | 75 | 75 | 75 | 75 |  |  |  |  | G
- installation (%) | 25 | 25 | 25 | 25 | 25 |  |  |  |  | G
Fixed O&M (M € /1,000 t biodiesel) | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 90% | 110% | 90% | 110% | D, K, L
Variable O&M (M € /1,000 t biodiesel) | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 90% | 110% | 90% | 110% | D, K, L
Notes:
A. The plant size is assumed based on the plants sizes of existing vegetable oil based bio-diesel plants in EU.
A1. This value is the hourly rating and has been calculated as if the unit produces 100,000 t/year and was in operations 8,000 h/year.
B. Energy input from supporting chemicals of minor amounts is not considered.
C. The total capital cost include total installed cost (total direct costs) and all indirect costs such as engineering, construction, contractor’s fee, contingency and working capital.
D. O&M costs, costs for main raw materials are not included
E. 2050 values are based on industry best plant in 2015. 2020 and 2030 values interpolated between 2015 and 2050 values.
F. Total output excludes the heat loss.
G. Estimated from Iowa State biodiesel profitability file.
H. Best plants operate at greater than 95% of capacity.
I. The uncertainty is one standard deviation from the average from the NBB survey.
J. Range of capital cost is +/- 25% of mean.
K. Operating cost is +/- 10% of mean.
L. M €/k tonne is million euro per 1,000 tonnes
References
[1] Personal Communication. 2018. T Jensen, Emmelev A/S
[2] International Institute for Sustainable Development. 2012. Biofuels – At What Cost? Mandating ethanol and biodiesel consumption in Germany. https://www.iisd.org/gsi/sites/default/files/bf_awc_germany.pdf
[3] Desmet Ballestra. 2015. Biodiesel. http://www.desmetballestra.com/images/PDF-Brochures-2014/Biodiesel2015.pdf
[4] US Energy Information Administration. 2015. International Energy Statistics. Biofuels Production. http://www.eia.gov/cfapps/ipdbproject/IEDIndex3.cfm?tid=79&pid=79&aid=1
[5] Energy Statistics 2015. https://ens.dk/sites/ens.dk/files/Statistik/energy_statistics_2015.pdf
[6] IEA Bioenergy Task 39. Newsletter #39. Denmark Feature. http://task39.sites.olt.ubc.ca/files/2015/06/IEA-Bioenergy-Task-39-Newsletter-Issue-39-May-2015-final.pdf
[7] Chen, R., Qin, Z., Han, J., Wang, M., Taheripour, F., Tyner, W., O'Connor, D., Duffield, J. 2018. Life cycle energy and greenhouse gas emission effects of biodiesel in the United States with induced land use change impacts. Bioresource Technology, Volume 251, 2018, Pages 249-258, ISSN 0960-8524, https://doi.org/10.1016/j.biortech.2017.12.031.
[8] Cargill. 2017. Cargill to build state of- the-art biodiesel plant in Wichita, Kansas. https://www.cargill.com/2017/cargill-to-build-state-of-the-art-biodiesel-plant-in-wichita-ks
[9] IRENA. 2013. Road Transport: The Cost of Renewable Solutions. http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2013/Road_Transport.ashx
[10] Berghout, Niels. (2008). Technological learning in the German biodiesel industry: An experience curve approach to quantify reductions in production costs, energy use and greenhouse gas emissions. http://task39.sites.olt.ubc.ca/files/2013/05/Technological-learning-in-the-German-Biodiesel-Industry.pdf
[11] Iowa State University. 2017. Biodiesel Profitability. http://www.extension.iastate.edu/agdm/energy/xls/d1-15biodieselprofitability.xlsx

## 90 UCO & animal fat FAME
Technology | UCO and Animal Fat FAME
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t biodiesel/year | 50 | 50 | 50 | 50 | 50 | 50% | 200% | 50% | 200% | A | 1
Typical total plant size MW biodiesel/year | 60 | 60 | 60 | 60 | 60 | 50% | 200% | 50% | 200% | A1
Inputs
Veg Oil Consumption, MWh/MWh Total Input | 0.906 | 0.909 | 0.912 | 0.912 | 0.912 | 99% | 101% | 99% | 101% | E,I | 1
Methanol Consumption, MWh/MWh Total Input | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 93% | 107% | 93% | 107% | B,E,I | 1
Electricity Consumption, MWh/MWh Total Input | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 50% | 150% | 50% | 150% | E,I | 1
Natural Gas Consumption, MWh/MWh Total Input | 0.044 | 0.04 | 0.036 | 0.034 | 0.032 | 50% | 50% | 50% | 50% | E,I | 1
Outputs
Biodiesel Output, MWH/MWh | 0.84 | 0.85 | 0.86 | 0.86 | 0.87 | 99% | 101% | 99% | 101% | F | 1
Glycerine Output, MWH/MWh Total Input | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 99% | 101% | 99% | 101% | F | 1
Forced outage (%) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | H
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Financial data
Specific investment (M € /MW) | 1.0812 | 1.0161 | 0.93483 | 0.89419 | 0.84 | 80% | 120% | 90% | 110% | C, J, L | 3
- equipment (%) | 75 | 75 | 75 | 75 | 75 |  |  |  |  | G
- installation (%) | 25 | 25 | 25 | 25 | 25 |  |  |  |  | G
Fixed O&M (M € /MW/year) | 0.12241 | 0.12241 | 0.12241 | 0.12241 | 0.12241 | 90% | 110% | 90% | 110% | D, K, L | 4
Variable O&M (€ /MWh) | 7.6544 | 7.6544 | 7.6544 | 7.6544 | 7.6544 | 90% | 110% | 90% | 110% | D, K, L | 4
Start-up (M € /MW) | 0 | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) biodiesel) | 37.2 | 37.2 | 37.2 | 37.2 | 37.2
Specific density (kg/l) or (ton/m3) | 0.885 | 0.885 | 0.885 | 0.885 | 0.885
Specific investment (M € /1,000 t biodiesel/year) | 1.33 | 1.25 | 1.15 | 1.1 | 1 | 80% | 120% | 90% | 110%
- equipment (%) | 75 | 75 | 75 | 75 | 75 |  |  |  |  | G
- installation (%) | 25 | 25 | 25 | 25 | 25 |  |  |  |  | G
Fixed O&M (M € /1,000 t biodiesel) | 0.14689 | 0.14689 | 0.14689 | 0.14689 | 0.14689 | 90% | 110% | 90% | 110% | D, K, L
Variable O&M (M € /1,000 t biodiesel) | 0.079096 | 0.079096 | 0.079096 | 0.079096 | 0.079096 | 90% | 110% | 90% | 110% | D, K, L
Notes:
A. The plant size is assumed based on the plants sizes of existing vegetable oil based bio-diesel plants in EU.
A1. This value is the hourly rating and has been calculated as if the unit produces 100,000 t/year and was in operations 8,000 h/year.
B. Energy input from supporting chemicals of minor amounts is not considered.
C. The total capital cost include total installed cost (total direct costs) and all indirect costs such as engineering, construction, contractor’s fee, contingency and working capital.
D. O&M costs, costs for main raw materials are not included
E. 2050 values are based on industry best plant in 2015. 2020 and 2030 values interpolated between 2015 and 2050 values.
F. Total output excludes the heat loss.
G. Estimated from Iowa State biodiesel profitability file.
H. Best plants operate at greater than 95% of capacity.
I. The uncertainty is one standard deviation from the average from the NBB survey.
J. Range of capital cost is +/- 25% of mean.
K. Operating cost is +/- 10% of mean.
L. M €/k tonne is million euro per 1,000 tonnes
References
[1] Personal Communication. 2018. T Jensen, Emmelev A/S
[2] International Institute for Sustainable Development. 2012. Biofuels – At What Cost? Mandating ethanol and biodiesel consumption in Germany. https://www.iisd.org/gsi/sites/default/files/bf_awc_germany.pdf
[3] Desmet Ballestra. 2015. Biodiesel. http://www.desmetballestra.com/images/PDF-Brochures-2014/Biodiesel2015.pdf
[4] US Energy Information Administration. 2015. International Energy Statistics. Biofuels Production. http://www.eia.gov/cfapps/ipdbproject/IEDIndex3.cfm?tid=79&pid=79&aid=1
[5] Energy Statistics 2015. https://ens.dk/sites/ens.dk/files/Statistik/energy_statistics_2015.pdf
[6] IEA Bioenergy Task 39. Newsletter #39. Denmark Feature. http://task39.sites.olt.ubc.ca/files/2015/06/IEA-Bioenergy-Task-39-Newsletter-Issue-39-May-2015-final.pdf
[7] Chen, R., Qin, Z., Han, J., Wang, M., Taheripour, F., Tyner, W., O'Connor, D., Duffield, J. 2018. Life cycle energy and greenhouse gas emission effects of biodiesel in the United States with induced land use change impacts. Bioresource Technology, Volume 251, 2018, Pages 249-258, ISSN 0960-8524, https://doi.org/10.1016/j.biortech.2017.12.031.
[8] Cargill. 2017. Cargill to build state of- the-art biodiesel plant in Wichita, Kansas. https://www.cargill.com/2017/cargill-to-build-state-of-the-art-biodiesel-plant-in-wichita-ks
[9] IRENA. 2013. Road Transport: The Cost of Renewable Solutions. http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2013/Road_Transport.ashx
[10] Berghout, Niels. (2008). Technological learning in the German biodiesel industry: An experience curve approach to quantify reductions in production costs, energy use and greenhouse gas emissions. http://task39.sites.olt.ubc.ca/files/2013/05/Technological-learning-in-the-German-Biodiesel-Industry.pdf
[11] Iowa State University. 2017. Biodiesel Profitability. http://www.extension.iastate.edu/agdm/energy/xls/d1-15biodieselprofitability.xlsx

## 91 Hydrogenated veg oil
Technology | HVO / renwable diesel
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t HVO/year | 500 | 500 | 750 | 850 | 1000 | 50% | 200% | 50% | 100% | A, B
Typical total plant size MW HVO | 730 | 730 | 1100 | 1250 | 1460 | 50% | 200% | 50% | 100% | A, A1, B
Inputs
Feedstock Consumption, MWh/MWh Total Inputs | 0.881 | 0.881 | 0.881 | 0.881 | 0.881 | 99% | 101% | 99% | 101% | C | 3,4,11
Hydrogen Consumption, MWh/MWh Total Inputs | 0.105 | 0.105 | 0.105 | 0.105 | 0.105 | 93% | 107% | 93% | 107% | C, D | 3,4,11
Electricity Consumption, MWh/MWh Total Inputs | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 50% | 150% | 50% | 150% | C | 3,4,11
Natural Gas Consumption, MWh/MWh Total Inputs | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 50% | 50% | 50% | 50% | C | 3,4,11
Outputs
HVO Output, MWh/MWh Total Input | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 99% | 101% | 99% | 101% | C, H
Naphta Output, MWh/MWh Total Input | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 99% | 101% | 99% | 101% | C, H
Fuel Gas Output, MWh/MWh Total Input | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 99% | 101% | 99% | 101% | C, H
LPG Output, MWh/MWh Total Input | 0.0275 | 0.0275 | 0.0275 | 0.0275 | 0.0275 | 99% | 101% | 99% | 101% | C, H
District Heating Output, MWh/MWh Total input | 0.003555 | 0.003555 | 0.003555 | 0.003555 | 0.003555 | 99% | 101% | 99% | 101% | C, H
Forced outage (%) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | I
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2 | [5 empty] | 7
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M € /MW) | 0.76499 | 0.75609 | 0.63754 | 0.5984 | 0.57819 | 90% | 110% | 90% | 110% | E, J, L | 10, 12
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M € /MW/year) | 0.035581 | 0.035581 | 0.035419 | 0.035325 | 0.035581 | 90% | 110% | 90% | 110% | F, K, L | 7
Variable O&M (€ /MWh) | 8.4812 | 8.4812 | 8.4812 | 8.4812 | 8.4812 | 90% | 110% | 90% | 110% | F, K, L | 7
Startup (M € /MW) | 0 | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) | 44.1 | 44.1 | 44.1 | 44.1 | 44.1
Specific density (kg/l) or (ton/m3) | 0.77 | 0.77 | 0.77 | 0.77 | 0.77
Specific investment (M € /1,000 t HVO) | 1.1169 | 1.1039 | 0.93506 | 0.88 | 0.84416 | 90% | 110% | 90% | 110% | E, J, L | 10, 12
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M € /1,000 t HVO) | 0.051948 | 0.051948 | 0.051948 | 0.051948 | 0.051948 | 90% | 110% | 90% | 110% | F, K, L | 7
Variable O&M (M € /1,000 t HVO) | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 90% | 110% | 90% | 110% | F, K, L | 7
Startup (M € /1,000 t HVO) | 0 | 0 | 0 | 0 | 0
Notes:
A. The plant size is assumed based on the plants sizes of existing HVO plants.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size uncertainty represents the current range in the market.
C. Performance is typical based on public data and confidential data reviewed by (S&T)2 Consultants Inc.
D. Hydrogen consumption is also a function of the feedstock to a small degree.
E. The total capital cost include total installed cost (total direct costs) and all indirect costs such as engineering, construction, contractor’s fee, contingency and working capital.
F. O&M costs, costs for main raw materials are not included.
G. There is limited potential for process improvements.
H. Total output excludes the heat loss.
I. Best plants operate at greater than 95% of capacity.
J. Range of capital cost is +/- 25% of mean.
K. Operating cost uncertainty is +/- 10% of mean.
L. M €/k tonne is million euro per 1,000 tonnes
References
[1] Neste. 2013. North American Tallow Pathway Description. https://www.arb.ca.gov/fuels/lcfs/2a2b/apps/nes-na-tallow-rpt-011414.pdf
[2] US EPA. 2017. EPA Approval for REG Geismar. https://www.epa.gov/sites/production/files/2017-05/documents/reg-geismar-deter-ltr-2017-04-13.pdf
[3] Kalnes, T et al. 2012. Green diesel production by hydrorefining renewable feedstocks. https://www.uop.com/wp-content/uploads/2012/12/UOP-Hydrorefining-Green-Diesel-Tech-Paper.pdf
[4] de Jong, S., Hoefnagels, R., Faaij, A., Slade, R., Mawhood, R. and Junginger, M. 2015. The feasibility of short-term production strategies for renewable jet fuels – a comprehensive techno-economic comparison. Biofuels, Bioprod. Bioref., 9: 778–800. https://www.doi.org/10.1002/bbb.1613
[5] Neste Financial Statements. https://www.neste.com/en/corporate-info/investors/financials
[6] US Energy Information Administration. New York Harbour ULSD Price. https://www.eia.gov/dnav/pet/pet_pri_spt_s1_d.htm
[7] Iowa State University. 2017. Biodiesel Profitability. http://www.extension.iastate.edu/agdm/energy/xls/d1-15biodieselprofitability.xlsx
[8] Rogelio Sotelo-Boyás, Fernando Trejo-Zárraga and Felipe de Jesús Hernández-Loyo (2012). Hydroconversion of Triglycerides into Green Liquid Fuels, Hydrogenation, Prof. Iyad Karamé (Ed.), InTech, DOI: 10.5772/48710. Available from: https://www.intechopen.com/books/hydrogenation/hydroconversion-of-triglycerides-into-green-liquid-fuels
[9] Tao, L., Milbrandt, A., Zhang, Y. and Wang, W. 2017. Techno-economic and resource analysis of hydroprocessed renewable jet fuel. Biotechnology for Biofuels 2017 10:261. https://doi.org/10.1186/s13068-017-0945-3
[10] Miller, P., Kumar, A. 2014. Techno-economic assessment of hydrogenation-derived renewable diesel production from canola and camelina, In Sustainable Energy Technologies and Assessments, Volume 6, 2014, Pages 105-115, ISSN 2213-1388, https://doi.org/10.1016/j.seta.2014.01.008
[11] Diamond Green Diesel. Press release. 2016. https://www.prnewswire.com/news-releases/diamond-green-diesel-to-be-expanded-to-275-million-gallons-annually-300248085.html
[12] Neste Renewable Diesel Handbook. https://www.neste.com/sites/default/files/attachments/neste_renewable_diesel_handbook.pdf
[13] Sub Group on Advanced Biofuels. 2017. Cost of Biofuel. http://platformduurzamebiobrandstoffen.nl/wp-content/uploads/2017/07/2017_SGAB_Cost-of-Biofuels.pdf

## 92 HVO jet fuel
Technology | HVO Jet Fuel
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t HVO/year | 400 | 400 | 600 | 700 | 800 | 50% | 200% | 50% | 100% | A, B
Typical total plant size MW HVO | 580 | 580 | 875 | 1020 | 1165 | 50% | 200% | 50% | 100% | A, A1, B
Inputs
Feedstock Consumption, MWh/MWh Total Inputs | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 90% | 110% | 90% | 110% | C, G | 2,3
Hydrogen Consumption, MWh/MWh Total Inputs | 0.099 | 0.099 | 0.099 | 0.099 | 0.099 | 90% | 110% | 90% | 110% | C,D, G | 2,3
Electricity Consumption, MWh/MWh Total Inputs | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 90% | 110% | 90% | 110% | C, G | 2,3
Natural Gas Consumption, MWh/MWh Total Inputs | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 90% | 110% | 90% | 110% | C, G | 2,3
Outputs
HVO Jet Output, GJ/GJ Total Input | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 90% | 110% | 90% | 110% | C, H
Naphta Output, MWh/MWh Total Input | 0.0651 | 0.0651 | 0.0651 | 0.0651 | 0.0651 | 90% | 110% | 90% | 110% | C, H
LPG Output, MWh/MWh Total Input | 0.0924 | 0.0924 | 0.0924 | 0.0924 | 0.0924 | 90% | 110% | 90% | 110% | C, H
Fuel Gas Output, MWh/MWh Total Input | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 90% | 110% | 90% | 110% | C, H
District Heating Output, MWh/MWh Total input | 0.02655 | 0.02655 | 0.02655 | 0.02655 | 0.02655 | 90% | 110% | 90% | 110% | C, H
Forced outage (%) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | I
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M € /MW HVO Jet) | 0.95835 | 0.95835 | 0.81039 | 0.7549 | 0.71345 | 50% | 150% | 50% | 150% | A, E, J, L
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M € /MW/year) | 0.035826 | 0.035826 | 0.035622 | 0.035651 | 0.035672 | 90% | 110% | 90% | 110% | F, K, L
Variable O&M (€ /MWh) | 8.5005 | 8.5005 | 8.5005 | 8.5005 | 8.5005 | 90% | 110% | 90% | 110% | F, K, L
Start-up (M € /1,000 t HVO Jet) | 0 | 0 | 0 |  | 0
Technology specific data
Specific energy content (GJ/ton) | 44 | 44 | 44 | 44 | 44
Specific density (kg/l) or (ton/m3) | 0.77 | 0.77 | 0.77 | 0.77 | 0.77
Specific investment (M € /1000 t HVO Jet) | 1.3896 | 1.3896 | 1.1818 | 1.1 | 1.039 | 50% | 150% | 50% | 150% | A, E, J, L
-equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M € /1,000 t HVO) | 0.051948 | 0.051948 | 0.051948 | 0.051948 | 0.051948 | 90% | 110% | 90% | 110% | F, K, L
Variable O&M (M € /1,000 t HVO) | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 90% | 110% | 90% | 110% | F, K, L
Startup (M € /1,000 t HVO) | 0 | 0 | 0 | 0 | 0
Notes:
A. The plant size is assumed based on the plants sizes of existing HVO plants. Jet production is 80% of HVO diesel production with the other 20% representing increased co-products.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size uncertainty represents the current range in the market.
C. Performance is typical based similar performance to HVO diesel but with less primary product and more co-products.
D. Hydrogen consumption is also a function of the feedstock to a small degree.
E. The total capital cost include total installed cost (total direct costs) and all indirect costs such as engineering, construction, contractor’s fee, contingency and working capital.
F. O&M costs, costs for main raw materials are not included.
G. There is limited potential for process improvements.
H. Total output excludes the heat loss.
I. Best plants operate at greater than 95% of capacity.
J. Range of capital cost is +/- 25% of mean.
K. Operating cost uncertainty is +/- 10% of mean.
L. M €/k tonne is million euro per 1,000 tonnes.
References
[1] AltAir. 2017. The Department of Energy: Wet and Gaseous Feedstocks: Barriers and Opportunities. https://energy.gov/sites/prod/files/2017/07/f35/BETO_2017WTE-Workshop_BryanSherbacow-AltAir.pdf
[2] Antonissen, K. 2016. Greenhouse gas performance of renewable jet fuel: a comparison of conversion pathways. https://dspace.library.uu.nl/bitstream/handle/1874/347665/MSc%20Thesis%20K.Y%20Antonissen%2c%20May%202016%20%281%29.pdf?sequence=2&isAllowed=y
[3] de Jong, S., Antonissen, K., Hoefnagels, R., Lonza, L., Wang, M., Faaij, A., and Junginger, M. 2017. Life-cycle analysis of greenhouse gas emissions from renewable jet fuel production. Biotechnology for Biofuels201710:64. https://doi.org/10.1186/s13068-017-0739-7
[4] Tao, L., Milbrandt, A., Zhang, Y., and Wang, W. 2017. Techno‑economic and resource analysis of hydroprocessed renewable jet fuel. Biotechnology for Biofuels. 10:261. https://doi.org/10.1186/s13068-017-0945-3
[5] Starck, L., Pidol, L., Jeuland, N., Chapus, T., Bogers, P., Bauldreay, J. 2016. Production of Hydroprocessed Esters and Fatty Acids (HEFA) - Optimization of Process Yield. Oil Gas Sci. Technol. - Rev. IFP Energies nouvelles. Volume 71, Number 1, January-February 2016. https://doi.org/10.2516/ogst/2014007
[6] Stratton et al. 2010. Life Cycle Greenhouse Gas Emissions from Alternative Jet Fuels. http://web.mit.edu/aeroastro/partner/reports/proj28/partner-proj28-2010-001.pdf
[7] de Jong, S., Hoefnagels, R., Faaij, A., Slade, R., Mawhood, R. and Junginger, M. 2015. The feasibility of short-term production strategies for renewable jet fuels – a comprehensive techno-economic comparison. Biofuels, Bioprod. Bioref., 9: 778–800. https://www.doi.org/10.1002/bbb.1613

## 93 1st generation ethanol
Technology | 1st Generation Ethanol
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Ethanol/year, 1,000 tonnes/year | 320 | 320 | 400 | 450 | 500 | 50% | 120% | 60% | 100% | A, B | 11
Ethanol/year, MW | 280 | 280 | 350 | 400 | 440 | 50% | 120% | 60% | 100% | A, B
Inputs
Feedstock Consumption, MWh/MWh Total Input | 0.83 | 0.83 | 0.84 | 0.85 | 0.85 | 98% | 105% | 98% | 102% | C
Electricity Consumption, MWh/MWh Total Input | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 75% | 125% | 75% | 125% | D
Natural Gas Consumption, MWh/MWh Total Input | 0.15 | 0.15 | 0.14 | 0.13 | 0.13 | 75% | 125% | 75% | 125% | D
Outputs
Ethanol Output, MWh/MWh Total Inputs | 0.46 | 46 | 0.47 | 0.47 | 0.47 | 0.95 | 1.02 | 0.95 | 1.02 | E, F
DDG Output, MWh/MWh Total Input | 0.29 | 0.27 | 0.28 | 0.25 | 0.25 | 98% | 105% | 98% | 102% | E, F
Forced outage (%) | 0 | 0 | 0 | 0 | 0
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ /MW Ethanol) | 0.73779 | 0.72333 | 0.69439 | 0.66375 | 0.66168 | 95% | 125% | 95% | 125% | I, J | 10
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW/year) | 0.060759 | 0.060759 | 0.060759 | 0.060759 | 0.060759 | 95% | 125% | 95% | 125% | J | 8
Variable O&M (€ /MWh) | 8.3007 | 8.3007 | 8.3007 | 8.3007 | 8.3007 | 90% | 110% | 90% | 110% | G, B, J | 8
Start-up (M€ /1,000 t Ethanol) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | H
Technology specific data
Specific energy content (GJ/ton) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
Specific density (kg/l) or (ton/m3) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
Specific investment (M€ /1,000 t Ethanol) | 0.64557 | 0.63291 | 0.60759 | 0.59 | 0.58228 | 95% | 125% | 95% | 125% | I, J | 10
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t Ethanol) | 0.060759 | 0.060759 | 0.060759 | 0.060759 | 0.060759 | 0.95 | 125% | 95% | 125% | J | 8
Variable O&M (M€ /1,000 t Ethanol) | 0.062025 | 0.062025 | 0.062025 | 0.062025 | 0.062025 | 90% | 110% | 90% | 110% | G, B, J | 8
Start-up (M€ /1,000 t Ethanol) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | H
Notes:
A. The plant size is assumed based on the plants sizes of existing ethanol plants.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size uncertainty represents the current range in the market.
C. The feedstock starch content impacts the yield. Ethanol yields in the United States have been slowly increasing from a combination of improved conversion efficiency and higher starch content of the feedstock.
D. The upper and lower values are representative of the range between individual plants.
E. Output excludes the low quality waste heat.
F. Change over time is a function of increased ethanol yield, which also results in lower DDG yield as the mass must be conserved.
G. Variable costs are reduced from improved energy efficiency.
H. Start-up costs are included on variable costs.
I. Capital costs can be site specific and process technology supplier dependent. The costs provided for in the table are from a technology developer with a reputation for low capital costs.
J. M €/k tonne is million euro per 1,000 tonnes
References
[1] (S&T)2 Consultants Inc. Database of actual plant performance.
[2] Energy Statistics 2015. https://ens.dk/sites/ens.dk/files/Statistik/energy_statistics_2015.pdf
[3] ePure. 2017. Fuel Blends. http://epure.org/about-ethanol/fuel-market/fuel-blends/
[4] Biograce Version 4d without the extra 30% processing energy factor.
[5] Hettinga, W., Junginger, H., Dekker S., Hoogwijk, M., McAloon, A., Hicks, K. 2009. Understanding the reductions in US corn ethanol production costs: An experience curve approach. Energy Policy 37(2009)190–203. http://naldc.nal.usda.gov/download/22550/PDF
[6] IEA Bioenergy Task 39. 2009. Potential for Improving Carbon/Energy Balance of Bioethanol. http://task39.sites.olt.ubc.ca/files/2013/05/IEA_Bioenergy_Task-39_Improving_carbon_and_energy_balance.pdf
[7] US Energy Information Administration. 2015. International Energy Statistics. Biofuels Production. http://www.eia.gov/cfapps/ipdbproject/IEDIndex3.cfm?tid=79&pid=79&aid=1
[8] ePure. 2014. State of the Industry Report 2014. http://epure.org/media/1137/state-of-the-industry-report-2014.pdf
[9] ePure. 2017. 2016 Industry Statistics. http://epure.org/media/1610/2016-industry-statistics.pdf
[10] Iowa State University. 2017. Ethanol Profitability. http://www.extension.iastate.edu/agdm/energy/xls/d1-10ethanolprofitability.xlsx
[11] Capital Journal. Oct. 10, 2017. Ringneck Energy pouring cement, building foundations for ethanol plant near Onida. http://www.capjournal.com/news/ringneck-energy-pouring-cement-building-foundations-for-ethanol-plant-near/article_4ee23aac-adec-11e7-80fb-a7814e744ba7.html
[12] Biofuel Journal. 2017. Third Quarter. Construction begins. Page 40-42.
[13] Ringneck Energy prospectus. 2016. http://ringneckenergy.com/wp-content/uploads/2016/12/2015_PPM_w_Exhibits.pdf

## 94 Pyrolysis oils
Technology | Fast Pyrolysis Bio Oil
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t Bio Oil/year | 20 | 80 | 200 | 500 | 1000 | 50% | 125% | 75% | 125% | A, B | 1, 6
Typical total plant size. MW | 10 | 40 | 105 | 265 | 520 | 50% | 125% | 75% | 125% | A, A1, B | 1, 6
Inputs
Feedstock Consumption, MWh/MWh Total Input | 1 | 1 | 1 | 1 | 1 | 90% | 150% | 90% | 125% | E | 4
Outputs
Bio Oil Output, MWh/MWh Total Input | 0.6 | 0.6 | 0.62 | 0.64 | 0.65 | 90% | 110% | 90% | 110% | E | 4
Steam, Output, MWh/MWh Total Input | 0.232 | 0.232 | 0.232 | 0.232 | 0.232 | 90% | 110% | 90% | 110% | E | 4
Power, Output, MWh/MWh Total Input | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.9 | 1.1 | 0.9 | 1.1 | E | 4
Forced outage (%) | n.a. | 4 | 0 | 0 | 0
Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 4 |  |  |  |  | C | 8
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ /MW Bio Oil) | 2.4 | 1.92 | 1.1429 | 0.84906 | 0.69231 | 0.75 | 1.25 | 0.75 | 1.25 | D, G | 6, 8
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW/year Bio Oil) | 0.072 | 0.072 | 0.068571 | 0.067925 | 0.069231 | 0.75 | 1.25 | 0.75 | 1.25 | F, G | 6
Variable O&M (€ /MWh Bio Oil) | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 75% | 125% | 75% | 125% | F, G | 6
Start up (M€ /1,000 t Bio Oil) | n.a. | 0 | 0 |  | 0
Technology specific data
Specific energy content (GJ/ton) bio-oil) | 16 | 16 | 16 | 16 | 16
Specific density (kg/l) or (ton/m3) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Specific investment (M€ /1,000 t Bio Oil) | 1.2 | 0.96 | 0.6 | 0.45 | 0.36 | 0.75 | 1.25 | 0.75 | 1.25 | D, G | 6, 8
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t Bio Oil) | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.75 | 1.25 | 0.75 | 1.25 | F, G | 6
Variable O&M (M€ /1,000 t Bio Oil) | 0.012 | 0.012 | 0.012 | 0.012 | 0.012 | 0.75 | 125% | 75% | 125% | F, G | 6
Start up (M€ /1,000 t Bio Oil) | n.a. | 0 | 0 | 0 | 0
Notes:
A. The plant size range is likely limited by the feedstock availability.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size range is typical of the range found in the literature. It is highly uncertain given that the commercial demonstration plants in operation are much smaller.
C. This is twice the time normally found in process operations.
D. Capital costs for nth plant are used for 2050 and earlier costs are estimates.
E. These are based on the commercial demonstration plant results.
F. Nth plant estimates.
G. M €/k tonne is million euro per 1,000 tonnes
References
[1] Muggen, G. 2015. Looking back at the first half year of commercial scale pyrolysis oil production at Empyro. tcbiomass Chicago November 4th 2015. http://www.gastechnology.org/tcbiomass/tcb2015/Muggen_Gerhard-Presentation-tcbiomass2015.pdf
[2] BTG Bioliquids. Empyro project. https://www.btg-btl.com/en/company/projects/empyro
[3] Mahajan. M. 2018. Biomass-A Massive opportunity in disguise. https://ec.europa.eu/energy/sites/ener/files/documents/32_dharmesh_mahajan-honeywell.pdf
[4] Bridgwater, A., Meier, D. Radlein, D. 1999. An overview of fast pyrolysis of biomass. Organic Geochemistry, Volume 30, Issue 12, Pages 1479-1493, https://doi.org/10.1016/S0146-6380(99)00120-5.
[5] BTG. November 2017 Newsletter. https://www.btg-btl.com/nieuwsbrieven/2017/november/en
[6] Mark M. Wright, Justinus A. Satrio, and Robert C. Brown 2010. Techno-Economic Analysis of Biomass Fast Pyrolysis to Transportation Fuels https://www.nrel.gov/docs/fy11osti/46586.pdf
[7] Hu, W., Dang, Q., Rover, M., Brown, R., Wright, M. 2015. Comparative techno-economic analysis of advanced biofuels, biochemicals, and hydrocarbon chemicals via the fast pyrolysis platform. Biofuels, 7:1, 57-67. http://dx.doi.org/10.1080/17597269.2015.1118780
[8] Shemfe, M.,Sai Gu, S., Ranganathan, P. 2015. Techno-economic performance analysis of biofuel production and miniature electric power generation from biomass fast pyrolysis and bio-oil upgrading, Fuel, Volume 143, 2015, Pages 361-372, https://doi.org/10.1016/j.fuel.2014.11.078.
[9] BE-Sustainable. 2014. Empyro BV breaks ground of its biomass to liquid pyrolysis plant. http://www.besustainablemagazine.com/cms2/empyro-bv-breaks-ground-of-its-biomass-to-liquid-pyrolysis-plant/
[10] Ensyn. 2016. Scale-up & Optimization BETO Workshop. https://www.energy.gov/sites/prod/files/2016/10/f33/Graham_0.pdf
[11] BTG. Pyrolysis oil properties. https://www.btg-btl.com/en/applications/oilproperties
[12] Environment Canada. 1999. Bunker C Fuel Oil. www.etc-cte.ec.gc.ca/databases/oilproperties/pdf/web_bunker_c_fuel_oil.pdf

## 95 Cellulosic ethanol
Technology | Cellulosic Ethanol
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 tonnes/year | 60 | 60 | 150 | 175 | 200 | 50% | 150% | 50% | 150% | A, B | 9
Typical total plant size, MW | 55 | 55 | 130 | 155 | 180 | 50% | 150% | 50% | 150% | A, A1, B | 9
Inputs
Feedstock Consumption, MWh/MWh Total Input | 1 | 1 | 1 | 1 | 1 | 90% | 150% | 90% | 150% | C | 1
Outputs
Ethanol Output, MWh/MWh Total Input | 0.29 | 0.29 | 0.37 | 0.39 | 0.4 | 80% | 120% | 80% | 120% | C | 1
Electiricity Output, MWh/MWh Total Input | 0.04 | 0.04 | 0.05 | 0.05 | 0.06 | 80% | 120% | 80% | 120% | C | 1
Forced outage (%) | 4 | 4 | 2 | 0 | 0
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ /MW Ethanol) | 5.6919 | 5.6919 | 2.5614 | 2.2483 | 2.1345 | 75% | 150% | 75% | 150% | D, G | 1, 10, 11
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW/year Ethanol) | 0.11384 | 0.11384 | 0.056919 | 0.057332 | 0.056919 | 95% | 200% | 95% | 200% | F, G | 1
Variable O&M (€ /MW Ethanol) | 27.1044 | 27.1044 | 13.5522 | 13.3828 | 13.5522 | 95% | 200% | 95% | 200% | F, G | 1
Start-up (M€ /1,000 t Ethanol) | 0 | 0 | 0 |  | 0 |  |  |  |  | E
Technology specific data
Specific energy content (GJ/ton) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
Specific density (kg/l) or (ton/m3) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
Specific investment (M€ /1,000 t Ethanol) | 5.0633 | 5.0633 | 2.2785 | 2 | 1.8987 | 75% | 150% | 75% | 150% | D, G | 1, 10, 11
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t Ethanol) | 0.10127 | 0.10127 | 0.050633 | 0.051 | 0.050633 | 95% | 200% | 95% | 200% | F, G | 1
Variable O&M (M€ /1,000 t Ethanol) | 0.20253 | 0.20253 | 0.10127 | 0.1 | 0.10127 | 95% | 200% | 95% | 200% | F, G | 1
Start-up (M€ /1,000 t Ethanol) | 0 | 0 | 0 | 0 | 0 |  |  |  |  | E
Notes:
A. The plant size is assumed based on the plants sizes of existing ethanol plants.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size uncertainty represents the current range in the market.
C. Not all process developers are attempting to maximize ethanol output; this can result in higher feedstock consumption but lower chemical use. Co-product production is higher if the ethanol yield is low.
D. There is a wide range of reported capital costs for the existing plants and a wide range in the cost of future plants.
E. Start-up costs are included in the operating costs.
F. O&M costs are based on the nth plant. There are no public estimates for the costs from current plants. It has been estimated that they are twice the values for the nth plants. This may be optimistic unless the on line performance can be improved.
G. M €/k tonne is million euro per 1,000 tonnes
References
[1] Tao, L., Schell, D., Davis, R., Tan, E., Elander, R. and Bratis, A. 2014. NREL 2012 Achievement of Ethanol Cost Targets: Biochemical Ethanol Fermentation via Dilute-Acid Pretreatment and Enzymatic Hydrolysis of Corn Stover. NREL/TP-5100-61563. https://www.nrel.gov/docs/fy14osti/61563.pdf
[2] Kacelle. 2014. Bringing cellulosic ethanol to industrial production at Kalundborg, Denmark. https://biorefiningalliance.com/wp-content/uploads/2014/12/KACELLE-PUBLISHABLE-SUMMARY-web.pdf
[3] POET-DSM achieves cellulosic biofuel breakthrough. Nov 2017. http://poetdsm.com/pr/poet-dsm-achieves-cellulosic-biofuel-breakthrough
[4] Thakrar, A. 2017. PROJECT LIBERTY: Lessons learned in commercializing cellulosic biofuels. Presented at 6TH International Conference on Lignocellulosic Ethanol. Brussels, Sept 2017. https://ec.europa.eu/energy/en/events/6th-international-conference-ethanol-lignocellulosics.
[5] Van der Meij, R. 2017. A venture capitalist’s view on investment in lingo-cellulosic ethanol. Presented at 6TH International Conference on Lignocellulosic Ethanol. Brussels, Sept 2017. https://ec.europa.eu/energy/en/events/6th-international-conference-ethanol-lignocellulosics.
[6] Merritt, M. 2017. Real Progress in Cellulosic Biofuel. Biofuels, Bioprod. Bioref., 11: 943-944. https://doi.org/10.1002/bbb.1837
[7] Beta Renewables. Oct 2017. The Alessandria court admitted the Gruppo Mossi Ghisolfi companies to the “concordato preventivo”. http://www.betarenewables.com/en/media-relations/news-detail/32
[8] DuPont to sell cellulosic ethanol plant in blow to biofuel. Nov 2017. https://www.reuters.com/article/us-dowdupont-ethanol/dupont-to-sell-cellulosic-ethanol-plant-in-blow-to-biofuel-idUSKBN1D22T5
[9] Clariant. 2017. Clariant And Enviral Announce First License Agreement on Sunliquid® Cellulosic Ethanol Technology. https://www.clariant.com/en/Corporate/News/2017/09/Clariant-and-Enviral-announce-first-license-agreement-on-sunliquid-cellulosic-ethanol-technology
[10] Clariant. 2017. Clariant to Build Flagship Sunliquid® Cellulosic Ethanol Plant in Romania. https://www.clariant.com/en/Corporate/News/2017/10/Clariant-to-build-flagship-sunliquid-cellulosic-ethanol-plant-in-Romania
[11] IEA Bioenergy Task 39. Cellulosic Ethanol Plants. http://demoplants.bioenergy2020.eu/
[12] Brian Foody. 2016. Scaling Up Cellulosic Biofuels, Ideas & Experience. Presented at Scaling Up, Ottawa, Ontario, Nov 15, 2016.
[13] Lee R Lynd, Xiaoyu Liang, Mary J Biddy, Andrew Allee, Hao Cai, Thomas Foust, Michael E Himmel, Mark S Laser, Michael Wang, Charles E Wyman. 2017. Cellulosic ethanol: status and innovation, In Current Opinion in Biotechnology, Volume 45, 2017, Pages 202-211, ISSN 0958-1669, https://doi.org/10.1016/j.copbio.2017.03.008
[14] de Jong, S., Hoefnagels, R., Faaij, A., Slade, R., Mawhood, R. and Junginger, M. 2015. The feasibility of short-term production strategies for renewable jet fuels – a comprehensive techno-economic comparison. Biofuels, Bioprod. Bioref., 9: 778–800. https://www.doi.org/10.1002/bbb.1613
[15] Irena. 2016. Innovation Outlook. Advanced Liquid Biofuels. http://www.irena.org/DocumentDownloads/Publications/IRENA_Innovation_Outlook_Advanced_Liquid_Biofuels_2016.pdf
[16] Sub Group on Advanced Biofuels. 2017. Cost of Biofuel. http://platformduurzamebiobrandstoffen.nl/wp-content/uploads/2017/07/2017_SGAB_Cost-of-Biofuels.pdf

## 97 Methanol from biomass gasif.
Technology | Bio Methanol
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t Methanol/year | 100 | 100 | 200 | 250 | 300 | 50% | 200% | 50% | 125% | A, B | 3, 5, 6
Typical total plant size, MW | 65 | 65 | 130 | 165 | 195 | 50% | 200% | 50% | 125% | A, A1, B | 3, 5, 6
Inputs
Feedstock Consumption, MWh/MWh Total Input | 1 | 1 | 1 | 1 | 1 | 90% | 150% | 90% | 120% |  | 1
Outputs
Methanol Output, MWh/MWh Total Input | 0.58 | 0.58 | 0.61 | 0.63 | 0.65 | 100% | 133% | 100% | 133% | D | 1
District heat Output, MWh/MWh Total Input | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 80% | 125% | 80% | 125% | D | 1
Electricity Output, MWh/MWh Total Input | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 80% | 125% | 80% | 125% | D | 1
Forced outage (%) | 4 | 4 | 0 | 0 | 0
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 20 | 20 | 20 | 20
Construction time (years) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Financial data
Specific investment (M€ /MW Methanol) | 5.258 | 5.258 | 2.9211 | 2.1212 | 1.4606 | 50% | 100% | 80% | 120% | F | 1, 3, 5, 6
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW/year Methanol) | 0.058423 | 0.058423 | 0.038948 | 0.038358 | 0.038948 | 90% | 110% | 90% | 110% | E, F | 1
Variable O&M (€ /MWh methanol) | 20.4043 | 20.4043 | 13.6029 | 13.6029 | 13.6029 | 90% | 110% | 90% | 110% | E,,F | 1
Start up (M€ /1,000 t Methanoll) | 0 | 0 | 0 |  | 0
Technology specific data
Specific energy content (GJ/ton) methanol) | 20.1 | 20.1 | 20.1 | 20.1 | 20.1
Specific density (kg/l) or (ton/m3) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
Specific investment (M€ /1,000 t Methanol) | 3.4177 | 3.4177 | 1.8987 | 1.4 | 0.94937 | 50% | 100% | 80% | 120% | F | 1, 3, 5, 6
Fixed O&M (M€ /1,000 t Methanol) | 0.037975 | 0.037975 | 0.025316 | 0.025316 | 0.025316 | 90% | 110% | 90% | 110% | E, F | 1
Variable O&M (M€ /1,000 t Methanol) | 0.11392 | 0.11392 | 0.075949 | 0.075949 | 0.075949 | 90% | 110% | 90% | 110% | E,,F | 1
Start up (M€ /1,000 t Methanoll) | 0 | 0 | 0 | 0 | 0
Notes:
A. The plant size range is assumed based on the proposed Värmlands plant and the NREL nth plant.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. Feedstock availability is likely to determine the maximum plant size.
C. Some plants may produce their own power and have no power imports.
D. Plants that produce their own power will have much lower heat available to district heat.
E. Assumed a 25/75 split on fixed to variable operating costs.
F. M €/k tonne is million euro per 1,000 tonnes
References
[1] Andersson, J.,Lundgren, J., and Marklund, M. 2014. Methanol production via pressurized entrained flow biomass gasification – Techno-economic comparison of integrated vs. stand-alone production, In Biomass and Bioenergy, Volume 64, 2014, Pages 256-268, ISSN 0961-9534, https://doi.org/10.1016/j.biombioe.2014.03.063
[2] Danish Technology Institute. 2011. GreenSynFuels. EUDP project journal number: 64010-0011. http://serenergy.com/wp-content/uploads/2015/11/GreenSynFuels_report_final.pdf
[3] Clausen, L. 2014. Integrated torrefaction vs. external torrefaction – A thermodynamic analysis for the case of a thermochemical biorefinery. Energy, Volume 77, Pages 597-607. https://doi.org/10.1016/j.energy.2014.09.042.
[4] IEA Bioenergy Task 39. 2016. IEA-Bioenergy-Task-39-Newsletter-Issue-42-April-2016. http://task39.sites.olt.ubc.ca/files/2012/01/IEA-Bioenergy-Task-39-Newsletter-Issue-42-April-2016.pdf
[5] Värmlands Metanol AB. http://www.varmlandsmetanol.se/Om%20Projektet.htm
[6] Värmlands Metanol AB. 2016. Metanol från skog - ett miljövänligt drivmedel. http://www.varmlandsmetanol.se/dokument/Folder%20VM%20sept%202016.pdf
[7] NREL. 2011. Technoeconomic comparison of biofuels: ethanol, methanol, and gasoline from gasification of woody residues. https://www.nrel.gov/docs/fy12osti/52636.pdf
[8] Sub Group on Advanced Biofuels. 2017. Cost of Biofuel. http://platformduurzamebiobrandstoffen.nl/wp-content/uploads/2017/07/2017_SGAB_Cost-of-Biofuels.pdf

## 98 Methanol from power
Technology | Power to Methanol
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t Methanol/year | 5 | 50 | 100 | 125 | 150 | 50% | 150% | 50% | 150% | A, B | 4, 5, 11
Typical total plant size, MW | 3 | 33 | 65 | 83 | 100 | 50% | 150% | 50% | 150% | A, A1, B | 4, 5
Inputs
CO2 Consumption, t/t Methanol | 1.37 | 1.37 | 1.37 | 1.37 | 1.37 | 100% | 110% | 100% | 110% |  | 5
Hydrogen Consumption, t/t Methanol | 0.192 | 0.192 | 0.192 | 0.192 | 0.192 | 100% | 110% | 100% | 110% |  | 5
Electricity Consumption, MWh/MWh Total Inputs | 1 | 1 | 1 | 1 | 1 | 90% | 120% | 95% | 110% | C | 2,3
Outputs
Methanol Output, MWh/MWh Input | 0.58 | 0.58 | 0.61 | 0.63 | 0.65 | 100% | 133% | 100% | 133% | D | 2,3
District Heating Output, MWh/MWh Total input | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0% | 100% | 0% | 100% | E | 2,3
Forced outage (%) | 4 | 4 | 0 | 0 | 0
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 20 | 20 | 20 | 20
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ /MW Methanol) | 4.5134 | 4.5134 | 3.009 | 2.2567 | 1.5045 | 50% | 100% | 80% | 120% | F | 1, 3, 5, 6
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW Methanol/year) | 0.052657 | 0.052657 | 0.052657 | 0.052657 | 0.052657 | 90% | 110% | 90% | 110% | E, F | 1
Variable O&M (€ /MWh) | 6.2687 | 6.2687 | 6.2687 | 6.2687 | 6.2687 | 90% | 110% | 90% | 110% | E, F | 1
Start up (M€ /1,000 t Methanol) | 0 | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) methanol) | 20.1 | 20.1 | 20.1 | 20.1 | 20.1
Specific density (kg/l) or (ton/m3) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
Specific investment (M€ /1,000 t Methanol) | 3 | 3 | 2 | 1.5 | 1 | 50% | 100% | 80% | 120% | F | 1, 3, 5, 6
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t Methanol) | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 90% | 110% | 90% | 110% | E, F | 1
Variable O&M (M€ /1,000 t Methanol) | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 90% | 110% | 90% | 110% | E, F | 1
Start up (M€ /1,000 t Methanol) | 0 | 0 | 0 |  | 0
Notes:
A. The plant size range is based on the CRI plants and other analysis in the literature.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. CO2 availability is likely to determine the maximum plant size.
C. Power use improvement depends on improved efficiency for electrolyzers.
D. Methanol is the only output.
E. Waste heat is of low quality.
F. The methanol synthesis step does not lend itself to intermittent operation. The concept of intermittent power to methanol is not practical without intermediate storage for hydrogen that would allow the methanol plant to operate continuously. This would have a significant capital cost impact.
G. There is a wide range of capital costs in the literature.
H. M €/k tonne is million euro per 1,000 tonnes
References
[1] Next generation of methanol fuel cell vehicles sees the light of day. 2017. http://serenergy.com/next-generation-of-methanol-fuel-cell-vehicles-sees-the-light-of-day/
[2] Stefansson, B. 2015. Power and CO2 emissions to methanol. https://eu-ems.com/event_images/presentations/Benedikt%20Stefansson%20presentation.pdf
[3] Stefansson, B. 2017. CO2 to Renewable Methanol: experiences and perspectives for the steel industry. https://www.co2-cato.org/cato-download/4123/20170512_143353_20-11.00-Stefansson-public.pdf
[4] MefCO2 Project Brochure. 2017. http://www.mefco2.eu/pdf/MefCO2_Brochure_00.pdf
[5] Atsonios K, et al., Investigation of technical and economic aspects for methanol production through CO2 hydrogenation, International Journal of Hydrogen Energy (2016), http://dx.doi.org/10.1016/j.ijhydene.2015.12.074
[6] Methanol Institute. http://www.methanol.org/the-methanol-industry/
[7] Hovsapian, R. 2017. Role of Electrolyzers in Grid Services. US DOE. https://energy.gov/sites/prod/files/2017/06/f34/fcto_may_2017_h2_scale_wkshp_hovsapian.pdf
[8] Manuel Götz, Jonathan Lefebvre, Friedemann Mörs, Amy McDaniel Koch, Frank Graf, Siegfried Bajohr, Rainer Reimert, Thomas Kolb, Renewable Power-to-Gas: A technological and economic review, In Renewable Energy, Volume 85, 2016, Pages 1371-1390, ISSN 0960-1481, https://doi.org/10.1016/j.renene.2015.07.066
[9] Danish Technology Institute. 2011. GreenSynFuels. EUDP project journal number: 64010-0011. http://serenergy.com/wp-content/uploads/2015/11/GreenSynFuels_report_final.pdf
[10] Haldor Topsøe. 2017. Gasoline synthesis (TIGAS). https://www.topsoe.com/processes/gasoline-synthesis/gasoline-synthesis-tigas
[11] M. Pérez-Fortes and E. Tzimas; Techno-economic and environmental evaluation of carbon dioxide utilisation for fuel production. Synthesis of methanol and formic acid; EUR 27629 EN; https://dx.doi.org/10.2790/981669
[12] enea Consulting. 2016. The Potential of Power to Gas. Technology review and economic potential assessment. http://www.enea-consulting.com/wp-content/uploads/2016/01/ENEA-Consulting-The-potential-of-power-to-gas.pdf
[13] CRI. 2017. Commercial Scale Plants. http://carbonrecycling.is/comercial-scale/

## 99 SNG from methan. of biogas
Technology | SNG from Biogas
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 GJ SNG/year | 70 | 100 | 250 | 500 | 700 | 75% | 125% | 75% | 125% | A, B | 1, 7
Typical total plant size, MW | 2.3148 | 3.3069 | 8.2672 | 16.5344 | 23.1481 | 75% | 125% | 75% | 125% | A, A1, B | 1, 7
Inputs
Biogas Consumption, MWh/MWh Total Input | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 80% | 120% | 80% | 120% | C, I | 2
Hydrogen Consumption, MWh/MWh Total Input | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 80% | 120% | 80% | 120% | C, E | 2
Electricity Consumption, MWh/MWh Total Input | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 50% | 150% | 50% | 150% | D | 2
Outputs
SNG Output, MWh/MWh Total Input | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 90% | 110% | 95% | 105% | G | 2
District Heating Output, MWh/MWh Total input | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 50% | 150% | 50% | 150% | G | 2
Forced outage (%) | 4 | 4 | 0 | 0 | 0 |  |  |  |  | F
Planned outage (weeks per year) | 2 | 2 | 2 | 2 | 2
Technical lifetime (years) | 25 | 25 | 25 | 25 | 25
Construction time (years) | 1 | 1 | 1 | 1 | 1
Financial data
Specific investment (M€ /MW SNG) | 1.0886 | 0.9072 | 0.756 | 0.6048 | 0.4536 | 50% | 150% | 50% | 150% | H | 1
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW/year SNG) | 0.043546 | 0.036288 | 0.03024 | 0.024192 | 0.018144 | 90% | 110% | 90% | 110% |  | 1
Variable O&M (€ /MWh SNG) | 5.184 | 4.32 | 3.6 | 2.88 | 2.16 | 90% | 110% | 90% | 110% |  | 1
Start up (€ /GJ SNG) | 0 | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) SNG) | 50.7 | 50.7 | 50.7 | 50.7 | 50.7
Specific investment (M€ / 1000 GJ SNG) | 0.036 | 0.03 | 0.025 | 0.02 | 0.015 | 50% | 150% | 50% | 150% | H | 1
- equipment (%) | 75 | 75 | 75 | 75 | 75
-installation (%) | 25 | 25 | 25 | 25 | 25
Fixed O&M (€ /GJ SNG) | 0.144 | 0.12 | 0.1 | 0.08 | 0.06 | 90% | 110% | 90% | 110% |  | 1
Variable O&M (€ /GJ SNG) | 0.144 | 0.12 | 0.1 | 0.08 | 0.06 | 90% | 110% | 90% | 110% |  | 1
Start up (€ /GJ SNG) | 0 | 0 | 0 | 0 | 0
Notes:
A. The plant size range is likely limited by the biogas availability.
B. A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
C. Plant size progression is based on moving from small biogas system to large systems as the technology is proven.
D. There are variations in the process that will have some impact on the overall efficiency. It is not yet clear what might become the industry standard.
E. This is the power for the system excluding the electrolyzer.
F. The methanation step does not lend itself to intermittent operation. The concept of intermittent power to SNG is not practical without intermediate storage for hydrogen that would allow the methanation plant to operate continuously. This would have a significant capital cost impact.
G. Some recoverable waste heat is available from the process.
H. There is a significant range in the capital cost estimates.
I. Assumes that the biogas is 65% methane.
References
[1] Manuel Götz, Jonathan Lefebvre, Friedemann Mörs, Amy McDaniel Koch, Frank Graf, Siegfried Bajohr, Rainer Reimert, Thomas Kolb, Renewable Power-to-Gas: A technological and economic review, In Renewable Energy, Volume 85, 2016, Pages 1371-1390, ISSN 0960-1481, https://doi.org/10.1016/j.renene.2015.07.066
[2] Swiss Federal Office of Energy SFOE. 2017. Direct Methanation of Biogas. https://www.aramis.admin.ch/Default.aspx?DocumentID=45656&Load=true
[3] gwf gas + energy. 2014. Das e-gas-Projekt am Biogasanlagen-standort in Werlte. https://www.di-verlag.de/media/content/gwf-GE/gwf_Gas_5_14/gwf-GE_05_2014_FB_Kurt.pdf?xaf26a=7841c984ef837209544e
[4] Rauch, R., Hrbek, J. and Hofbauer, H. 2014. Biomass gasification for synthesis gas production and applications of the syngas. WIREs Energy Environ, 3: 343–362. https://doi.org/10.1002/wene.97
[5] Combination of Power-to-Gas with Biogas Plant. Vienna University of Technology. https://www.tuwien.ac.at/fileadmin/t/tuwien/fotos/pa/download/2015/HM2015/Flyer_Power_to_Bio--Gas_EN.pdf
[6] Hitachi Zosen Corporation and Hitachi Zosen Inova to Build First Joint Power-To-Gas Plant. Dec 2017. http://www.hz-inova.com/cms/en/home?p=6276
[7] Hansen, J., Holstebroe, M., Jensen, M., Rass-Hansen, J., Heiredal-Clausen, T. 2016. SOEC Enabled Biogas Upgrading. 12th European SOFC & SOE Forum.
[8] Udvikling og effektivisering af biogasproduktionen I Danmark – Delrapport 1 og 2, Danish Energy Agency Biogas Taskforce 2015.

## 100 Hydrothermal liquifaction
Technology | Bio Oil
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t Bio Oil/year | n.a. | 120 | 180 | 250 | 300 | 50% | 125% | 75% | 125% | A, B | 1, 6
Typical total plant size. MW | n.a. | 145 | 220 | 300 | 360 | 50% | 125% | 75% | 125% | A, A1, B | 1, 6
Inputs
Feedstock Consumption, MWh/MWh Total Input | n.a. | 0.95 | 0.95 | 0.95 | 0.95 | 90% | 150% | 90% | 125% | E | 4
Electricity Consumption, MWh/MWh Total Input | n.a. | 0.05 | 0.05 | 0.05 | 0.05 | 75% | 125% | 75% | 125% | E | 4
Outputs
Bio Oil Output, MWh/MWh Total Input | n.a. | 0.82 | 0.82 | 0.82 | 0.82 | 90% | 110% | 90% | 110% | E | 4
Co-products Output MWh/MWh Total Input | n.a. | 0 | 0 | 0 | 0 | 90% | 110% | 90% | 110% | E | 4
Forced outage (%) | n.a. | 4 | 0 | 0 | 0
Planned outage (weeks per year) | 4 | 4 | 4 | 4 | 4 |  |  |  |  | C | 8
Technical lifetime (years) | 20+ | 20+ | 20+ | 20+ | 20+
Construction time (years) | 2 | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ / MW Bio Oil) | n.a. | 2.1973 | 1.648 | 1.236 | 1.0986 | 75% | 125% | 75% | 125% | D, G | 6, 8
- equipment (%) | n.a. | 75 | 75 | 75 | 75
-installation (%) | n.a. | 25 | 25 | 25 | 25
Fixed O&M (M€ / MW Bio Oil/year) | n.a. | 0.062779 | 0.062779 | 0.062779 | 0.062779 | 75% | 125% | 75% | 125% | F, G | 6
Variable O&M (€ /MWh) | n.a. | 14.0132 | 14.0132 | 14.0132 | 14.0132 | 75% | 125% | 75% | 125% | F, G | 6
Start up (€ /MW Bio Oil) | n.a. | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) HTL) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
Specific density (kg/l) or (ton/m3) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Specific investment (M€ /1000 t Bio Oil) | n.a. | 2.6667 | 2 | 1.5 | 1.3333 | 75% | 125% | 75% | 125% | D, G | 6, 8
- equipment (%) | n.a. | 75 | 75 | 75 | 75
-installation (%) | n.a. | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t Bio Oil) | n.a. | 0.07619 | 0.07619 | 0.07619 | 0.07619 | 75% | 125% | 75% | 125% | F, G | 6
Variable O&M (M€ /1,000 t Bio Oil) | n.a. | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 75% | 125% | 75% | 125% | F, G | 6
Start up (M€ /1,000 t Bio Oil) | n.a. | 0 | 0 |  | 0
Notes:
A. The plant size range is likely limited by the feedstock availability.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size range is typical of the range found in the literature. It is highly uncertain given that there is no commercial demonstration plant in operation yet.
C. This is twice the time normally found in process operations.
D. Capital costs for nth plant are used for 2050 and earlier costs are estimates.
E. These are based on extrapolated pilot plant results.
F. Nth plant estimates
G. M €/k tonne is million euro per 1,000 tonnes
References
[1] Steeper Energy Announces Eur 50.6 M (Dkk 377 M) Advanced Biofuel Project With Norwegian-Swedish Joint Venture Silva Green Fuel In Licensing Deal. 2017. http://steeperenergy.com/2017/12/15/steeper-energy-announces-eur-50-6-m-dkk-377-m-advanced-biofuel-project-with-norwegian-swedish-joint-venture-silva-green-fuel-in-licensing-deal/
[2] Jensen, C.U., Rodriguez Guerrero, J.K., Karatzos, S. et al. 2017. Fundamentals of Hydrofaction™: Renewable crude oil from woody biomass. Biomass Conv. Bioref. (2017) 7: 495. https://doi.org/10.1007/s13399-017-0248-8
[3] Environment Canada. 1999. Bunker C Fuel Oil. www.etc-cte.ec.gc.ca/databases/oilproperties/pdf/web_bunker_c_fuel_oil.pdf
[4] Fracking Biomass. Biofuels Digest. Feb 2, 2017. http://www.biofuelsdigest.com/bdigest/2017/02/02/fracking-biomass-steeper-energy-and-the-pursuit-of-renewable-hydrocarbons/
[5] Jensen, C.U., Rodriguez Guerrero, J.K., Karatzos, S. et al. Biomass Conv. Bioref. (2017) 7: 495. https://doi.org/10.1007/s13399-017-0248-8
[6] Toms, P. 2017. Hydrofaction™ Oil: A Solution for Decarbonizing Long-haul Transport. https://www.bio.org/sites/default/files/0830AM-Perry%20Toms.pdf
[7] Zhu, Y., Biddy, M., Jones, S., Elliott, D., Schmidt, A. 2014. Techno-economic analysis of liquid fuel production from woody biomass via hydrothermal liquefaction (HTL) and upgrading, In Applied Energy, Volume 129, 2014, Pages 384-394, ISSN 0306-2619, https://doi.org/10.1016/j.apenergy.2014.03.053
[8] Licella. 2016. Licella Canfor Joint Venture at the forefront of global bioenergy. http://www.licella.com.au/news/licella-canfor-joint-venture-at-the-forefront-of-global-bioenergy/
[9] C.U. Jensen, J.K.R. Guerrero, S. Karatzos, G. Olofsson and S.B. Iversen, 10 - Hydrofaction™ of forestry residues to drop-in renewable transportation fuels, In Direct Thermochemical Liquefaction for Energy Applications, edited by Lasse Rosendahl,, Woodhead Publishing, 2018, Pages 319-345, ISBN 9780081010297, https://doi.org/10.1016/B978-0-08-101029-7.00009-6.
[10] Harris Group. 2013. Production of Advanced Biofuels via Liquefaction Hydrothermal Liquefaction Reactor Design. NREL/SR-5100-60642. http://www.ourenergypolicy.org/wp-content/uploads/2015/08/60462.pdf
[11] Magdeldin, M., Kohl, T., Järvinen, M. 2018. Techno-economic Assessment of Integrated Hydrothermal Liquefaction and Combined Heat and Power Production from Lignocellulose Residues, J. sustain. dev. energy water environ. syst., 6(1), pp 89-113, 2018. https://doi.org/10.13044/j.sdewes.d5.0177
[12] Pedersen, T. H., Hansen, N. H., Pérez, O. M., Cabezas, D. E. and Rosendahl, L. A. 2018. Renewable hydrocarbon fuels from hydrothermal liquefaction: A techno‐economic analysis. Biofuels, Bioprod. Bioref., 12: 213-223. doi:10.1002/bbb.1831

## 101 Catalytic Hydropyrolysis 2
Technology | Catalytic Hydropyrolysis conf. 2
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t Bio Oil/year | n.a. | 40 | 80 | 120 | 160 | 50% | 125% | 75% | 125% | A, B | 3, 4
Typical total plant size. MW | n.a. | 56.8788 | 113.7575 | 170.6363 | 227.515 | 50% | 125% | 75% | 125% | A, A1, B | 3, 4
Inputs
Feedstock Consumption, MWh/MWh Total Input | n.a. | 0.99 | 0.99 | 0.99 | 0.99 | 90% | 150% | 90% | 125% | D | 5
Electricity Consumption, MWh/MWh Total Input | n.a. | 0.01 | 0.01 | 0.01 | 0.01 | 75% | 125% | 75% | 125% | D | 5
Outputs
Gasoline fraction, MWh/MWh Total Input | n.a. | 0.38 | 0.39 | 0.4 | 0.41 | 90% | 110% | 90% | 110% | D | 5
Diesel fraction, MWh/MWh Total Input | n.a. | 0.17 | 0.18 | 0.18 | 0.19 | 90% | 110% | 90% | 110% | D | 5
Co-products Output MWh/MWh Total Input | n.a. | 0 | 0 | 0 | 0 | 90% | 110% | 90% | 110% | D | 5
Forced outage (%) | n.a. | 4 | 4 | 0 | 0
Planned outage (weeks per year) | n.a. | 2 | 3 | 4 | 5 | [5 empty] | 5
Technical lifetime (years) | n.a. | 20+ | 20+ | 20+ | 20+
Construction time (years) | n.a. | 2 | 2 | 2 | 2 | [5 empty] | 5
Financial data
Specific investment (M€ /MW Bio Oil) | n.a. | 2.7823 | 1.5766 | 1.1546 | 0.92742 | 75% | 125% | 75% | 125% | C, F | 5, 11
- equipment (%) | n.a. | 75 | 75 | 75 | 75
-installation (%) | n.a. | 25 | 25 | 25 | 25
Fixed O&M (M€ /MW/year Bio Oil) | n.a. | 0.027427 | 0.027427 | 0.027427 | 0.027427 | 75% | 125% | 75% | 125% | E, F | 5
Variable O&M (€ /MWh Bio Oil) | n.a. | 1.306 | 1.306 | 1.306 | 1.306 | 75% | 125% | 75% | 125% | E, F | 5
Start up (€ /l Bio Oil) | n.a. | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) | 43 | 43 | 43 | 43 | 43
Specific density (kg/l) or (ton/m3) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
Specific investment (M€ /l1000 t Bio Oil) | n.a. | 3.9563 | 2.2419 | 1.6418 | 1.3188 | 75% | 125% | 75% | 125% | C, F | 5, 11
- equipment (%) | n.a. | 75 | 75 | 75 | 75
-installation (%) | n.a. | 25 | 25 | 25 | 25
Fixed O&M (M€ /1,000 t Bio Oil) | n.a. | 0.039 | 0.039 | 0.039 | 0.039 | 75% | 125% | 75% | 125% | E, F | 5
Variable O&M (€ /1,000 t Bio Oil) | n.a. | 0.0156 | 0.0156 | 0.0156 | 0.0156 | 75% | 125% | 75% | 125% | E, F | 5
Start up (€ /l Bio Oil) | n.a. | 0 | 0 | 0 | 0
Notes:
A. The plant size range is likely limited by the feedstock availability.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size range is typical of the range found in the literature. It is highly uncertain given that there is no commercial demonstration plant in operation yet.
C. Capital costs for nth plant are used for 2050 and earlier costs are estimates.
D. These are based on extrapolated pilot plant results.
E. Nth plant estimates
F. M €/k tonne is million euro per 1,000 tonnes

## 101 Catalytic Hydropyrolysis 1
Technology | Catalytic Hydroprocessing conf. 1
| 2015 | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower |  | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t liquid fuels/year | n.a. | 40 | 80 | 120 | 160 | 50% |  | 125% | 75% | 125% | A, B | 3, 4
Typical total plant size. MW | n.a. | 57 | 114 | 171 | 228 | 50% |  | 125% | 75% | 125% | A, A1, B | 3, 4
Inputs
Feedstock Consumption, MWh/MWh Total Input | n.a. | 0.77 | 0.77 | 0.77 | 0.77 | 90% |  | 150% | 90% | 125% | C | 1
Hydrogen Consumption, MWh/MWh Total Input | n.a. | 0.23 | 0.23 | 0.23 | 0.23 | 75% |  | 125% | 75% | 125% | C | 1
Outputs
Liquid Fuel Output, MWh/MWh Total Input | n.a. | 0.38 | 0.38 | 0.38 | 0.38 | 90% | 110% |  | 90% | 110% | C | 1
Biochar, Output, MWh/MWh Total Input | n.a. | 0.13 | 0.13 | 0.13 | 0.13 | 90% | 110% |  | 90% | 110% | C | 1
Gas Output, MWh/MWh Total Input | n.a. | 0.31 | 0.31 | 0.31 | 0.31 | 90% | 110% |  | 90% | 110% | C | 1
District Heat MWh/MWh Total Input | n.a. | 0.18 | 0.18 | 0.18 | 0.18 | 90% | 110% |  | 90% | 110% | C | 1
Financial data
Specific investment (M€ /l1000 t Liquid Fuels) | n.a. | 2.18 | 1.23 | 0.9 | 0.73 | 75% |  | 125% | 75% | 125% | D, E, F | 5, 11
- equipment (%) | n.a. | 75 | 75 | 75 | 75
-installation (%) | n.a. | 25 | 25 | 25 | 25
Fixed O&M (1,000 € /MW) | n.a. | 44 | 44 | 44 | 44 | 0.75 |  | 1.25 | 0.75 | 1.25 | E, F | 5
Variable O&M (€ /MWh of fuel) | n.a. | 0.02 | 0.02 | 0.02 | 0.02 | 0.75 |  | 1.25 | 0.75 | 1.25 | E, F | 5
Start up (€ /l Liquid Fuel) | n.a. | 0 | 0 | 0 | 0
Technology specific data
Specific energy content (GJ/ton) |  | 43
Specific density (kg/l) or (ton/m3) |  | 0.83
Notes:
A. The plant size range is likely limited by the feedstock availability.
A1. This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B. The plant size range is typical of the range found in the literature. It is highly uncertain given that there is no commercial demonstration plant in operation yet.
C. These are based on extrapolated pilot plant results.
D. Tan [5] reports that the hydrogen plant and distillation account for 45% of the total plant costs for configuration 2. The cost for this configuration are therefore 55% of Configuration 2.
E. Nth plant estimates
M €/k tonne is million euro per 1,000 tonnes

## 102 Hydrogen to Jet
Technology | Hydrogen to Jet Fuel
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 kt FT Liquids/year | 2 | 13 | 41 | 165 | 50% | 150% | 50% | 150% | A, B, | 18, 20, 23
Typical total plant size, MW Output | 3.1 | 20.5 | 64.5 | 259.6 | 50% | 150% | 50% | 150% | A,B,C | 18, 20
Inputs
CO2 Consumption, t/t FT Liquids | 4.3 | 3.9 | 3.6 | 3.3 | 100% | 110% | 100% | 110% | C, D, E
Hydrogen Consumption, MWh/MWh Total Inputs | 0.995 | 0.995 | 0.995 | 0.995 | 75% | 125% | 75% | 125% | E
Power Consumption, MWh/MWh Total Inputs | 0.005 | 0.005 | 0.005 | 0.005 | 75% | 125% | 75% | 125% | E
Outputs
FT Liquids Output, MWh/MWh Total Input | 0.65 | 0.7 | 0.73 | 0.75 | 80% | 120% | 80% | 120% | F, G, O | 20, 18
District Heat Output, MWh/MWh Total Input | 0.25 | 0.2 | 0.17 | 0.15 | 80% | 120% | 80% | 120% | H
Forced outage (%) | 0 | 0 | 0 | 0 |  |  |  |  | I
Planned outage (weeks per year) | 3 | [8 empty] | 18
Technical lifetime (years) | 25
Construction time (years) | 2
Financial data
Specific investment (M€ /MW Liquids/year) | 2.1 | 1.6 | 1.1 | 0.9 | 75% | 150% | 75% | 125% | G, J | 18, 20, 26, 30
- equipment (%) | 75 | 75 | 75 | 75 |  |  |  |  | K
-installation (%) | 25 | 25 | 25 | 25
Fixed O&M (€ /MWH Liquids) | 16.9 | 12.7 | 8.5 | 7.4 | 90% | 110% | 90% | 110% | L | 18
Variable O&M (€ /MWH Liquids) | 5.3 | 4.2 | 3.2 | 2.1 | 90% | 110% | 90% | 110% | M | 26
Start up (€ /l FT Liquids) | 0 | 0 | 0 | 0
Technology specific data
Specific investment (€ /l FT Liquids/year) | 3.3 | 2.5 | 1.7 | 1.4 | 75% | 150% | 75% | 125% | G, J | 18, 20, 26, 30
- equipment (%) | 75 | 75 | 75 | 75 |  |  |  |  | K
-installation (%) | 25 | 25 | 25 | 25
Fixed O&M (€ /l FT Liquids) | 0.16 | 0.12 | 0.08 | 0.07 | 90% | 110% | 90% | 110% | L | 18
Variable O&M (€ /l FT Liquids) | 0.05 | 0.04 | 0.03 | 0.02 | 90% | 110% | 90% | 110% | M | 26
Start up (€ /l FT Liquids) | 0 | 0 | 0 | 0
Notes
A. The plant size range is based on the Schmidt and Mortensen reports and other analysis in the literature. Scale up is our assumption.
B. CO2 availability is likely to determine the maximum plant size.
C. Conversion to MW is based on 8,000 operating hours per year and the energy output in all liquid fuels. The conversion is rounded. Some reports are based on only 4,000 hours of operation. Figure 1-2 utilizes the 2050 estimates.
D. Carbon efficiency in the literature ranges from 75 to 95%. Assuming that the early plants have low carbon efficiency and increase over time.
E. Denominator of FT liquids is the total liquid fuel output.
F. Hydrogen and power are the only energy input. Power will be required for pumping, compression, and utilities in addition to hydrogen production. Power estimated based on typical electric demand in petroleum refineries.
G. FT Liquids efficiency increases as hydrogen production efficiency increases with adoption of more efficient technologies. 2020 and 2030 assume alkaline electrolysis, 2040 is based on PEM systems, and 2050 assumes SOEC. Limited improvement in FT synthesis assumed, although jet fuel selectivity may improve over time.
H. Own calculations.
I. Some heat is lost in the process to drive the RWGS reaction. Assumes that total losses and internal consumption is 10% of the input. The quality of the district heat will depend on the electrolysis technology employed. The FT portion of the process will have excess steam available. The quantity and quality of the steam will depend on the FT process employed and the plant configuration.
J. This will depend on the level of hydrogen storage and the frequency of low surplus electricity periods that are outside of the range used for the calculation of the required hydrogen storage.
K. The capital costs drop as plant size increases and through technological learning. Hydrogen storage costs are included (10% of capital costs) but not sized in the reference. No CO2 storage is assumed.
L. Own Assumption
M. Based on 5% of capital cost.
N. Based on 1.5% of capital cost. Excludes cost of power and carbon dioxide.
O. A reasonable distribution of the FT fuels might be 60% jet fuel, 20% gasoline, and 20% lighter products (LPG and fuel gas), but the distribution of outputs could be very different depending on the plant design, catalyst and the operating conditions.

## 102 Power to Jet
Technology | Power to Jet Fuel
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size 1,000 t FT Liquids/year | 2 | 13 | 41 | 165 | 50% | 150% | 50% | 150% | A, B, C | 18, 20, 23
Typical total plant size, MW Output | 3.1 | 20.5 | 64.5 | 259.6 | 50% | 150% | 50% | 150% | A,B,C | 18, 20
Inputs
CO2 Consumption, t/t FT Liquids | 4.3 | 3.9 | 3.6 | 3.3 | 100% | 110% | 100% | 110% | D, E
Electricity Consumption, MWh/MWh Total Inputs | 1 | 1 | 1 | 1 | 100% | 100% | 100% | 100% | F
Outputs
FT Liquids Output, MWh/MWh Total Input | 0.37 | 0.4 | 0.5 | 0.55 | 80% | 120% | 80% | 120% | G, H, O | 20, 18
District Heat Output, MWh/MWh Total Input | 0.43 | 0.4 | 0.3 | 0.25 | 80% | 120% | 80% | 120% | I
Forced outage (%) | 0 | 0 | 0 | 0 |  |  |  |  | J
Planned outage (weeks per year) | 3 | [8 empty] | 18
Technical lifetime (years) | 25 |  |  |  | 20 | 30
Construction time (years) | 2
Financial data
Specific investment (M€ /MW Output) | 3.2 | 2.5 | 1.9 | 1.6 | 75% | 150% | 75% | 125% | K | 18, 20, 26, 30
- equipment (%) | 75 | 75 | 75 | 75 |  |  |  |  | L
-installation (%) | 25 | 25 | 25 | 25
Fixed O&M (€ /MWh FT Liquids) | 26.5 | 15.9 | 10.6 | 5.3 | 90% | 110% | 90% | 110% | M | 18
Variable O&M (€ /MWH FT Liquids) | 8.5 | 5.3 | 3.2 | 2.1 | 90% | 110% | 90% | 110% | N | 26
Start up (€ /MWh FT Liquids) | 0 | 0 | 0 | 0
Technology specific data
Specific investment (€ /l FT Liquids/year) | 5 | 4 | 3 | 2.5 | 75% | 150% | 75% | 125% | K | 18, 20, 26, 30
- equipment (%) | 75 | 75 | 75 | 75 |  |  |  |  | L
-installation (%) | 25 | 25 | 25 | 25
Fixed O&M (€ /l FT Liquids) | 0.25 | 0.15 | 0.1 | 0.05 | 90% | 110% | 90% | 110% | M | 18
Variable O&M (€ /l FT Liquids) | 0.08 | 0.05 | 0.03 | 0.02 | 90% | 110% | 90% | 110% | N | 26
Start up (€ /l FT Liquids) | 0 | 0 | 0 | 0
Notes:
A. The plant size range is based on the Schmidt and Mortensen reports and other analysis in the literature. Scale up is our assumption.
B. CO2 availability is likely to determine the maximum plant size.
C. Conversion to MW is based on 8,000 operating hours per year and the energy output in all liquid fuels. The conversion is rounded. Some reports are based on only 4,000 hours of operation. Figure 1-2 utilizes the 2050 estimates.
D. Carbon efficiency in the literature ranges from 75 to 95%. Assuming that the early plants have low carbon efficiency and increase over time.
E. Denominator of FT liquids is the total liquid fuel output.
F. Power is the only energy input. Power will be required for pumping, compression, and utilities in addition to hydrogen production.
G. FT Liquids efficiency increases as hydrogen production efficiency increases with adoption of more efficient technologies. 2020 and 2030 assume alkaline electrolysis, 2040 is based on PEM systems, and 2050 assumes SOEC. Limited improvement in FT synthesis assumed, although jet fuel selectivity may improve over time.
H. Own calculations.
I. Some heat is lost in the process to drive the RWGS reaction. Assumes that total losses and internal consumption is 20% of the input. The quality of the district heat will depend on the electrolysis technology employed. The FT portion of the process will have excess steam available. The quantity and quality of the steam will depend on the FT process employed and the plant configuration.
J. This will depend on the level of hydrogen storage and the frequency of low surplus electricity periods that are outside of the range used for the calculation of the required hydrogen storage.
K. The capital costs drop as plant size increases and through technological learning. Hydrogen storage costs are included (10% of capital costs) but not sized in the reference. No CO2 storage is assumed.
L. Own Assumption
M. Based on 5% of capital cost.
N. Based on 1.5% of capital cost. Excludes cost of power and carbon dioxide.
O. A reasonable distribution of the FT fuels might be 60% jet fuel, 20% gasoline, and 20% lighter products (LPG and fuel gas), but the distribution of outputs could be very different depending on the plant design, catalyst and the operating conditions.

## 103 Hydrogen to Ammonia
Technology | Green Ammonia plant: Hydrogen to ammonia (excl. electrolyzer and excl. ASU)
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size, TPD | 229 | 458 | 916 | 2290 | 100% | 100% | 100% | 100% | A
Typical total plant size, MW (Ammonia output) | 50 | 100 | 200 | 500 | 100% | 100% | 100% | 100%
Inputs
N2 Consumption, t/t Ammonia | 0.839 | 0.839 | 0.839 | 0.839 | 98% | 102% | 98% | 102% | B | [1]
Hydrogen Consumption, t/t Ammonia | 0.18 | 0.18 | 0.18 | 0.18 | 98% | 102% | 98% | 102% | B | [1]
Hydrogen Consumption, MWh/MWh Total Inputs | 0.947 | 0.947 | 0.947 | 0.947 | 98% | 102% | 98% | 102% | B | [1]
Electricity Consumption, MWh/MWh Total Inputs | 0.053 | 0.053 | 0.053 | 0.053 | 95% | 110% | 75% | 150% | C | [1]
Outputs
Ammonia Output, MWh/MWh total Input | 0.823 | 0.823 | 0.823 | 0.823 | 98% | 102% | 98% | 102% |  | [1]
High value heat MWh/MWh total input | 0.108 | 0.108 | 0.108 | 0.108 | 98% | 102% | 98% | 102% | D | [1]
District Heating Output, MWh/MWh Total input | 0.038 | 0.038 | 0.038 | 0.038 | 0% | 100% | 0% | 100% | E | [1]
Forced outage (%), unplanned shutdown | 5% | 3% | 3% | 2% | 2% | 8% | 2% | 4% |  | [3]
Planned outage (weeks per year) | 3% | 3% | 3% | 3% | [5 empty] | [3]
Operation capacity | 20-100% | 20-100% | 20-100% | 20-100% | [5 empty] | [2]
Technical lifetime (years) | 30 | 30 | 30 | 30
Construction time (years) | 2 | 2 | 2 | 2
Financial data
Specific investment (M€ /MW Ammonia output) | 1.5863 | 1.2974 | 1.0612 | 0.81355 | 1.24 | 2.09 | 0.57 | 0.95 | F, I, J | [3]
- equipment (%) | 50 | 50 | 50 | 50 | [5 empty] | [3]
-installation (%) | 50 | 50 | 50 | 50 | [5 empty] | [3]
Fixed O&M (k€/MW Ammonia/year) | 47.5887 | 38.9229 | 31.8351 | 24.4064 | 37.2 | 62.7 | 17.1 | 28.5 | G | [3]
Variable O&M (€/MWh Ammonia) | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.04 | 0.01 | 0.04 | H | [3]
Start up (M€ /1,000 t Ammonia) | N.A. | N.A. | N.A. | N.A.
Technology specific data
Specific investment mark-up factor optional ASU | 1.09 | 1.09 | 1.09 | 1.09 | 97% | 100% | 97% | 100% | F | [3]
Specific energy content (GJ/ton Ammonia) | 18.9 | 18.9 | 18.9 | 18.9
Specific density (kg/l) or (ton/m3) Ammonia | 626 | 626 | 626 | 626
Specific investment (M€ /TPD Ammonia output) | 0.34635 | 0.28328 | 0.2317 | 0.17763 | 0.27074 | 0.45633 | 0.12445 | 0.20742 | F, I | [3]
Fixed O&M (M€ /TPD Ammonia) | 10.3905 | 8.4984 | 6.9509 | 5.3289 | 8.1223 | 13.69 | 3.7336 | 6.2227 |  | [3]
Variable O&M (€ /t Ammonia) | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | [3]
Start up (M€ /TPD Ammonia) | N.A. | N.A. | N.A. | N.A.
Notes:
A: Typical NH₃ plant size based on H2 supply from 100 MWe electrolyzer for 2020.
B: Assume 98% efficiency with respect to mass of the ammonia synthesis
C: Assumption of higher pressure electrolysis available in the future, requiring lower compression power. A green ammonia plant that contains a dedicated ASU for nitrogen production will have additional power requirements, cf. chapter 3.3
D: Steam at up to 350°C may be produced by NH₃ synthesis
E: Heat available at 30-60°C and requires heat pump for use for district heating.
F: Specific investment of green NH₃ plant (excl. electrolysis, excl. ASU, NH₃ storage and utilities) is estimated as 54% of conventional NH₃ plant based on NG. Cost is decreasing with time mainly because of scale effect (increasing plant size). To add the cost of an ASU a multiplication factor of 1.06-1.09 should be applied to the total Specific Investment (both entries in Financial Data and Technology-specific data) as a rule of thumb.
G: Fixed O&M is taken as 3% of CAPEX
H: Variable O&M estimated as cost for catalyst replacement and misc. consumables
I: Financial data is given in 2015-€ as in the other datasheets (and in contrast to Figure 9-2, which is showing the corresponding cost in 2019-€)
J: Cost projection is considering economy of scale only and does not consider further technical development, due to the maturity of ammonia synthesis. In case capacities are expected for other years than shown in the datasheet, one should use the corresponding cost data of the respective capacity instead of the cost data for a given year. See also Figure 16 in the chapter.
References
[1] Based on calculated mass and energy balance
[2] Based on normal operation ranges for instrumentations and rotating equipment. Lower capacity range is possible but it is normally expensive as spare insturmentation and rotating equipment is required
[3] Based on collected data, i.e. based on several sources, as specified in the qualitative section

## 104 Methane pyrolysis, MBR
| Technology | Moving-bed Methane Decomposition (MBR)
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input) | N/A | 77 | 85 | 93.5 | 38.5 | 115.5 | 47 | 140 | A, G, H, I
| Typical total plant size (MW H2 output) | N/A | 32 | 35 | 39 | 16 | 48 | 19.5 | 58.5 | A, F, G | [2]
| Typical total plant size (kg H2/day output) | N/A | 23000 | 25000 | 28000 | 12000 | 35000 | 14000 | 42000 | A, E, G, K | [2]
- Inputs
| Natural Gas (% total input(MWh/MWh)) | N/A | 78 | 80 | 82 | 76 | 80 | 78 | 84 | A, G, H | [2]
| Electricity (% total input(MWh/MWh)) | N/A | 22 | 20 | 18 | 20 | 24 | 16 | 22 | A, G | [2]
- Outputs
| Hydrogen Gas (% total input (MWh/MWh)) | N/A | 41 | 42 | 43 | 37 | 45 | 39 | 47 | A, F, G | [2]
| Carbon Black (% total input (MWh/MWh)) | N/A | 28 | 29 | 30 | 25 | 31 | 27 | 33 | A, G, N | [2]
| Methane (% total input (MWh/MWh)) | N/A | 9 | 8 | 7 | 4.5 | 13.5 | 3.5 | 10.5 | A, G, H, M | [2]
| Recovered Heat (% total input (MWh/MWh)) | N/A | 16 | 15 | 14 | 8 | 24 | 7 | 21 | A, G | [2]
| Heat loss (% total input (MWh/MWh)) | N/A | 6 | 6 | 6 | 5 | 9 | 3 | 9 | A, G | [2]
| Forced outage (%) | N/A | 20 | 10 | 1 | 10 | 30 | 0 | 2 | A
| Planned outage (weeks per year) | N/A | 10 | 4 | 2 | 10 | 22 | 0 | 0 | A, C, D, G
| Technical lifetime (years) | N/A | 20 | 25 | 25 | 15 | 25 | 20 | 30 | A, G | [6]
| Construction time (years) | N/A | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A, D,G
Financial data (2015)
| Specific investment (M€/MW of total H2 output) | N/A | 0.6 | 0.55 | 0.485 | 0.3 | 0.9 | 0.2 | 0.7 | A, B, F, G, J, K | [1], [3]
| - hereof equipment (%) | N/A | 50 | 50 | 50 | 45 | 55 | 45 | 55 | A, G
| - hereof installation (%) | N/A | 50 | 50 | 50 | 45 | 55 | 45 | 55 | A, G
| Fixed O&M (€ / MW of total H2 output) | N/A | 12000 | 11000 | 9700 | 6000 | 18000 | 4900 | 15000 | A, B, G | [1], [3]
| Variable O&M (€ / MWh of total H2 output) | N/A | 4 | 3.6 | 3.24 | 2 | 6 | 1.62 | 4.86 | A, G, L | [1], [3]
| Startup cost (€ / MW of total H2 output) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Technology specific data
| Methane conversion (%) | N/A | 89 | 90 | 91 | N/A | N/A | N/A | N/A | A, G, M
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | The technology is not available in 2020.
B | The cost estimate is highly dependent on the materialization of the pilot plants currently being built and their performance. If reaching a mature technology level by 2030, it is expected that some cost reduction will occur in the coming years, but the level of cost reduction is uncertain.
C | The planned outages might be higher than stated in the early stages of the technology development.
D | The estimate is based on previous engineering experience.
E | The value is an average of published bandwidth values.
F | The Lower Heating Value (LHV) of the hydrogen used is 120 MJ/kg.
G | The projected values for 2040 and 2050 are assumed based on a 10% change over time. This is due to potential improvements in the efficiency of the process, optimization of the operation of the technology, and reduction in the prices of material/equipment/inputs.
H | Total input of electricity and methane energy converted through methane LHV of 50.0 MJ/kg.
I | Plant size based on input is a combination of methane consumption and electricity input.
J | The investment cost includes the process units and associated equipment needed to start up the plant. It does not include peripheral equipment such as buildings (e.g. control rooms) or electrical interfaces.
K | The techno-economic analysis for both investment and sizing is based on theoretical conversion models coupled with actual energy and material costs at the time of the analysis.
L | The variable O&M is calculated to be similar to SMR technology excluding the cost of natural gas input and carbon tax. What is included is process cooling costs and general wear and tear.
M | Unconverted methane is recycled to prevent methane slip.
N | The Lower Heating Value (LHV) of the carbon black used is 28.0 MJ/kg.
References:
1 | Brett Parkinson, J. W. (2017). Techno‐Economic Analysis of Methane Pyrolysis in Molten Metals: Decarbonizing Natural Gas. Chemical Engineering Technology, 1022-1030.
2 | Gaudernack, B., & Lynum, S. (1998). Hydrogen from natural gas without release of CO2 to the atmosphere. Hydrogen Energy, 1087-1093.
3 | Tiina Keipi a, V. H. (2016). Techno-economic analysis of four concepts for thermal decomposition of methane: Reduction of CO2 emissions in natural gas combustion. Energy Conversion and Management, 1-12.
6 | N. Z. Muradov, Thermocatalytic CO2‐Free Production of Hydrogen from Hydrocarbon Fuels, Technical Report, No. DE‐FC36‐99GO10456, U.S. Department of Energy, Oak Ridge, TN 2004.

## 104 Methane pyrolysis, Plasma
| Technology | Plasma-assisted Methane Decomposition (Plasma)
|  | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Typical total plant size (MW input) | N/A | 273 | 300 | 330 | 136.5 | 409.5 | 165 | 495 | A, G, H, I | [2]
| Typical total plant size (MW H2 output) | N/A | 125 | 140 | 150 | 62.5 | 187.5 | 75 | 225 | A, F, G | [2]
| Typical total plant size (kg H2/day output) | N/A | 89000 | 98000 | 110000 | 45000 | 130000 | 55000 | 160000 | A, E, G, K | [2]
- Inputs
| Natural Gas (% total input(MWh/MWh)) | N/A | 84 | 86 | 88 | 82 | 86 | 86 | 90 | A, G, H | [2]
| Electricity (% total input(MWh/MWh)) | N/A | 16 | 14 | 12 | 14 | 18 | 10 | 14 | A, G | [2]
| - Outputs |  | 100 | 100 | 100
| Hydrogen Gas (% total input (MWh/MWh)) | N/A | 45 | 46 | 47 | 41 | 49 | 43 | 51 | A, F, G | [2]
| Carbon Black (% total input (MWh/MWh)) | N/A | 30 | 31 | 32 | 27 | 33 | 29 | 35 | A, G, N | [2]
| Methane (% total input (MWh/MWh)) | N/A | 9 | 8 | 7 | 4.5 | 13.5 | 3.5 | 10.5 | A, G, H, M
| Recovered Heat (% total input (MWh/MWh)) | N/A | 11 | 10 | 10 | 5.5 | 16.5 | 5 | 15 | A, G | [2]
| Heat loss (% total input (MWh/MWh)) | N/A | 5 | 5 | 4 | 4 | 10 | 2 | 8 | A, G | [2]
| Forced outage (%) | N/A | 20 | 10 | 1 | 10 | 30 | 0 | 2 | A
| Planned outage (weeks per year) | N/A | 16 | 4 | 2 | 10 | 22 | 2 | 4 | A, C, D, G
| Technical lifetime (years) | N/A | 20 | 25 | 25 | 15 | 25 | 20 | 30 | A, G | [6]
| Construction time (years) | N/A | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A, D,G
Financial data (2015)
| Specific investment (M€/MW of total H2 output) | N/A | 0.83333 | 0.76667 | 0.66667 | 0.4 | 1.3 | 0.3 | 1 | A, B, E, F, G, J, K | [1], [3]
| - hereof equipment (%) | N/A | 50 | 50 | 50 | 45 | 55 | 45 | 55 | A, G
| - hereof installation (%) | N/A | 50 | 50 | 50 | 45 | 55 | 45 | 55 | A, G
| Fixed O&M (€ / MW of total H2 output) | N/A | 25000 | 23000 | 20000 | 13000 | 38000 | 10000 | 31000 | A, B, G | [1], [3]
| Variable O&M (€ / MWh of total H2 output) | N/A | 4 | 3.6 | 3.24 | 2 | 6 | 1.62 | 4.86 | A, L, G | [1], [3]
| Startup cost (€ / MW of total H2 output) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Technology specific data
| Methane conversion (%) | N/A | 89 | 90 | 91 | N/A | N/A | N/A | N/A | A, G, M
| 66.8449 | - of which proces electricity | #REF! | #REF! | #REF! | #REF! |  |  |  |  | A, E | 8/13
Notes:
A | The technology is not available in 2020.
B | The cost estimate is highly dependent on the materialization of the pilot plants currently being built and their performance. If reaching a mature technology level by 2030, it is expected that some cost reduction will occur in the coming years, but the level of cost reduction is uncertain.
C | The planned outages might be higher than stated in the early stages of the technology development.
D | The estimate is based on previous engineering experience.
E | The value is an average of published bandwidth values.
F | The Lower Heating Value (LHV) of the hydrogen used is 120 MJ/kg.
G | The projected values for 2040 and 2050 are assumed based on a 10% change over time. This is due to potential improvements in the efficiency of the process, optimization of the operation of the technology, and reduction in the prices of material/equipment/inputs.
H | Total input of electricity and methane energy converted through methane LHV of 50.0 MJ/kg.
I | Plant size based on input is a combination of methane consumption and electricity input.
J | The investment cost includes the process units and associated equipment needed to start up the plant. It does not include peripheral equipment such as buildings (e.g. control rooms) or electrical interfaces.
K | The techno-economic analysis for both investment and sizing is based on theoretical conversion models coupled with actual energy and material costs at the time of the analysis.
L | The variable O&M is calculated to be similar to SMR technology excluding the cost of natural gas input and carbon tax. What is included is process cooling costs and general wear and tear.
M | Unconverted methane is recycled to prevent methane slip.
N | The Lower Heating Value (LHV) of the carbon black used is 28.0 MJ/kg.
References:
1 | Brett Parkinson, J. W. (2017). Techno‐Economic Analysis of Methane Pyrolysis in Molten Metals: Decarbonizing Natural Gas. Chemical Engineering Technology, 1022-1030.
2 | Gaudernack, B., & Lynum, S. (1998). Hydrogen from natural gas without release of CO2 to the atmosphere. Hydrogen Energy, 1087-1093.
3 | Tiina Keipi a, V. H. (2016). Techno-economic analysis of four concepts for thermal decomposition of methane: Reduction of CO2 emissions in natural gas combustion. Energy Conversion and Management, 1-12.
6 | N. Z. Muradov, Thermocatalytic CO2‐Free Production of Hydrogen from Hydrocarbon Fuels, Technical Report, No. DE‐FC36‐99GO10456, U.S. Department of Energy, Oak Ridge, TN 2004.