## Geothermal - large
Technology
| Technology | Geothermal power plant - large system (flash or dry)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 55 | 55 | 55 | 30 | 500 | 30 | 500 |  | 1
| Generating capacity for total power plant (MWe) | 110 | 110 | 110 | 30 | 500 | 30 | 500 |  | 1
| Electricity efficiency, net (%), name plate | 16 | 17 | 18 | 8 | 18 | 10 | 20 | A | 5
| Electricity efficiency, net (%), annual average | 15 | 16 | 17 | 8 | 18 | 10 | 20 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
| Ramping (% per minute) | 3 | 10 | 20 | [5 empty] | 8
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | C | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | C | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
| CH4 (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
Financial data
| Nominal investment (M$/MWe) | 4 | 3.44 | 2.84 | 2.7 | 5.75 | 1.7 | 4.55 | B,D,E,F | 1,2,3,4
| - of which equipment | 60% | 60% | 60% | 40% | 70% | 40% | 70% |  | 3
| - of which installation | 40% | 40% | 40% | 30% | 50% | 30% | 50% |  | 3
| Fixed O&M ($/MWe/year) | 50000 | 43000 | 35500 | 37500 | 62500 | 26600 | 44400 | B,D | 1,4
| Variable O&M ($/MWh) | 0.25 | 0.22 | 0.18 | 0.1875 | 0.3125 | 0.135 | 0.225 | B,D | 1,4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
| Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | IEA, World Energy Outlook, 2015.
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Geothermal Energy Association, 2015, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from Geothermal Facilities"
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These large units are assumed to be flach units at high source temperatures.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%, which is an estimate build upon cases from IRENA (ref. 3)
C | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
D | The learning rate is assumed to impact the geothermal specific equipment and installation. The power plant units (i.e. the turbine and pump) is assumed to have very litle development. From Ref. 3 it is assumed that half of the investment cost are on the geothermal specific equipment.
E | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Geothermal - small
Technology
| Technology | Geothermal power plant - small system (binary or condensing)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 10 | 10 | 10 | 0.3 | 20 | 0.3 | 20 |  | 1,8
| Generating capacity for total power plant (MWe) | 20 | 20 | 20 | 5 | 30 | 5 | 30 |  | 1
| Electricity efficiency, net (%), name plate | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Electricity efficiency, net (%), annual average | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
| Construction time (years) | 2 | 2 | 2 | 1,5 | 3 | 1,5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 30 | 31 | 32 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | B | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | B | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
| CH4 (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
Financial data
| Nominal investment (M$/MWe) | 5 | 4.3 | 3.55 | 3.75 | 6.25 | 1.7 | 4.55 | C,D,E,F | 1,2,4,8
| - of which equipment | 60% | 60% | 60% | 40% | 70% | 40% | 70% |  | 3
| - of which installation | 40% | 40% | 40% | 30% | 50% | 30% | 50% |  | 3
| Fixed O&M ($/MWe/year) | 65000 | 55900 | 46200 | 48800 | 81300 | 34700 | 57800 | C,D | 1,4
| Variable O&M ($/MWh) | 0.37 | 0.3182 | 0.2627 | 0.2775 | 0.4625 | 0.19703 | 0.32837 | C,D | 1,4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
| Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Budisulistyo & Krumdieck , 2014, "Thermodynamic and economic analysis for the pre- feasibility study of a binary geothermal power plant"
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Climate Policy Initiative, 2015, Using Private Finance to Accelerate Geothermal Deployment: Sarulla Geothermal Power Plant, Indonesia.
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These smaller units are assumed to be binary units at medium source temperatures.
B | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Large hydro power plant
Technology
| Technology | Hydro power plant - large system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 150 | 150 | 150 | 100 | 2000 | 100 | 2000 |  | 1,8,10
| Generating capacity for total power plant (MWe) | 150 | 150 | 150 | 100 | 2000 | 100 | 2000 |  | 1,8,10
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B | 1
| Construction time (years) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 62 | 62 | 62 | 46.5 | 77.5 | 46.5 | 77.5 | C | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 40 | 40 | 40 | 20 | 95 | 20 | 95 |  | 2,12
| Capacity factor (%), incl. outages | 35.8846 | 35.8846 | 35.8846 | 20 | 95 | 20 | 95 |  | 2,12
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.08 | 1.9968 | 1.8512 | 1.65 | 2.25 | 1.4 | 2.05 | D,E,F | 1,4,5,6,9
| - of which equipment | 30% | 30% | 30% | 20% | 50% | 20% | 50% |  | 11
| - of which installation | 70% | 70% | 70% | 50% | 80% | 50% | 80% |  | 11
| Fixed O&M ($/MWe/year) | 37700 | 36200 | 33600 | 28300 | 47100 | 25200 | 42000 | C | 1,4,5,6
| Variable O&M ($/MWh) | 0.65 | 0.624 | 0.5785 | 0.4875 | 0.8125 | 0.43388 | 0.72313 | C | 1,5
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IEA, World Energy Outlook, 2015.
5 | Learning curve approach for the development of financial parameters.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
9 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
10 | General Electric, www.gerenewableenergy.com, Accessed: 20th July 2017
11 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
12 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Medium-small hydro power plant
Technology
| Technology | Hydro power plant - Medium system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 2
| Generating capacity for total power plant (MWe) | 50 | 50 | 50 | 20 | 100 | 20 | 100 |  | 2
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | 10.5 | 17.5 | 10.5 | 17.5 | B
Additional data for non thermal plants
| Capacity factor (%), theoretical | 80 | 80 | 80 | 50 | 95 | 50 | 95 |  | 8,9
| Capacity factor (%), incl. outages | 75.8846 | 75.8846 | 75.8846 | 50 | 95 | 50 | 95 |  | 8,9
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.29 | 2.1984 | 2.0381 | 1.4 | 5.2 | 1.4 | 5.2 | C,D | 4,5,6,7
| - of which equipment | 30% | 30% | 30% | 20% | 50% | 20% | 50% |  | 7
| - of which installation | 70% | 70% | 70% | 50% | 80% | 50% | 80% |  | 7
| Fixed O&M ($/MWe/year) | 41900 | 40200 | 37300 | 22000 | 41900 | 22000 | 41900 |  | 4,5,7
| Variable O&M ($/MWh) | 0.5 | 0.48 | 0.445 | 0.375 | 0.625 | 0.33375 | 0.55625 | B | 1
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
2 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
5 | IEA, World Energy Outlook, 2015.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
8 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
9 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## Mini-micro hydro power plant
Technology
| Technology | Hydro power plant - Mini/micro system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 5 | 5 | 5 | 1 | 10 | 1 | 10 |  | 1,8
| Generating capacity for total power plant (MWe) | 5 | 5 | 5 | 1 | 10 | 1 | 10 |  | 1,8
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 70 | 90 | 70 | 90 | A | 7
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 70 | 90 | 70 | 90 | A | 7
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | 80 | 80 | 80 | 50 | 95 | 50 | 95 |  | 2,10
| Capacity factor (%), incl. outages | 75.8846 | 75.8846 | 75.8846 | 50 | 95 | 50 | 95 |  | 2,10
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | E
| Minimum load (% of full load) | - | - | - | - | - | - | - | E
| Warm start-up time (hours) | - | - | - | - | - | - | - | E
| Cold start-up time (hours) | - | - | - | - | - | - | - | E
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.7 | 2.592 | 2.403 | 1.2 | 4 | 1.2 | 4 | D,F | 1,5,9
| - of which equipment | 30% | 30% | 30% | 20% | 50% | 20% | 50% |  | 9
| - of which installation | 70% | 70% | 70% | 50% | 80% | 50% | 80% |  | 9
| Fixed O&M ($/MWe/year) | 53000 | 50900 | 47200 | 39800 | 66300 | 35400 | 59000 | C | 1,5,9
| Variable O&M ($/MWh) | 0.5 | 0.48 | 0.445 | 0.375 | 0.625 | 0.33375 | 0.55625 | C | 1,5
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IEA, World Energy Outlook, 2015.
5 | Learning curve approach for the development of financial parameters.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IFC, 2015, "Hydroelectric Power - A guide for developers and investers".
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
9 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
10 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properbly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive and the uncertainty can be even more extreme than listed. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | It is assumed that micro and mini hydro do not have a reservior (run-of-river) and therefor is not capable of regulation. The possibility of a turbine bypass could give the possibility of down regulation.
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## Hydro pumped storage
Technology
| Technology | Hydro pumped storage
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 250 | 250 | 250 | 100 | 500 | 100 | 500 | A | 1,6
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 100 | 4000 | 100 | 4000 |  | 1,6
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1,3,5
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1,3,5
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 5
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 5
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 4.3 | 4.3 | 4.3 | 2.15 | 6.45 | 2.15 | 6.45 | B | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 15 | 45 | 15 | 45 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 2,5
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 0.86 | 0.86 | 0.86 | 0.6 | 6 | 0.6 | 6 | C,E | 1,3,4
| - of which equipment (%) | 30% | 30% | 30% | 20% | 50% | 20% | 50% |  | 7
| - of which installation (%) | 70% | 70% | 70% | 50% | 80% | 50% | 80% |  | 7
| Fixed O&M ($/MWe/year) | 8000 | 8000 | 8000 | 4000 | 30000 | 4000 | 30000 |  | 3,4,6.7
| Variable O&M ($/MWh) | 1.325 | 1.325 | 1.325 | 0.5 | 3 | 0.5 | 3 |  | 1,7
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Size of reservoir (MWh) | 10000 | 10000 | 10000 | 3000 | 20000 | 3000 | 20000 | D | 1,6
| Load/unload time (hours) | 10 | 10 | 10 | 4 | 12 | 4 | 12 | D | 1,6
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
3 | Lazard, 2016, “Lazard’s Levelised Cost of Storage – version 2.0”.
4 | MWH, 2009, Technical Analysis of Pumped Storage and Integration with Wind Power in the Pacific Northwest
5 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
6 | Connolly, 2009, "A Review of Energy Storage Technologies - For the integration of fluctuating renewable energy".
7 | IRENA, 2012, "Renewable Energy Technologies: Cost Analysis Series - Hydropower".
Notes:
A | Size per turbine.
B | Uncertainty (Upper/Lower) is estimated as +/- 50%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | The size of the total power plant and not per unit (turbine).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## Ground-mounted PV
Technology
| Technology | Utility-scale Solar PV
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity a typical power plant (MWe) | 10 | 20 | 50 |  |  |  |  | C | 1
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 35 | 40 | 40 | 25 | 40 | 35 | 45 |  | 1,6
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1
| Space requirement (1000 m2/MWp) | 14 | 14 | 14 | 13 | 18 | 13 | 18 |  | 6
Additional data for non thermal plants
| Capacity factor (%), theoretical | 19.4064 | 22.2603 | 22.2603 | 17 | 23 | 17 | 23 |  | 1,2
| Capacity factor (%), incl. outages | 19.4064 | 22.2603 | 22.2603 | 17 | 23 | 17 | 23 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
| Financial data | [9 empty] | 0.71 | 0.781
| Nominal investment (M$/MWe) | 0.792 | 0.56232 | 0.41184 | 0.7 | 1.2 | 0.31 | 0.71 | D,R,S | 1,3,4
| - of which equipment | 44.44% | 39.12% | 34.72%
| - of which installation | 55.56% | 60.88% | 65.28%
| Fixed O&M ($/MWe/year) | 14400 | 10000 | 8000 | 10800 | 18000 | 5300 | 10700 | E,Q | 5,6
| Variable O&M ($/MWh) | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1800 | 1800 | 1800 |  |  |  |  | F | 8
| DC/AC sizing factor (Wp/W) | 1.1 | 1.1 | 1.1 |  |  |  |  | G
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
| Performance ratio [-] | 0.86 | 0.95 | 0.97 |  |  |  |  | I | 5.6
| PV module conversion efficiency (%) | 20.5% | 23% | 26% | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kW) | 1700 | 1950 | 1950 |  |  |  |  | J, L
| Peak power full load hours (kWh/kWp) | 1550 | 1750 | 1750 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.32 | 0.2 | 0.13 | [5 empty] | 6.9
| Balance Of Plant cost ($/Wp) | 0.4 | 0.3112 | 0.2444 | [5 empty] | 6.9
| Specific investment, total system ($/Wp) | 0.72 | 0.5112 | 0.3744 |  |  |  |  | M | 5,6,9
| Specific investment, total system (M$/MW) | 0.792 | 0.56232 | 0.41184 |  |  |  |  | P
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IEA, World Energy Outlook, 2019.
4 | Learning curve approach for the development of financial parameters.
5 | Cirata 1 MW Solar PV O&M and Financial Perspective, Sharing Experience. PJB.
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | Permasalahan penetrasi solar pv pada sistem grid nasional, Dewan Energi Nasional, Juni 2017 PT Len Industri (Persero)
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1800 kWh/m2 corresponds to a good location in Indonesia, in the top 20% percentile of the best solar sites.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Indonesian prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Rooftop PV
Technology
| Technology | Rooftop PV grid connected
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kW) | 5 | 5 | 5 |  |  |  |  | C | 1,6
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 35 | 40 | 40 | 25 | 40 | 35 | 45 |  | 1,6
| Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1
| Space requirement (m2/kW) | 7 | 6 | 5 | 13 | 18 | 13 | 18 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 17.6941 | 19.4064 | 19.4064 | 17 | 23 | 17 | 23 |  | 1,2
| Capacity factor (%), incl. outages | 17.6941 | 19.4064 | 19.4064 | 17 | 23 | 17 | 23 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.32 | 0.9372 | 0.6864 | 1.15 | 2 | 0.5 | 1.2 | D,R,S | 1,3,4
| - of which equipment | 44.44% | 39.12% | 34.72%
| - of which installation | 55.56% | 60.88% | 65.28%
| Fixed O&M ($/MWe/year) | 14400 | 10000 | 8000 | 10800 | 18000 | 5300 | 10700 | E,Q | 5,6
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1600 | 1600 | 1600 |  |  |  |  | F | 8
| DC/AC sizing factor (Wp/W) | 1.1 | 1.1 | 1.1 |  |  |  |  | G
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
| Performance ratio | 0.86 | 0.95 | 0.97 |  |  |  |  | I | 5.6
| PV module conversion efficiency (%) | 20.5% | 23% | 26% | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kW) | 1550 | 1700 | 1700 |  |  |  |  | J, L
| Peak power full load hours (kWh/kWp) | 1400 | 1550 | 1550 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.53333 | 0.33333 | 0.21667 | [5 empty] | 6.9
| Balance Of Plant cost ($/Wp) | 0.66667 | 0.51867 | 0.40733 | [5 empty] | 6.9
| Specific investment, total system ($/Wp) | 1.2 | 0.852 | 0.624 |  |  |  |  | M | 5,6,9
| Specific investment, total system (million $/MW) | 1.32 | 0.9372 | 0.6864 |  |  |  |  | P
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IEA, World Energy Outlook, 2019.
4 | Learning curve approach for the development of financial parameters.
5 | Cirata 1 MW Solar PV O&M and Financial Perspective, Sharing Experience. PJB.
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | Permasalahan penetrasi solar pv pada sistem grid nasional, Dewan Energi Nasional, Juni 2017 PT Len Industri (Persero)
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1800 kWh/m2 corresponds to a good location in Indonesia, in the top 20% percentile of the best solar sites.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Indonesian prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Industrial PV
Technology
| Technology | Industrial PV - Large scale grid connected
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kWe) | 100 | 100 | 100 |  |  |  |  | C | 6
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | #REF! | #REF! | #REF! | 25 | 40 | 35 | 45 |  | 1,6
| Construction time (years) | #REF! | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1
| Space requirement (1000 m2/MWe) | 9 | 8 | 7 | 13 | 18 | 13 | 18
Additional data for non thermal plants
| Capacity factor (%), theoretical | 17.6941 | 19.4064 | 19.4064 | 14 | 22 | 16 | 23 |  | 1,2
| Capacity factor (%), incl. outages | 17.6941 | 19.4064 | 19.4064 | 14 | 22 | 16 | 23 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.188 | 0.84348 | 0.61776 | 1.05 | 1.8 | 0.465 | 1.065 | D,R,S | 1,3,4
| - of which equipment | 44.44% | 35.84% | 33.96%
| - of which installation | 55.56% | 64.16% | 66.04%
| Fixed O&M ($/MWe/year) | 14400 | 10000 | 8000 | 10800 | 18000 | 5300 | 10700 | E,Q | 5,6
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1600 | 1600 | 1600 |  |  |  |  | F | 8
| DC/AC sizing factor (Wp/W) | 1.1 | 1.1 | 1.1 |  |  |  |  | G
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
| Performance ratio | 0.86 | 0.95 | 0.97 |  |  |  |  | I | 5.6
| PV module conversion efficiency (%) | 20.5% | 23% | 26% | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kW) | 1550 | 1700 | 1700 |  |  |  |  | J, L
| Peak power full load hours (kWh/kWp) | 1400 | 1550 | 1550 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.48 | 0.27486 | 0.1907 | [5 empty] | 6.9
| Balance Of Plant cost ($/Wp) | 0.6 | 0.4668 | 0.3666 | [5 empty] | 6.9
| Specific investment, total system ($/Wp) | 1.08 | 0.7668 | 0.5616 |  |  |  |  | M | 5,6,9
| Specific investment, total system (million $/MW) | 1.188 | 0.84348 | 0.61776 |  |  |  |  | P
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IEA, World Energy Outlook, 2019.
4 | Learning curve approach for the development of financial parameters.
5 | Cirata 1 MW Solar PV O&M and Financial Perspective, Sharing Experience. PJB.
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | Permasalahan penetrasi solar pv pada sistem grid nasional, Dewan Energi Nasional, Juni 2017 PT Len Industri (Persero)
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1800 kWh/m2 corresponds to a good location in Indonesia, in the top 20% percentile of the best solar sites.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Indonesian prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Floating PV
Technology
| Technology | Floating PV - Large scale grid connected
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (MWe) | 10 | 10 | 10 |  |  |  |  | C
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | #REF! | #REF! | #REF! | 25 | 40 | 35 | 45 |  | 1,6
| Construction time (years) | #REF! | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1
| Space requirement (1000 m2/MWe) | 14 | 12 | 12 | 13 | 18 | 13 | 18
Additional data for non thermal plants
| Capacity factor (%), theoretical | 20.9589 | 24.0411 | 24.0411 | 14 | 22 | 16 | 23 |  | 1,2
| Capacity factor (%), incl. outages | 20.9589 | 24.0411 | 24.0411 | 14 | 22 | 16 | 23 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 0.891 | 0.65934 | 0.48132 | 0.833 | 1.428 | 0.3689 | 0.8449 | D,R,S | 1,3,4
| - of which equipment | 50.62% | 49.93% | 47.2%
| - of which installation | 49.38% | 50.07% | 52.8%
| Fixed O&M ($/MWe/year) | 16200 | 13500 | 11300 | 12200 | 20300 | 8500 | 14100 | E,Q | 5,6
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1800 | 1800 | 1800 |  |  |  |  | F | 8
| DC/AC sizing factor (Wp/W) | 1.1 | 1.1 | 1.1 |  |  |  |  | G
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
| Performance ratio | 0.86 | 0.95 | 0.97 |  |  |  |  | I | 5.6
| PV module conversion efficiency (%) | 20.5% | 23% | 26% | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kW) | 1700 | 1950 | 1950 |  |  |  |  | J, L
| Peak power full load hours (kWh/kWp) | 1550 | 1750 | 1750 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.41 | 0.2993 | 0.20652 | [5 empty] | 6.9
| Balance Of Plant cost ($/Wp) | 0.4 | 0.3001 | 0.23105 | [5 empty] | 6.9
| Specific investment, total system ($/Wp) | 0.81 | 0.5994 | 0.43756 |  |  |  |  | M | 5,6,9
| Specific investment, total system (million $/MW) | 0.891 | 0.65934 | 0.48132 |  |  |  |  | P
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IEA, World Energy Outlook, 2019.
4 | Learning curve approach for the development of financial parameters.
5 | Cirata 1 MW Solar PV O&M and Financial Perspective, Sharing Experience. PJB.
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | Permasalahan penetrasi solar pv pada sistem grid nasional, Dewan Energi Nasional, Juni 2017 PT Len Industri (Persero)
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
10 | Iselectric brochure. Last accessed: September 2020
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1800 kWh/m2 corresponds to a good location in Indonesia, in the top 20% percentile of the best solar sites.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Indonesian prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Wind Onshore
Technology
| Technology | Wind power - Onshore
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3.5 | 4 | 5 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 70 | 80 | 100 | [5 empty] | 1
| Electricity efficiency, net (%), name plate | 100 | 100 | 100 |  |  |  |  | A
| Electricity efficiency, net (%), annual average | 100 | 100 | 100
| Forced outage (%) | 2.5% | 2% | 2%
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 35 | 35.56 | 36.68 | 20 | 45 | 20 | 45 | B
| Capacity factor (%), incl. outages | 34.02 | 34.7416 | 35.8358
Ramping configurations
| Ramping (% per minute) | - | - | - |  |  |  |  | F
| Minimum load (% of full load) | - | - | - |  |  |  |  | F
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.5 | 1.275 | 1.08 | 1.2 | 2.35 | 0.8 | 1.85 | D,G | 1
| - of which equipment | 65% | 65% | 65% |  |  |  |  | C | 2, 3
| - of which installation | 35% | 35% | 35% |  |  |  |  | C | 2, 3
| Fixed O&M ($/MWe/year) | 60000 | 51000 | 43200 | 30000 | 70000 | 25000 | 60000 |  | 4
| Variable O&M ($/MWh) | 0 | 0 | 0 | [5 empty] | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
References:
1 | PLN data provided by the System Planning Division at PLN. Supported by review of international price data, cf. technology description.
2 | IRENA (2015). Renewable Power Generation Cost in 2014
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
5 | Vestas data provided by the Sales Division for the Asian Pacific.
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | The capacity factor provided represent an average of good locations in Indonesia, see presentation in catalogue text. As mentioned in the description, generelly speaking, the wind resource in Indonesia.
C | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
D | The IEA expects approximately a doubling of the accumulated wind power capacity between 2020 and 2030 and 4-5 times more by 2050 compared to 2020. Assuming a learning of 12.5 % per annum this yields a cost reduction of approx. 13 % by 2030 and approx. 25 % by 2050.
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
G | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Small wind onshore
Technology
| Technology | Wind power - Small onshore wind turbines < 1 MW
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.85 | 0.9 | 0.95 | [5 empty] | 6
| Generating capacity for total power plant (MWe) | 12.75 | 18 | 19 | [5 empty] | 5
| Electricity efficiency, net (%), name plate | 100 | 100 | 100 |  |  |  |  | A
| Electricity efficiency, net (%), annual average | 100 | 100 | 100
| Forced outage (%) | 3% | 2.5% | 2%
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 5, 6
| Space requirement (1000 m2/MWe) | 58 | 58 | 58 | [5 empty] | 1, 6
Additional data for non thermal plants
| Capacity factor (%), theoretical | 35 | 35.56 | 36.68 | 20 | 45 | 20 | 45 | B | 2
| Capacity factor (%), incl. outages | 33.8455 | 34.5643 | 35.8358
Ramping configurations
| Ramping (% per minute) | - | - | - |  |  |  |  | F
| Minimum load (% of full load) | - | - | - |  |  |  |  | F
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 4 | 3.4 | 2.88 | 3 | 5 | 3.6 | 2.16 | D,E | 5, 6
| - of which equipment | 55% | 55% | 55% |  |  |  |  | C
| - of which installation | 45% | 45% | 45% |  |  |  |  | C
| Fixed O&M ($/MWe/year) | 73200 | 62200 | 52700 | 54900 | 91500 | 65900 | 39500 | E | 4
| Variable O&M ($/MWh) | 0 | 0 | 0 | [5 empty] | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
References:
1 | PLN data provided by Pak Arief Sugiyanto, System Planning Devision at PLN. Supported by review of international price data, cf. technology description.
2 | Wind Energy Resources of Indonesia 2014-2017, EMD International A/S, Denmark, financed by the Environmental Support Programme 3 (ESP3) / Danida.
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
5 | Case: Faroe Islands, Húsahagi 2014
6 | Case: Kenya, Lake Turkana, 2014-2017
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | The capacity factor provided represent an average of good locations in Indonesia, see presentation in catalogue text. As mentioned in the description, generelly speaking, the wind resource in Indonesia is scarce.
C | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
D | The IEA expects approximately a doubling of the accumulated wind power capacity between 2020 and 2030 and 4-5 times more by 2050 compared to 2020. Assuming a learning of 12.5 % per annum this yields a cost reduction of approx. 13 % by 2030 and approx. 25 % by 2050.
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).

## Wind Offshore
Technology
| Technology | Wind power - Offshore
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 8 | 10 | 12 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 240 | 300 | 360
| Electricity efficiency, net (%), name plate | 100 | 100 | 100 |  |  |  |  | A
| Electricity efficiency, net (%), annual average | 100 | 100 | 100 |  |  |  |  | A
| Forced outage (%) | 4% | 3% | 3% | [5 empty] | 3
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | [5 empty] | 3
| Technical lifetime (years) | 27 | 30 | 30 | 20 | 35 | 20 | 35 |  | 3
| Construction time (years) | 3 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 3
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | 168 | 204 | 168 | 204 |  | 3
Additional data for non thermal plants
| Capacity factor (%), theoretical | 50 | 50.8 | 52.4 |  |  |  |  | B | 2
| Capacity factor (%), incl. outages | 47.8523 | 49.1244 | 50.6716
Ramping configurations
| Ramping (% per minute) | - | - | - |  |  |  |  | F
| Minimum load (% of full load) | - | - | - |  |  |  |  | F
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 3.5 | 2.975 | 2.52 | 2.4 | 3.7 | 1.55 | 2.9 | D,G | 3
| - of which equipment | 45% | 45% | 45% |  |  |  |  | C | 3
| - of which installation | 55% | 55% | 55% |  |  |  |  | C | 3
| Fixed O&M ($/MWe/year) | 72600 | 61700 | 52300 | 58200 | 78200 | 38000 | 57200 |  | 4
| Variable O&M ($/MWh) | 5.5 | 4.8 | 3.9 | 3.4 | 5.8 | 2.7 | 4.3 |  | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
References:
1 | PLN data provided by Pak Arief Sugiyanto, System Planning Devision at PLN. Supported by review of international price data, cf. technology description.
2 | Wind Energy Resources of Indonesia 2014-2017, EMD International A/S, Denmark, financed by the Environmental Support Programme 3 (ESP3) / Danida.
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | The capacity factor provided represent an average of good locations in Indonesia, see presentation in catalogue text.
C | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
D | The IEA expects approximately a doubling of the accumulated wind power capacity between 2020 and 2030 and 4-5 times more by 2050 compared to 2020. Assuming a learning of 12.5 % per annum this yields a cost reduction of approx. 13 % by 2030 and approx. 25 % by 2050.
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
G | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Tidal Impoundment
Technology
| Technology | Tidal power - Impoundment Type
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 10 | 25 | 1 | 25 | 1 | 25 | A | 3
| Generating capacity for total power plant (MWe) | 30 | 100 | 150 | 10 | 300 | 10 | 300 | B | 3
| Electricity efficiency, net (%), name plate | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
| Electricity efficiency, net (%), annual average | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
| Forced outage (%) | 4% | 4% | 4% | 2% | 6% | 2% | 6%
Planned outage (weeks per year)
| Technical lifetime (years) | 40 | 40 | 50 | 30 | 120 | 30 | 120 | C | 2
| Construction time (years) | 5 | 5 | 4 | 4 | 6 | 4 | 6 |  | 3,5
| Space requirement (1000 m2/MWe) | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | D
Additional data for non thermal plants
| Capacity factor (%), theoretical | 35 | 35 | 40 | 35 | 40 | 35 | 40 | E
Capacity factor (%), incl. outages
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 | G
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.5 | 5.1092 | 5.1 | 2.9 | 7.5 | 2.9 | 7.5 | E | 1,2,4
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 70800 | 62500 | 35700 | 23400 | 72000 | 23400 | 72000 | E | 1,2,3,4
| Variable O&M ($/MWh) | 0 | 0 | 0
Start-up costs ($/MWe/start-up)
Technology specific data
References:
1 | DECC GOV.UK, “The UK 2050 Calculator: Tidal Range Cost Data,” 2011.
2 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010
3 | IRENA, “Tidal Energy Technology Brief,” 2014
4 | Pacific Northwest National Laboratory (PNNL), Tethys
5 | Tatiana Montllonch Araquistain, Tidal Power: Economic and Technological assessment.
Notes:
A | Based on various projects and company datasheets. The turbine size can vary from project to project based on requirement. The Sihwa Lake project in Korea has 25.4 MW turbines.
B | The capacity is strongly dependent on resources available and shape of coastline. Although a lot of proposed plants are much larger in size, with some being over 2 GW as well, the capacity shown here is based on deployment of plants so far.
C | Actual operational life can be upto 120 years. However, lifetime is taken as 40 years, since there can be significant re-fitting costs after 40 years and discounted cash flows are insignificant after 40 years.
D | Based on information of proposed plants.
E | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
F | Bulb type turbines are commonly used for tidal impoundment plants. The value here is estimated based on efficiencies of bulb type water turbines.
G | Considered as similar to Hydro

## Tidal Stream
Technology
| Technology | Tidal power - Stream Type
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 2 | 2 | 0.1 | 6 | 1 | 6 | A | 3,5
| Generating capacity for total power plant (MWe) | 10 | 150 | 150 | 1 | 400 | 1 | 400 | A | 3,5
| Electricity efficiency, net (%), name plate | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2,3,5
| Electricity efficiency, net (%), annual average | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2,3,5
| Forced outage (%) | 4% | 4% | 4% | 2% | 6% | 2% | 6% |  | 2
Planned outage (weeks per year)
| Technical lifetime (years) | 25 | 25 | 30 | 20 | 30 | 20 | 30 | B
| Construction time (years) | 3 | 2 | 2 |  |  |  |  | C
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1,2,4
| Capacity factor (%), incl. outages | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1,2,4
Ramping configurations
| Ramping (% per minute) | - | - | -
| Minimum load (% of full load) | - | - | -
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.3 | 4.6 | 3.4 | 3 | 7.1 | 2 | 7.1 | B | 1,2,3
| - of which equipment | 87% | 87% | 87% | 83% | 91% | 83% | 91% |  | 1,2
| - of which installation | 13% | 13% | 13% | 9% | 17% | 9% | 17% |  | 1,2
| Fixed O&M ($/MWe/year) | 283000 | 230000 | 114000 | 93000 | 412000 | 93000 | 412000 | B | 1,2
| Variable O&M ($/MWh) | 11.7257 | 8.7943 | 7.3286 | [5 empty] | 4
Start-up costs ($/MWe/start-up)
Technology specific data
References:
1 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010.
2 | Ocean Energy Systems - OES (IEA), “International Levelised Cost of Energy for Ocean Energy Technologies,” 2015.
3 | SIMEC Atlantis Energy, Projects
4 | UK Govt., Electricity Generation Costs 2020 (back calculation from LCOE values)
5 | Pacific Northwest National Laboratory (PNNL), Tethys
Notes:
A | Projects are in the early stages os turbines and capacities are smaller. Larger projects are expected to be executed in smaller capacity phases.
B | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
C | Estimated based on MeyGen tidal stream project

## Coal Subcritical
Technology
| Technology | Subcritical coal power plant | [8 empty] | Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 150 | 150 | 150 | 100 | 200 | 100 | 200 |  | 1
| Generating capacity for total power plant (MWe) | 150 | 150 | 150 | 100 | 200 | 100 | 200 |  | 1
| Electricity efficiency, net (%), name plate | 34.83 | 35.8749 | 36.9198 | 30 | 38 | 33 | 39 |  | 1,2,3
| Electricity efficiency, net (%), annual average | 34.33 | 35.3599 | 36.3898 | 29 | 37 | 32 | 38 |  | 1,2,3
| Forced outage (%) | 7 | 5 | 3 | 5 | 20 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 6 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 3.25 | 3.25 | 3.25 | 2 | 4 | 2 | 4 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 3.5 | 3.5 | 3.5 | 2 | 4 | 2 | 4 | B | 1
| Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
| Warm start-up time (hours) | 3 | 3 | 3 | 1 | 5 | 1 | 5 | B | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 5 | 12 | 5 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | A,F | 2,4
| SO2 (degree of desulphuring, %) | 73 | 80 | 95 | 73 | 95 | 73 | 95 | A,C,D | 2,4
| NOX (g per GJ fuel) | 262.5 | 150 | 38 | 262.5 | 262.5 | 262.5 | 262.5 | A,D | 2,4
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 1.65 | 1.6005 | 1.551 | 1 | 1.7 | 1.05 | 1.7 | E,H | 1,3
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 45300 | 43900 | 42600 | 34000 | 56600 | 32000 | 53300 | G | 1,3
| Variable O&M ($/MWh) | 0.125 | 0.12125 | 0.1175 | 0.09375 | 0.15625 | 0.088125 | 0.14687 | G | 1,3
| Start-up costs ($/MWe/start-up) | 110 | 110 | 110 | 50 | 200 | 50 | 200 |  | 5
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability.
C | Indonesian sulphur content in coal is up to 360 g/GJ. Conversion factor 0.35 to mg/Nm3 yields 1030 mg/Nm3. With a max of 750 mg/Nm3 then gives a % of desulphuring of 73%.
D | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
E | For economy of scale a proportionality factor, a, of 0.8 is suggested.
F | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
G | Uncertainty (Upper/Lower) is estimated as +/- 25%.
H | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## Coal Supercritical
Technology
| Technology | Supercritical coal power plant
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
| Generating capacity for total power plant (MWe) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
| Electricity efficiency, net (%), name plate | 37.67 | 38.8001 | 39.9302 | 33 | 40 | 35 | 42 |  | 1,3,6,7
| Electricity efficiency, net (%), annual average | 36.67 | 37.7701 | 38.8702 | 33 | 40 | 35 | 42 |  | 1,3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 3.75 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 4 | 4 | 4 | 3 | 4 | 3 | 4 | B | 1
| Minimum load (% of full load) | 25 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | F | 2,4
| SO2 (degree of desulphuring, %) | 73 | 73 | 73 | 73 | 95 | 73 | 95 | C,D | 2,4
| NOX (g per GJ fuel) | 262.5 | 262.5 | 262.5 | 262.5 | 262.5 | 262.5 | 262.5 | D | 2,4
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.4 | 1.358 | 1.316 | 1.05 | 1.75 | 0.987 | 1.645 | E,G,H | 1,3,6,7
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 41200 | 40000 | 38700 | 30900 | 51500 | 29000 | 48400 | G | 1,3,6,7
| Variable O&M ($/MWh) | 0.12 | 0.1164 | 0.1128 | 0.09 | 0.15 | 0.0846 | 0.141 | G | 1,3
| Start-up costs ($/MWe/start-up) | 50 | 50 | 50 | 40 | 100 | 40 | 100 |  | 5
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IEA, World Energy Outlook, 2015.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability.
C | Indonesian sulphur content in coal is up to 360 g/GJ. Conversion factor 0.35 to mg/Nm3 yields 1030 mg/Nm3. With a max of 750 mg/Nm3 then gives a % of desulphuring of 73%.
D | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
E | For economy of scale a proportionality factor, a, of 0.85 is suggested.
F | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
G | Uncertainty (Upper/Lower) is estimated as +/- 25%.
H | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## Coal Ultra supercritical
Technology
| Technology | Ultra-supercritical coal power plant
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
| Electricity efficiency, net (%), name plate | 42.5 | 43.775 | 45.05 | 40 | 45 | 42 | 47 |  | 1,3,6,7
| Electricity efficiency, net (%), annual average | 41.5 | 42.745 | 43.99 | 40 | 45 | 42 | 47 |  | 1,3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 4.33 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 5 | 5 | 5 | 4 | 5 | 4 | 5 | B | 1
| Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | F | 2,4
| SO2 (degree of desulphuring, %) | 73 | 73 | 73 | 73 | 95 | 73 | 95 | C,D | 2,4
| NOX (g per GJ fuel) | 262.5 | 262.5 | 262.5 | 262.5 | 262.5 | 262.5 | 262.5 | D | 2,4
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.5248 | 1.4791 | 1.4333 | 1.1436 | 1.906 | 1.075 | 1.7916 | E,G,H | 1,3,6,7
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 56600 | 54900 | 53200 | 42500 | 70800 | 39900 | 66500 | G | 1,3,6,7
| Variable O&M ($/MWh) | 0.11 | 0.1067 | 0.1034 | 0.0825 | 0.1375 | 0.07755 | 0.12925 | G | 1,3
| Start-up costs ($/MWe/start-up) | 50 | 50 | 50 | 40 | 100 | 40 | 100 |  | 5
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IEA, World Energy Outlook, 2015.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability.
C | Indonesian sulphur content in coal is up to 360 g/GJ. Conversion factor 0.35 to mg/Nm3 yields 1030 mg/Nm3. With a max of 750 mg/Nm3 then gives a % of desulphuring of 73%.
D | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
E | For economy of scale a proportionality factor, a, of 0.85 is suggested.
F | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
G | Uncertainty (Upper/Lower) is estimated as +/- 25%.
H | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## IGCC
Technology
| Technology | IGCC
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 150-200 | 150-200 | 150-200 |  |  |  |  | A
| Generating capacity for total power plant (MWe) | 600 | 600 | 600 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | 42 | 43 | 45 |  |  |  |  | G | 1
| Electricity efficiency, net (%), annual average | 40 | 41 | 43 |  |  |  |  | G
| Cold gas efficiency (%) | 75 | 80 | 80 |  |  |  |  | B
| Forced outage (%) | 5.53 | 6 | 6 | [5 empty] | 2
| Planned outage (weeks per year) | 6.6 | 7 | 7 |  |  |  |  | C | 3
| Technical lifetime (years) | 30 | 30 | 30 | [5 empty] | 1
| Construction time (years) | 4 | 4 | 4 | [5 empty] | 4
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 3 | 3.5 | 5 |  |  |  |  | D | 5
| Minimum load (% of full load) | 50 | 40 | 30 |  |  |  |  | D | 5
| Warm start-up time (hours) | 6 | 6 | 6 | [5 empty] | 10, 11
| Cold start-up time (hours) | 15-80 | 15-80 | 15-80 |  |  |  |  | F | 10, 11
Environment
| PM 2.5 (mg per Nm3) | 115 | 100 | 100 | [5 empty] | 7,12
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 9,12
| NOX (g per GJ fuel) | 173 | 51.6796 | 49.3827 | [5 empty] | 7,12
CO (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.4 | 2.21 | 2.04 | 2.16 | 3.5 | 1.75 | 3 | H | 6,13
| - of which equipment (%) | 30 | 30 | 30 | 25 | 50 | 25 | 50 |  | 6,13
| - of which installation (%) | 70 | 70 | 70 | 50 | 75 | 50 | 75 |  | 6
| Fixed O&M ($/MWe/year) | 60000 | 58200 | 56400 | 56100 | 68400 | 52700 | 68400 |  | 6
| Variable O&M ($/MWh) | 12 | 11.6 | 11.2 | 15 | 7.88 | 14 | 7.88 |  | 6,13
| Start-up costs ($/MWe/start-up) | 100 | 100 | 100 |  |  |  |  | E
References:
1 | MDPI, 2018, "Life Cycle Analysis of Integrated Gasification Combined Cycle Power Generation in the Context of Southeast Asia,"
2 | IEEFA, 2018,"Lezna IGCC Project: High Costs and Unreliable Operations Can Be Expected"
3 | Nevile Holt - EPRI, 2004,"Coal-based IGCC Plans - Recent Operating Experience and Lessons Learned"
4 | EFDA, 2013, "Review and Update of Power Sector"
5 | Modern Power Systems, Increasing the flexibility of IGCC, https://www.modernpowersystems.com/features/featureincreasing-flexibility-of-igcc-4893259/
6 | Global CCS Institute, 2017, "Global Costs of Carbon Capture and Storage"
7 | Michael A. Mac Kinnon, University of California, 2017, "The role of natural gas and its infrastructure in mitigating greenhouse gas emissions, improving regional air quality, and renewable resource integration"
8 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
9 | United States Department of Energy National Energy Technology Laboratory, Gasification Plant Cost and Performance Optimization, 2002
10 | IEAGHG, Operating Flexibility of Power Plants with CCS
11 | EPRI, Increasing the Flexibility of IGCC Power Plants
12 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
13 | NREL ATB 2020
Notes:
A | IGCCs use combined (gas) cycles to produce power. Their efficiency is higher for big plant sizes (economy of scale). Preliminary screenings in Sumatra and Kalimantan identify in 150-200 MW the IGCC size.
B | The cold gas efficiency is the efficiency of the gasification unit
C | Unplanned outages can be sizeable. These mainly concern corrosion and fouling in the heat exchangers, particularly the syngas coolers.
D | It is assumed that improvements in the air sepration unit (ASU) and in the gasification unit boost the cycle's ramping capabilities in the coming years
E | Start-up costs vary depending on the idle time. Warm-up of the gasification unit requires time and can be expensive, therefore start-up cost is higher than a CC plant.
F | Start-up time is the necessary time to reach minimum load. It takes a long time for IGCC to reach full-load and it can vary depending on the specific technology, hence the wide range.
G | The efficiency is strongly dependent on coal type. High-grade coal can lead to efficiencies of over 45%, but low-rank coal (3-4000 kcal/kg) used in Indonesia leads to lower efficiencies with today's technology.
H | Price for one unit. An IGCC power plant consisting of two units can be considered to have a 10% lower overnight cost

## CCGT
Technology
| Technology | Combined Cycle Gas Turbine
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 600 | 600 | 600 | 200 | 800 | 200 | 800 |  | 1
| Generating capacity for total power plant (MWe) | 600 | 600 | 600 | 200 | 800 | 200 | 800 |  | 1
| Electricity efficiency, net (%), name plate | 57 | 60 | 61 | 45 | 62 | 55 | 65 |  | 1,3,5,10
| Electricity efficiency, net (%), annual average | 56 | 59 | 60 | 39 | 61 | 54 | 64
| Forced outage (%) | 5 | 5 | 5 | 3 | 10 | 3 | 10 |  | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | 3 | 8 | 3 | 8 |  | 1
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 1,2
| Minimum load (% of full load) | 45 | 30 | 15 | 30 | 50 | 10 | 40 | A | 5
| Warm start-up time (hours) | 2 | 1 | 1 | 1 | 3 | 0.5 | 2 | A | 1,5
| Cold start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 |  | 1,5
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 86.4 | 60 | 20 | 20 | 86 | 20 | 86 | A,D | 7,8
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 0.69 | 0.6555 | 0.6072 | 0.65 | 1 | 0.55 | 0.9 | F,H | 1,3,10
| - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| Fixed O&M ($/MWe/year) | 23500 | 22800 | 22100 | 17600 | 29400 | 16600 | 27600 | B | 1,3
| Variable O&M ($/MWh) | 2.3 | 2.231 | 2.162 | 1.725 | 2.875 | 1.6215 | 2.7025 | B | 1
| Start-up costs ($/MWe/start-up) | 80 | 80 | 80 | 60 | 100 | 60 | 100 | B | 6
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
3 | IEA, World Energy Outlook, 2015.
4 | Learning curve approach for the development of financial parameters.
5 | Siemens, 2010, "Flexible future for combined cycle".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
9 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
10 | IEA, Projected Costs of Generating Electricity, 2015.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## SCGT
Technology
| Technology | Simple Cycle Gas Turbine - large system
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 50 | 50 | 50 | 35 | 65 | 35 | 65 |  | 3
| Generating capacity for total power plant (MWe) | 100 | 100 | 100 | 35 | 150 | 35 | 150 |  | 3
| Electricity efficiency, net (%), name plate | 33.5 | 36 | 40 | [5 empty] | 1,2
| Electricity efficiency, net (%), annual average | 32.5 | 35 | 39 | [5 empty] | 1,2
| Forced outage (%) | 2 | 2 | 2
| Planned outage (weeks per year) | 3 | 3 | 3
| Technical lifetime (years) | 25 | 25 | 25
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.125 | 1.875 | 1.125 | 1.875 | B | 3
| Space requirement (1000 m2/MWe) | 0.02 | 0.02 | 0.02 | 0.015 | 0.025 | 0.015 | 0.025 | B | 3
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 3,8
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 | A | 6
| Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | [5 empty] | 3
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 7
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 86.4 | 60 | 20 | 20 | 86 | 20 | 86 | A,D | 3,7
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 0.7728 | 0.73416 | 0.68006 | 0.65 | 1.2 | 0.55 | 1.1 | F,G,H | 1-5
| - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| Fixed O&M ($/MWe/year) | 23200 | 22500 | 21800 | 17400 | 29000 | 16400 | 27300 | B | 1-5
Variable O&M ($/MWh)
| Start-up costs ($/MWe/start-up) | 24 | 24 | 24 | 18 | 30 | 18 | 30 | B | 6
References:
1 | IEA, Projected Costs of Generating Electricity, 2015.
2 | IEA, World Energy Outlook, 2015.
3 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
4 | Learning curve approach for the development of financial parameters.
5 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | The investment cost of an aero-derivative gas turbine will be in the higher end than an industrial gas turbine (ref. 5) . Roughly 50% higher.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## CCS - Supercritical coal
Technology
| Technology | Supercritical coal power plant with CCS
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | -60 | -60 | -60 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | -60 | -60 | -60 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | -7 | -7 | -7 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | -8 | -8 | -8 | [5 empty] | 1
| Forced outage (%) | 7 | 7 | 7
Planned outage (weeks per year)
Technical lifetime (years)
Construction time (years)
| CO2 emission reduction (%) | -88.76 | -90 | -90 |  |  |  |  | B | 1
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
Capacity factor (%), theoretical
Capacity factor (%), incl. outages
Ramping configuration
| Ramping (% per minute) | 4 | 4 | 4 |  |  |  |  | C | 7
| Minimum load (% of full load) | 30 | 30 | 30 |  |  |  |  | D | 7
| Warm start-up time (hours) | 4 | 4 | 4 |  |  |  |  | E | 8
| Cold start-up time (hours) | 12 | 12 | 12 |  |  |  |  | E | 8
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | [5 empty] | 3,7
| SO2 (degree of desulphuring, %) | 97 | 97 | 97 | [5 empty] | 3,7
| NOX (g per GJ fuel) | 263 | 263 | 263 | [5 empty] | 3,7
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 1.95 | +1.79 | +1.42 | +1.60 | +2.29 | +1.17 | +1.67 |  | 2,5,9,10
| - of which equipment (%) | 30 | 30 | 30 | 25 | 50 | 25 | 50 |  | 1
| - of which installation (%) | 70 | 70 | 70 | 50 | 75 | 50 | 75 |  | 1
| Fixed O&M ($/MWe/year) | 41800 | +40500 | +39300 | +13000 | +50000 | +13000 | +50000 |  | 1,7,9
| Variable O&M ($/MWh) | +3.10 | +3.01 | +2.91 | +2.50 | +8.20 | +2.35 | +7.71 |  | 1,5,9
References:
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | EIA, 2016, Capital Cost Estimates for Utility Scale Electricity Generating Plants
6 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermitent renewable energy sources
7 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2020
8 | IEAGHG, Operating Flexibility of Power Plants with CCS
9 | NREL ATB 2020
10 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020.
Notes:
A | The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.

## CCS - CCGT
Technology
| Technology | Natural Gas Combined Cycle with CCS
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | -40 | -40 | -40 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | -40 | -40 | -40 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | -7 | -7 | -7 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | -8 | -8 | -8 | [5 empty] | 1
| Forced outage (%) | 5 | 5 | 5
Planned outage (weeks per year)
| Technical lifetime (years) | -
Construction time (years)
| CO2 emission reduction (%) | -87.46 | -90 | -90 |  |  | -90 | -99 | B | 1
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 |  |  |  |  | C | 6
| Minimum load (% of full load) | 45 | 45 | 45 |  |  |  |  | D | 6
| Warm start-up time (hours) | 2 | 2 | 2 |  |  |  |  | E | 4
| Cold start-up time (hours) | 4 | 4 | 4 |  |  |  |  | E | 4
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | [5 empty] | 3,6
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 3,6
| NOX (g per GJ fuel) | 80 | 80 | 80 | [5 empty] | 3,6
| CH4 (g per GJ fuel) | - | - | -
| N2O (g per GJ fuel) | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.15 | +0.97 | +0.75 | +0.85 | +1.56 | +0.60 | +1.02 |  | 1,7,8
| - of which equipment (%) | 40 | 40 | 40 | 30 | 60 | 30 | 60 |  | 1
| - of which installation (%) | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 1
| Fixed O&M ($/MWe/year) | 9000 | +8700 | +8500 | +7000 | +14000 | +6600 | +14000 |  | 1,7,8
| Variable O&M ($/MWh) | +1.20 | +1.16 | +1.13 | +0.60 | +4.00 | +0.60 | +4.00 |  | 1,7,8
References:
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermitent renewable energy sources
6 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2020
7 | NREL ATB 2020
8 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020.
Notes:
A | The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~10-15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.

## CCS - IGCC
Technology
| Technology | IGCC with CCS
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | -65 | -65 | -65 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | -65 | -65 | -65 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | -7 | -7 | -7 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | -8 | -8 | -8 | [5 empty] | 1
Cold gas efficiency (%)
| Forced outage (%) | 6 | 6 | 6
Planned outage (weeks per year)
| Technical lifetime (years) | -
Construction time (years)
| CO2 emission reduction (%) | -86.32 | -90 | -90 |  |  | -90 | -99 | B | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 3 | 3 | 3 |  |  |  |  | C | 6
| Minimum load (% of full load) | 50 | 50 | 50 |  |  |  |  | D | 6
| Warm start-up time (hours) | 6 | 6 | 6 | [5 empty] | 4
| Cold start-up time (hours) | 15-80 | 15-80 | 15-80 | [5 empty] | 4,7
Environment
| PM 2.5 (mg per Nm3) | 115 | 115 | 115 | [5 empty] | 3,6
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 3,6
| NOX (g per GJ fuel) | 173 | 173 | 173 | [5 empty] | 3,6
CO (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 0.95 | +0.87 | +0.69 | +0.475 | +1.19 | +0.35 | +0.86 | E | 1,8,9
| - of which equipment (%) | 25 | 25 | 25 | 20 | 40 | 20 | 40 |  | 1
| - of which installation (%) | 75 | 75 | 75 | 60 | 80 | 60 | 80 |  | 1
| Fixed O&M ($/MWe/year) | 8900 | +8600 | +8400 | +7100 | +15000 | +6700 | +15000 |  | 1,8
| Variable O&M ($/MWh) | +5.30 | +5.14 | +4.98 | +3.97 | +6.63 | +3.74 | +6.23 |  | 1,8
References:
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermitent renewable energy sources
6 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2020
7 | EPRI, 2015, Increasing the Flecibility of IGCC Power Plants
8 | NREL ATB 2020
9 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020.
Notes:
A | The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~10-15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | Pre-combustion capture is assumed to cause a cost increase ranging between 30-50% of the IGCC price.
[6 empty] | #DIV/0! | #DIV/0!
#DIV/0!

## Biomass power plant (small)
Technology
| Technology | Biomass power plant (smal plant - palm oil / rice husk )
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5
| Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5
| Electricity efficiency, net (%), name plate | 32 | 32 | 32 | 25 | 35 | 25 | 35 |  | 1,3,7
| Electricity efficiency, net (%), annual average | 31 | 31 | 31 | 25 | 35 | 25 | 35 |  | 1,3,7
| Forced outage (%) | 7 | 7 | 7 | 5.25 | 8.75 | 5.25 | 8.75 | A | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 4.5 | 7.5 | 4.5 | 7.5 | A | 1
| Technical lifetime (years) | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 | A | 8,10
| Construction time (years) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A | 10
| Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 | A | 1,9
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | [5 empty] | 3
| Minimum load (% of full load) | 30 | 30 | 30 | [5 empty] | 3
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
| Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 3
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3
| CH4 (g per GJ fuel) | 0.94 | 0.94 | 0.94 | [5 empty] | 3
| N2O (g per GJ fuel) | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Financial data
| Nominal investment (M$/MWe) | 2 | 1.82 | 1.6 | 1.3 | 2.25 | 1.2 | 2 | B,C | 4-8,11
| - of which equipment | 65 | 65 | 65 | 50 | 85 | 50 | 85 |  | 1,2
| - of which installation | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1,2
| Fixed O&M ($/MWe/year) | 47600 | 43800 | 38100 | 35700 | 59500 | 28600 | 47600 | A | 4,5,8,11
| Variable O&M ($/MWh) | 3.043 | 2.7996 | 2.4344 | 2.2823 | 3.8037 | 1.8258 | 3.043 | A | 5,11
Start-up costs ($/MWe/start-up)
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | ASEAN Centre of Energy, 2016, "Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states".
3 | Danish Energy Agency and COWI, 2017, "Technology vatalogue for biomass to energy".
4 | IRENA, 2015, "Renewable power generation cost in 2014"
5 | IFC and BMF, 2017, "Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | India Central Electricity Authority, 2007, "Report on the Land Requirement of Thermal Power Stations".
10 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
11 | Learning curve approach for the development of financial parameters.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Biogas power plant (small)
Technology
| Technology | Biogas power plant
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | [5 empty] | 4
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | [5 empty] | 4
| Forced outage (%) | 5 | 5 | 5 | [5 empty] | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 7
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 7
| Space requirement (1000 m2/MWe) | 70 | 70 | 70 | [5 empty] | 12
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 |  | 11
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 |  | 10
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.15 | 1.9565 | 1.72 | 1.55 | 2.15 | 1.29 | 2.15 | B | 3,5,8,9
| - of which equipment | 65 | 65 | 65 | 50 | 85 | 50 | 85
| - of which installation | 35 | 35 | 35 | 15 | 50 | 15 | 50
| Fixed O&M ($/MWe/year) | 97000 | 89200 | 77600 | 72800 | 121300 | 58200 | 97000 | A | 5,7,9
| Variable O&M ($/MWh) | 0.11 | 0.1012 | 0.088 | 0.0825 | 0.1375 | 0.066 | 0.11 | A | 6,9
Start-up costs ($/MWe/start-up)
References:
1 | PLN, 2017, data provided the System Planning Division at PLN
2 | ASEAN Centre of Energy (2016). Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states.
3 | Winrock, 2015, "Buku Panduan Konversi POME Menjadi Biogas, Pengembangan Proyek di Indonesia", USAID – Winrock International.
4 | RENAC, 2014, "Biogas Technology and Biomass, Renewables Academy (RENAC)".
5 | IFC and BMF, 2017, Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | Learning curve approach for the development of financial parameters.
10 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
11 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
12 | Chazaro Gerbang Internasional, 2004, "Utilization of Biogas Generated from the Anaerobic Treatment of Palm Oil Mills Effluent (POME) as Indigenous Energy Source for Rural Energy Supply and Electrification - A Pre-Feasibility Study Report"
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## MSW incineration
Technology
| Technology | Incineration Power Plant - Municipal Solid Waste
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 21.5896 | 22.3341 | 23.0786
| Generating capacity for total power plant (MWe) | 21.5896 | 22.3341 | 23.0786
| Electricity efficiency, net (%), name plate | 29% | 30% | 31% | 27.5% | 31.5% | 29.5% | 32.5% | A | 1
| Electricity efficiency, net (%), annual average | 27.55% | 28.5% | 29.45% | 26.12% | 29.92% | 28.02% | 30.87% |  | 1
| Forced outage (%) | 1% | 1% | 1% | [5 empty] | 1
| Planned outage (weeks per year) | 2.9 | 2.6 | 2.1 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | 7.5 | 12.5 | 7.5 | 12.5 | C | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 15 | 25 | 15 | 25 | C | 1
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.375 | 0.625 | 0.375 | 0.625 | C | 1
| Cold start-up time (hours) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | C | 1
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment ( million $/MWe) | 6.8 | 6.2873 | 5.6304 | 5.1 | 7.038 | 4.2228 | 7.038 | C | 1
| - of which equipment | 4.012 | 3.3951 | 2.8152 | 3.009 | 3.519 | 2.1114 | 3.519 |  | 1
| - of which installation | 2.788 | 2.8921 | 2.8152 | 2.091 | 3.519 | 2.1114 | 3.519 |  | 1
| Fixed O&M ($/MWe/year) | 243700 | 224800 | 193500 | 195000 | 304600 | 154800 | 241900 | C | 1
| Variable O&M ($/MWh) | 24.1437 | 23.3794 | 22.5829 | 18.1078 | 30.1797 | 16.9371 | 28.2286 | C | 1
Start-up costs ($/MWe/start-up)
Technology specific data
| Waste treatment capacity (tonnes/h) | 27.7 | 27.7 | 27.7 |  |  |  |  | B
References:
1 | Danish Technology Catalogue “Technology Data for Energy Plants, Danish Energy Agency 2107
Notes:
A | Based on experience from the Netherlands where 30 % electric efficiency is achieve. 1 %-point efficiency subtracted to take into account higher temperature of cooling water in Indonesia (approx. +20 C).
B | The investment cost is based on waste to energy CHP plant in Denmark, according to Ref 1. A waste treatment capacity of 27,7 tonnes/h is assumed and an energy content of 10,4 GJ/ton. The specific finalcial data is adjusted to reflect that the plant in Indonesia runs in condensing mode and hence the electric capacity (MWe) is higher than for a combined heat and power, backpressure plant with the same treatment capacity.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Calculated from size, fuel efficiency and an average calory value for waste of 9.7 GJ/ton.

## Landfill
Technology
| Technology | Landfill Gas Power Plant - Municipal Solid Waste
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | 25 | 37 | 25 | 37 |  | 2
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | 25 | 37 | 25 | 37 |  | 2
| Forced outage (%) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Planned outage (weeks per year) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 |  | 3
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.5 | 2.5 | 2.5 | 2.2727 | 2.75 | 2.2727 | 2.875 | A | 3
| - of which equipment | 0.72 | 0.72 | 0.72 | 0.65455 | 0.792 | 0.65455 | 0.828 |  | 5
| - of which installation | 0.28 | 0.28 | 0.28 | 0.25455 | 0.308 | 0.25455 | 0.322 |  | 5
| Fixed O&M ($/MWe/year) | 125000 | 125000 | 125000 | 113640 | 137500 | 113636.3636 | 143750 | A | 3
| Variable O&M ($/MWh) | 13.5 | 13.5 | 13.5 | 10.125 | 16.875 | 10.125 | 16.875
Start-up costs ($/MWe/start-up)
Technology specific data
References:
1 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, Jakarta, Indonesia
2 | Renewables Academy" (RENAC) AG, 2014, "Biogas Technology and Biomass", Berlin, Germany.
3 | IEA-ETSAP and IRENA, 2015. "Biomass for Heat and Power, Technology Brief".
4 | PLN, 2017, data provided the System Planning Division at PLN
5 | MEMR, 2015, "Waste to Energy Guidebook", Jakarta, Indonesia.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 10-15%.

## Diesel power plant
Technology
| Technology | Diesel engine (using fuel oil)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 20 | 20 | 20 | [5 empty] | 1
| Generating capacity for total power plant (MWe) | 100 | 100 | 100
| Electricity efficiency, net (%), name plate | 46 | 47 | 48 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | 45 | 46 | 47 | 43 | 47 | 45 | 52 |  | 1
| Forced outage (%) | 3 | 3 | 3
| Planned outage (weeks per year) | 0.8 | 1 | 1 | [5 empty] | 2
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 2
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 2
| Space requirement (1000 m2/MWe) | 0.05 | 0.05 | 0.05 | [5 empty] | 2
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 25 | 25 | 25
| Minimum load (% of full load) | 6 | 6 | 6 |  |  |  |  | A | 1
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | [5 empty] | 1
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3
Environment
| PM 2.5 (gram per Nm3) | 19.6 | 19.6 | 19.6 |  |  |  |  | B, C | 3.4
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 |  |  |  |  | C | 3,4
| SO2 (g per GJ fuel) | 224 | 224 | 224 |  |  |  |  | C | 3.4
| NOX (g per GJ fuel) | 280 | 280 | 280 |  |  |  |  | C | 3.4
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 0.8 | 0.8 | 0.776 | 0.7 | 0.9 | 0.65 | 0.85 | D | 6.7
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 8000 | 8000 | 7760 | [5 empty] | 2
| Variable O&M ($/MWh) | 6.4 | 6 | 5.8 | [5 empty] | 2
| Start-up costs ($/MWe/start-up) | - | - | -
References:
1 | Wärtsila, 2011, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants
2 | Danish Energy Agency, 2016, "Technology Data for Energy Plants"
3 | Minister of Environment, Regulation 21/2008
4 | The International Council on Combustion Engines, 2008: Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2
5 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
6 | BWSC once again to deliver highly efficient power plant in the Faroe Islands.
7 | PLN, 2017, data provided the System Planning Division at PLN
Notes:
A | 30 % minimum load per unit - corresponds to 6 % for total plant when consisting of 5 units
B | Total particulate matter
C | Typical diesel exhaut emission according to Ref 3 (average of interval) unless this number exceeds the maximum allowed emission according to Minister of Environment Regulation 21/2008. Both SO2 and particulates are dependant on the fuel composition.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## Batteries
Technology
| Technology | Batteries - Lithium-ion (utility-scale)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Energy storage capacity for one unit (MWh) | 6 | 7 | 8 |  |  |  |  | A,B | 1,2
| Energy/Power ratio (hours) | 1.04 | 2.08 | 4.163 |  |  |  |  | E | 1,2
| Discharge time (hours) | 0.9984 | 1.9968 | 3.9965 |  |  |  |  | E | 1,2
| Round-trip efficiency (%) AC | 91 | 92 | 92 |  |  |  |  | C | 3,12
| Round-trip efficiency (%) DC | 95 | 96 | 96 |  |  |  |  | C | 3,12
| Self-discharge rate (%/day) | 0.1 | 0.1 | 0.1 | [5 empty] | 4
| Forced outage (%) | 0.38 | 0.35 | 0.25 |  |  |  |  | M
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.1 |  |  |  |  | L
| Technical lifetime (cycles) | 10000 | 15000 | 20000 |  |  |  |  | M | 5
| Technical lifetime (years) | 20 | 25 | 30 |  |  |  |  | D
| Construction time (years) | 0.2 | 0.2 | 0.2
| Energy density (Wh/kg) | 150 | 200 | 300
Ramping configurations
| Response time from idle to full-rated discharge (ms) | 50 | 50 | 50 | [5 empty] | 6
Financial data
| Nominal investment (MUSD/MWh) | 0.5785 | 0.26415 | 0.15727 | 0.45502 | 0.92032 | 0.075043 | 0.39799 | G | 13
| - energy component (MUSD/MWh) | 0.152 | 0.062 | 0.035 | 0.079552 | 0.21479 | 0.029548 | 0.13069 |  | 7,8
| - power component (MUSD/MW) | 0.311 | 0.184 | 0.069 | 0.27275 | 0.57959 | 0.045458 | 0.28411 | H | 9,10,11
| - other project costs (MUSD/MWh) | 0.115 | 0.11 | 0.105 | 0.10228 | 0.12501 | 0.022729 | 0.12501 | N | 9,12
| Fixed O&M (USD/MWh/year) | 621 | 310.5 | 155.1381 | 500 | 650 | 250 | 350 |  | 12
| Variable O&M (USD/MWh) | 2.3 | 2.07 | 1.84 | 0.45458 | 6.3642 | 0.34094 | 2.8411 | I | 10
Technology specific data
| Energy storage expansion cost (MUSD/MWh) | 0.267 | 0.163 | 0.086 | 0.18183 | 0.29434 | 0.052277 | 0.20002 | B,F | 7,8
| Output capacity expansion cost (MUSD/MW) | 0.311 | 0.184 | 0.069 | 0.27275 | 0.57959 | 0.045458 | 0.28411 | B,F | 9,10,11
References:
1 | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
2 | Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
3 | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
4 | Fan Xiayue, "Battery technologies for grid-level large-scale electrical energy storage", Transactions of Tianjin University, Springer, 2020.
5 | Environmental end energy study institute, Energy storage factsheet, https://www.eesi.org/papers/view/energy-storage-2019.
6 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127.
7 | Bloomberg New Energy Finance. New Energy Outlook 2019, 2019.
8 | International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
9 | R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17.
10 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596.
11 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015).
12 | Lazard, Lazard's Levelized Cost of Storage (2019).
13 | IEA, World Energy Outlook 2019, 2019.
Notes:
A | One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [2,14]. Units with C-rates below/above 1 are possible, depending on the system needs and cost of the energy and power rating components. A C-rate of 1 is here assumed for 2020, as it is close to several new installations.
B | Power and energy output can be scaled linearly by utilizing many modules (up to 100MW has been demonstrated). Output capacity expansion can be done reprogramming the management unit without any new battery module.
C | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D | Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C. Steady improvement in battery lifetime due to better materials and battery management expected. Number of cycles can be a more meaningful lifetime indicator.
E | The discharge time is the amount of hours the battery can discharge at rated output capacity. It equals the Energy/Power ratio corrected for the discharge efficiency.
F | Since multi-MWh LIB systems are scalar, the energy and outputr capacity expansion costs are here estimated to be equal to the energy and output capacity components plus the “other costs”
G | Power conversion cost is strongly dependent on scalability and application.
H | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
I | Cost per MWh of energy discharged from the battery
L | It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
M | Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
N | Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards.