## Index
INDEX | Technology Data for Energy Transport
111 1 el Main distri50-60kVcabl | Version | 7
111 2 el distri Rural | All cost data is in | 2020 | EURO
111 3 el distri suburban
111 4 el distri city
111 5 el distri new area
111 6 el trans OH-lines
111 7 el trans AC&DC cables | License:
111 8 el substations | This work is licensed under Attribution 4.0 International
111 9 el transformers
111 10 el compensation
Input 111 6 - OH-lines
Input 111 7 - Cables
Input 111 8 - Substations
Input 111 9 - Transformers | Date | Sheet | Change | Notes
Input 111 10 - Compensation | 2025-07-01 | 111 6-10 | Transmission of electricity added - note that 111 1-5 (Distribution of electricity) was not updated. See also additional cost sheet
112 6 gas Main distri line | 2025-02-21 | 113 | Updated sheets for Distict heating
112 7 gas Rural | 2023-08-31 | all sheets | update to 2020 prices
112 8 gas Suburban | 2021-11-01 | 121-123 + co2 terminals | co2 transport removed and transferred to the Technology Catalogue for Carbon Capture, Transport and Storage
112 9 gas City | 2021-03-01 | 131-133 | Transport of gasses and liquids added
112 1 gas New area | 2020-11-02 | 121-123 + co2 terminals | co2 transport added
113_11 DH Transmission
113_12 DH_Distribu Suburb
113_13 DH_Distribu City
113_14 DH_Distribu New area
131_1 H2 140
131_2 H2 70
131_3 NH3
131_4 DME
131_5 TOLU
132 Road transport
133 Ship transport
This file contains the technology data sheets related to industrial process heat. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. Dates and descriptions of updates are listed in the ammendment sheet below.

## alldata_flat
ws | Technology | cat | par | unit | priceyear | note | ref | est | year | val
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2020 | 1
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2050 | 1
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2020 | 5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2050 | 5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2015 | 1.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2020 | 1.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2030 | 1.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2050 | 1.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.15
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2015 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2020 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2030 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2050 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.15
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2015 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2020 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2030 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2050 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.6
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.15
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.5
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2015 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2020 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2030 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2050 | 0.3
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.2
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.1
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.25
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.25
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2015 | 0.2
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2020 | 0.2
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2030 | 0.2
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | ctrl | 2050 | 0.2
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Lower | 2020 | 35
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Lower | 2050 | 40
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Upper | 2020 | 40
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Upper | 2050 | 50
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | ctrl | 2015 | 40
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | ctrl | 2020 | 40
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | ctrl | 2030 | 40
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | ctrl | 2050 | 40
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Lower | 2020 | 0.45
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Lower | 2050 | 0.423
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Upper | 2020 | 0.45
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Upper | 2050 | 0.54
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | ctrl | 2015 | 0.45
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | ctrl | 2020 | 0.45
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | ctrl | 2030 | 0.45
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | ctrl | 2050 | 0.45
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | Lower | 2020 | 26.0952
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | Lower | 2050 | 25.1642
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | Upper | 2020 | 26.5735
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | Upper | 2050 | 26.5735
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | ctrl | 2015 | 24.9898
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | ctrl | 2020 | 26.2015
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | ctrl | 2030 | 27.4719
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | Q | 9 | ctrl | 2050 | 28.8039
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | Lower | 2020 | 6.1061
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | Lower | 2050 | 5.8438
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | Upper | 2020 | 6.7846
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | Upper | 2050 | 7.2145
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | ctrl | 2015 | 6.3802
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | ctrl | 2020 | 6.3802
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | ctrl | 2030 | 6.3802
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [F, G] | [6, 7] | ctrl | 2050 | 6.3802
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | Lower | 2020 | 3.1548
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | Lower | 2050 | 3.0193
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | Upper | 2020 | 3.5054
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | Upper | 2050 | 3.7275
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | ctrl | 2015 | 3.2965
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | ctrl | 2020 | 3.2965
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | ctrl | 2030 | 3.2965
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [I, G] | [6, 7] | ctrl | 2050 | 3.2965
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | Lower | 2020 | 3.969
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | Lower | 2050 | 3.7984
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | Upper | 2020 | 4.41
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | Upper | 2050 | 4.6894
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | ctrl | 2015 | 4.1472
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | ctrl | 2020 | 4.1472
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | ctrl | 2030 | 4.1472
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [H, G] | [6, 7] | ctrl | 2050 | 4.1472
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | Lower | 2020 | 81984.7345
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | Lower | 2050 | 83170.0348
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | Upper | 2020 | 85937.8768
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | Upper | 2050 | 91383.9937
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | ctrl | 2015 | 80816.3266
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | ctrl | 2020 | 80816.3266
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | ctrl | 2030 | 80816.3266
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [L, O] | 8 | ctrl | 2050 | 80816.3266
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | Lower | 2020 | 4828.4694
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | Lower | 2050 | 4898.2773
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | Upper | 2020 | 5061.2886
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | Upper | 2050 | 5382.0363
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | ctrl | 2015 | 4759.6563
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | ctrl | 2020 | 4759.6563
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | ctrl | 2030 | 4759.6563
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [M, O] |  | ctrl | 2050 | 4759.6563
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Lower | 2020 | 0.3737
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Lower | 2050 | 0.32961
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Upper | 2020 | 0.42
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Upper | 2050 | 0.42
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | ctrl | 2015 | 0.42
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | ctrl | 2020 | 0.42
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | ctrl | 2030 | 0.42
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | ctrl | 2050 | 0.42
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Lower | 2020 | 0.58
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Lower | 2050 | 0.58
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Upper | 2020 | 0.6263
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Upper | 2050 | 0.67039
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | ctrl | 2015 | 0.58
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | ctrl | 2020 | 0.58
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | ctrl | 2030 | 0.58
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | ctrl | 2050 | 0.58
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | Lower | 2020 | 17044.1948
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | Lower | 2050 | 17290.6125
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | Upper | 2020 | 17866.0323
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | Upper | 2050 | 18998.2513
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | ctrl | 2015 | 16801.2889
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | ctrl | 2020 | 16801.2889
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | ctrl | 2030 | 16801.2889
111 1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | [K, O] | 6 | ctrl | 2050 | 16801.2889
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.3256
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.4664
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2015 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2030 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2050 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.3256
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.4664
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 1
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 1
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 1
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 1
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 4.5
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 5.25
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2015 | 1.125
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2020 | 1.125
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2030 | 1.125
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2050 | 1.125
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2015 | 40
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2020 | 40
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2030 | 40
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2050 | 40
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.3256
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.4664
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2015 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2020 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2030 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2050 | 0.44
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2020 | 165.5671
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2050 | 140.0698
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2020 | 183.9635
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2050 | 218.9165
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2015 | 183.9635
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2020 | 183.9635
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2030 | 183.9635
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2050 | 183.9635
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2020 | 1699.8106
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2050 | 1639.1681
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2020 | 1730.968
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2050 | 1730.968
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2015 | 1730.968
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2020 | 1706.7345
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2030 | 1682.8402
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2050 | 1659.2804
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 501.4866
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 451.3379
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 557.2073
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 557.2073
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 557.2073
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 557.2073
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 557.2073
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 557.2073
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 1351.3341
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 1216.2006
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 1501.4823
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 1501.4823
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 1501.4823
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 1501.4823
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 1501.4823
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 1501.4823
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 1514.9871
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 1363.4884
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 1683.319
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 1683.319
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 1683.319
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 1683.319
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 1683.319
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 1683.319
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 3584.0977
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 3225.688
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 3982.3308
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 3982.3308
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 3982.3308
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 3982.3308
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 3982.3308
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 3982.3308
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 39.3448
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 35.4103
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 43.5983
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 43.5983
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 43.5983
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 43.5983
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 43.5983
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 43.5983
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 34.0279
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 30.6251
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 34.0279
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 30.6251
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 38.2814
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 90.3867
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 81.348
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 93.5768
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 93.5768
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 93.5768
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 93.5768
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 93.5768
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 93.5768
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2020 | 68619.4415
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2050 | 65600.1861
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2020 | 71777.6585
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2050 | 71777.6585
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2015 | 71777.6585
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2020 | 71777.6585
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2030 | 71777.6585
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2050 | 71777.6585
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2020 | 0.57346
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2050 | 0.52557
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2020 | 0.62
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2050 | 0.62
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2015 | 0.62
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2020 | 0.62
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2030 | 0.62
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2050 | 0.62
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.18858
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.16612
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.22
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.19
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2015 | 0.22
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2020 | 0.22
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2030 | 0.22
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2050 | 0.22
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2020 | 0.38
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2050 | 0.42
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2020 | 0.42654
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2050 | 0.38
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2015 | 0.38
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2020 | 0.38
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2030 | 0.38
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2050 | 0.38
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.78
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.78
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.81
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.81
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2015 | 0.78
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2020 | 0.78
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2030 | 0.78
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2050 | 0.78
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2020 | 11690.7197
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2050 | 11176.328
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2020 | 12228.7863
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2050 | 12228.7863
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2015 | 12228.7863
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2020 | 12228.7863
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2030 | 12228.7863
111 2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2050 | 12228.7863
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.432
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.552
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2015 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2030 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2050 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.432
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.552
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 1
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 1
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 1
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 1
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 2.25
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 3
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2015 | 1.125
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2020 | 1.125
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2030 | 1.125
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2050 | 1.125
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2015 | 40
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2020 | 40
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2030 | 40
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2050 | 40
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.432
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.552
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2015 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2020 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2030 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2050 | 0.48
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2020 | 368.4586
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2050 | 331.6128
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2020 | 409.3985
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2050 | 517.8891
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2015 | 409.3985
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2020 | 409.3985
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2030 | 409.3985
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2050 | 409.3985
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2020 | 2799.9397
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2050 | 2700.0491
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2020 | 2851.2624
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2050 | 2851.2624
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2015 | 2851.2624
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2020 | 2811.3448
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2030 | 2771.9859
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2050 | 2733.1781
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 8676.4834
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 7808.835
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 9640.5371
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 9640.5371
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 9640.5371
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 9640.5371
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 9640.5371
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 9640.5371
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 1374.3029
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 1236.8726
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 1527.0032
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 1527.0032
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 1527.0032
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 1527.0032
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 1527.0032
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 1527.0032
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 3857.8099
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 3472.0289
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 4286.4554
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 4286.4554
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 4286.4554
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 4286.4554
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 4286.4554
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 4286.4554
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 4060.7014
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 3654.6313
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 4511.8904
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 4511.8904
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 4511.8904
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 4511.8904
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 4511.8904
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 4511.8904
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 74.4361
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 66.9925
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 85.0698
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 85.0698
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 85.0698
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 85.0698
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 85.0698
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 85.0698
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 69.1192
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 62.2073
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 79.753
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 79.753
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 79.753
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 79.753
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 79.753
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 79.753
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 125.478
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 112.9302
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 136.1117
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 136.1117
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 136.1117
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 136.1117
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 136.1117
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 136.1117
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2020 | 38630.2041
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2050 | 36930.4751
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2020 | 40408.1633
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2050 | 40408.1633
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2015 | 40408.1633
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2020 | 40408.1633
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2030 | 40408.1633
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2050 | 40408.1633
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2020 | 0.78
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2050 | 0.78
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2020 | 0.8
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2050 | 0.8
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2015 | 0.8
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2020 | 0.8
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2030 | 0.8
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2050 | 0.8
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.13
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.13
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.14
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.14
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2015 | 0.14
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2020 | 0.14
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2030 | 0.14
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2050 | 0.14
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2020 | 0.22
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2050 | 0.22
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2020 | 0.2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2050 | 0.2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2015 | 0.2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2020 | 0.2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2030 | 0.2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2050 | 0.2
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.87
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.87
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.86
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.86
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2015 | 0.86
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2020 | 0.86
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2030 | 0.86
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2050 | 0.86
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2020 | 11690.7197
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2050 | 11176.328
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2020 | 12228.7863
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2050 | 12228.7863
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2015 | 12228.7863
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2020 | 12228.7863
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2030 | 12228.7863
111 3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2050 | 12228.7863
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.45
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.575
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2015 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2030 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2050 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.45
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.575
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 1
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 1
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 1
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 1
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 1.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 2.25
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2015 | 1.125
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2020 | 1.125
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2030 | 1.125
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2050 | 1.125
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2015 | 40
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2020 | 40
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2030 | 40
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2050 | 40
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.45
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.575
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2015 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2020 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2030 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2050 | 0.5
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2020 | 371.4552
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2050 | 334.166
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2020 | 412.728
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2050 | 531.0492
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2015 | 388.131
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2020 | 388.131
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2030 | 388.131
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2050 | 388.131
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2020 | 3383.7895
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2050 | 3263.0694
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2020 | 3445.8142
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2050 | 3445.8142
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2015 | 3240.4576
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2020 | 3397.5728
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2030 | 3562.3058
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2050 | 3735.026
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 12345.5414
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 11815.1207
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 12899.7744
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 12899.7744
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 12899.7744
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 12899.7744
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 12899.7744
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 12899.7744
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 2187.0059
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 2093.0422
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 2285.188
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 2285.188
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 2285.188
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 2285.188
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 2285.188
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 2285.188
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 5717.3565
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 5471.7128
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 5974.0279
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 5974.0279
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 5974.0279
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 5974.0279
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 5974.0279
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 5974.0279
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 5876.1154
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 5623.6507
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 6139.9141
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 6139.9141
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 6139.9141
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 6139.9141
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 6139.9141
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 6139.9141
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 110.5908
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 105.8393
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 127.6047
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 127.6047
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 127.6047
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 127.6047
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 127.6047
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 127.6047
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 106.3373
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 101.7685
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 122.2879
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 122.2879
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 122.2879
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 122.2879
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 122.2879
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 122.2879
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 163.7594
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 156.7235
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 179.71
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 179.71
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 179.71
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 179.71
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 179.71
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 179.71
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2020 | 41078.3051
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2050 | 41759.5608
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2020 | 42968.9384
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2050 | 45691.9968
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2015 | 40408.1633
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2020 | 40408.1633
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2030 | 40408.1633
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2050 | 40408.1633
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2015 | 0.86
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2020 | 0.86
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2030 | 0.86
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2050 | 0.86
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.04
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.04
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.05
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.05
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2015 | 0.05
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2020 | 0.05
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2030 | 0.05
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2050 | 0.05
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2015 | 0.14
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2020 | 0.14
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2030 | 0.14
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2050 | 0.14
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.96
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.96
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.95
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.95
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2015 | 0.95
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2020 | 0.95
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2030 | 0.95
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2050 | 0.95
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2020 | 12431.5923
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2050 | 12637.7618
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2020 | 13003.7577
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2050 | 13003.7577
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2015 | 12228.7863
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2020 | 12228.7863
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2030 | 12228.7863
111 4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2050 | 12228.7863
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.432
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.552
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2015 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2030 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | ctrl | 2050 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.432
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.552
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 1
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 1
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 1
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 1
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 2.25
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 2.25
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 3
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 3
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 3
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 3
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 3
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 3
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2015 | 1.125
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2020 | 1.125
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2030 | 1.125
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | ctrl | 2050 | 1.125
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2015 | 40
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2020 | 40
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2030 | 40
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | ctrl | 2050 | 40
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.432
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.552
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2015 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2020 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2030 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | ctrl | 2050 | 0.48
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2020 | 165.5671
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Lower | 2050 | 140.0698
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2020 | 183.9635
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | Upper | 2050 | 218.9165
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2015 | 183.9635
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2020 | 183.9635
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2030 | 183.9635
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | EUR/MWh/year | 2020 | [E, F] | [1, 6] | ctrl | 2050 | 183.9635
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2020 | 1418.357
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Lower | 2050 | 1367.7557
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2020 | 1444.3554
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | Upper | 2050 | 1444.3554
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2015 | 1444.3554
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2020 | 1424.1344
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2030 | 1404.1965
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | L | 7 | ctrl | 2050 | 1384.5378
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 3584.0977
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 3225.688
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 3982.3308
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 3982.3308
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 3982.3308
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 3982.3308
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 3982.3308
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 3982.3308
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 501.4866
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 451.3379
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 557.2073
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 557.2073
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 557.2073
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 557.2073
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 557.2073
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 557.2073
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 1351.3341
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 1216.2006
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 1501.4823
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 1501.4823
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 1501.4823
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 1501.4823
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 1501.4823
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 1501.4823
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2020 | 1514.9871
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Lower | 2050 | 1363.4884
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2020 | 1683.319
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | Upper | 2050 | 1683.319
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2015 | 1683.319
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2020 | 1683.319
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2030 | 1683.319
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [G, F] | 6 | ctrl | 2050 | 1683.319
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 39.3448
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 35.4103
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 43.5983
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 43.5983
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 43.5983
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 43.5983
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 43.5983
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 43.5983
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 34.0279
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 30.6251
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 34.0279
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 30.6251
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 38.2814
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2020 | 90.3867
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Lower | 2050 | 81.348
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2020 | 93.5768
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | Upper | 2050 | 93.5768
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2015 | 93.5768
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2020 | 93.5768
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2030 | 93.5768
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [H, F] | 6 | ctrl | 2050 | 93.5768
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2020 | 38630.2041
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Lower | 2050 | 36930.4751
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2020 | 40408.1633
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | Upper | 2050 | 40408.1633
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2015 | 40408.1633
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2020 | 40408.1633
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2030 | 40408.1633
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | J | 6 | ctrl | 2050 | 40408.1633
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2020 | 0.78
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2050 | 0.78
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2020 | 0.8
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2050 | 0.8
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2015 | 0.8
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2020 | 0.8
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2030 | 0.8
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | ctrl | 2050 | 0.8
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.13
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.13
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.14
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.14
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2015 | 0.14
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2020 | 0.14
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2030 | 0.14
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | ctrl | 2050 | 0.14
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2020 | 0.22
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2050 | 0.22
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2020 | 0.2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2050 | 0.2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2015 | 0.2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2020 | 0.2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2030 | 0.2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | ctrl | 2050 | 0.2
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.87
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.87
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.86
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.86
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2015 | 0.86
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2020 | 0.86
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2030 | 0.86
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | ctrl | 2050 | 0.86
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2020 | 11690.7197
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Lower | 2050 | 11176.328
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2020 | 12228.7863
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | Upper | 2050 | 12228.7863
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2015 | 12228.7863
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2020 | 12228.7863
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2030 | 12228.7863
111 5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | EUR/MW | 2020 | [I, F, J] | 6 | ctrl | 2050 | 12228.7863
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2025 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2030 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2035 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2040 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2045 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2050 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2025 | 2
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2050 | 2
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2025 | 4
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2050 | 4
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2025 | 5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2030 | 5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2035 | 5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2040 | 5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2045 | 5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2050 | 5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2025 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2050 | 3
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2025 | 7
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2050 | 7
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2025 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2030 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2035 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2040 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2045 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2050 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2025 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2050 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2025 | 2
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2050 | 2
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2025 | 1.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2030 | 1.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2035 | 1.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2040 | 1.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2045 | 1.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2050 | 1.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2025 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2050 | 1
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2025 | 2
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2050 | 2
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | ctrl | 2025 | 0.75
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | ctrl | 2030 | 0.75
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | ctrl | 2035 | 0.72
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | ctrl | 2040 | 0.68
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | ctrl | 2045 | 0.65
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | ctrl | 2050 | 0.62
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | lower | 2025 | 0.58
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | lower | 2050 | 0.48
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | upper | 2025 | 0.98
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,10 | 1 | upper | 2050 | 0.8
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | ctrl | 2025 | 0.6
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | ctrl | 2030 | 0.6
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | ctrl | 2035 | 0.58
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | ctrl | 2040 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | ctrl | 2045 | 0.53
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | ctrl | 2050 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | lower | 2025 | 0.46
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | lower | 2050 | 0.38
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | upper | 2025 | 0.78
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9 | 1 | upper | 2050 | 0.65
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.45
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.45
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.45
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.45
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.45
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.45
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.4
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.4
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.55
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.5
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.6
111 6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.6
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2025 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2030 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2035 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2040 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2045 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2050 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2025 | 2
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2050 | 2
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2025 | 4
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2050 | 4
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2025 | 5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2030 | 5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2035 | 5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2040 | 5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2045 | 5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2050 | 5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | lower | 2025 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | lower | 2050 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | upper | 2025 | 7
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | upper | 2050 | 7
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2025 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2030 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2035 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2040 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2045 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2050 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | lower | 2025 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | lower | 2050 | 1
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | upper | 2025 | 2
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | upper | 2050 | 2
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2025 | 4.51
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2030 | 4.51
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2035 | 4.32
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2040 | 4.13
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2045 | 3.94
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2050 | 3.75
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | lower | 2025 | 3.47
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | lower | 2050 | 2.88
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | upper | 2025 | 5.86
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | upper | 2050 | 4.88
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2025 | 4.51
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2030 | 4.51
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2035 | 4.32
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2040 | 4.13
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2045 | 3.94
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | ctrl | 2050 | 3.75
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | lower | 2025 | 3.47
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | lower | 2050 | 2.88
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | upper | 2025 | 5.86
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,9,11,12 | 1 | upper | 2050 | 4.88
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2025 | 3.22
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2030 | 3.22
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2035 | 3.09
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2040 | 2.95
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2045 | 2.82
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2050 | 2.68
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | lower | 2025 | 2.48
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | lower | 2050 | 2.06
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | upper | 2025 | 4.19
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | upper | 2050 | 3.48
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2025 | 4.07
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2030 | 4.07
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2035 | 3.91
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2040 | 3.74
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2045 | 3.57
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | ctrl | 2050 | 3.4
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | lower | 2025 | 3.13
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | lower | 2050 | 2.62
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | upper | 2025 | 5.29
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2020 | 1,2,3,4,10,11 | 1 | upper | 2050 | 4.42
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2025 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2030 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2035 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2040 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2045 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2050 | 2.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2025 | 2
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2050 | 2
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2025 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2050 | 3
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.45
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.45
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.55
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.55
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.5
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.45
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.45
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.55
111 7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2025 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2030 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2035 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2040 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2045 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2050 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2025 | 1
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2050 | 1
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2025 | 3
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2050 | 3
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2025 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2030 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2035 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2040 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2045 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2050 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | lower | 2025 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | lower | 2050 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | upper | 2025 | 2.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | upper | 2050 | 2.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
111 8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2025 | 0.6
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2030 | 0.6
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2035 | 0.58
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2040 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2045 | 0.53
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2050 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | lower | 2025 | 0.46
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | lower | 2050 | 0.38
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | upper | 2025 | 0.78
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | upper | 2050 | 0.65
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2025 | 0.25
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2030 | 0.25
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2035 | 0.24
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2040 | 0.23
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2045 | 0.22
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | ctrl | 2050 | 0.21
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | lower | 2025 | 0.19
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | lower | 2050 | 0.16
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | upper | 2025 | 0.33
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2020 | 1,2,3,4,5,9 | 1 | upper | 2050 | 0.27
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2025 | 0.75
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2030 | 0.75
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2035 | 0.72
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2040 | 0.69
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2045 | 0.66
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2050 | 0.63
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | lower | 2025 | 0.58
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | lower | 2050 | 0.48
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | upper | 2025 | 0.98
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | upper | 2050 | 0.82
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2025 | 0.32
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2030 | 0.32
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2035 | 0.3
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2040 | 0.29
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2045 | 0.28
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | ctrl | 2050 | 0.27
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | lower | 2025 | 0.25
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | lower | 2050 | 0.21
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | upper | 2025 | 0.42
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2020 | 1,2,3,4,6,10 | 1 | upper | 2050 | 0.35
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2025 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2030 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2035 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2040 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2045 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2050 | 1.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2025 | 1
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2050 | 1
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2025 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2050 | 2
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.45
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.45
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.45
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.45
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.45
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.45
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.4
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.4
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.55
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.5
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.6
111 8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.6
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | est | 2025 | 0.2
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | est | 2030 | 0.2
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | est | 2035 | 0.2
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | est | 2040 | 0.2
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | est | 2045 | 0.2
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | est | 2050 | 0.2
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2025 | 0.1
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2050 | 0.1
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2025 | 0.3
111 9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2050 | 0.3
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | est | 2025 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | est | 2030 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | est | 2035 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | est | 2040 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | est | 2045 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | est | 2050 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | lower | 2025 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | lower | 2050 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | upper | 2025 | 1
111 9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | upper | 2050 | 2
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | est | 2025 | 40
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | est | 2030 | 40
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | est | 2035 | 40
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | est | 2040 | 40
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | est | 2045 | 40
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | est | 2050 | 40
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
111 9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | est | 2025 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | est | 2030 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | est | 2035 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | est | 2040 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | est | 2045 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | est | 2050 | 0.5
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
111 9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2025 | 20.9
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2030 | 20.9
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2035 | 20
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2040 | 19.2
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2045 | 18.3
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2050 | 17.4
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | lower | 2025 | 16.1
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | lower | 2050 | 13.38
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | upper | 2025 | 27.2
111 9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | upper | 2050 | 22.62
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2025 | 20.8
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2030 | 20.8
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2035 | 19.9
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2040 | 19.1
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2045 | 18.2
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2050 | 17.3
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | lower | 2025 | 16
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | lower | 2050 | 13.31
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | upper | 2025 | 27
111 9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | upper | 2050 | 22.49
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2025 | 16
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2030 | 16
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2035 | 15.3
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2040 | 14.7
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2045 | 14
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | est | 2050 | 13.3
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | lower | 2025 | 12.3
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | lower | 2050 | 10.23
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | upper | 2025 | 20.8
111 9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2020 | 1,2,3,4 | 1 | upper | 2050 | 17.29
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | est | 2025 | 1.5
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | est | 2030 | 1.5
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | est | 2035 | 1.5
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | est | 2040 | 1.5
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | est | 2045 | 1.5
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | est | 2050 | 1.5
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | lower | 2025 | 1
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | lower | 2050 | 1
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | upper | 2025 | 2
111 9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &capex/year |  |  | 2 | upper | 2050 | 2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | est | 2025 | 0.2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | est | 2030 | 0.2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | est | 2035 | 0.2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | est | 2040 | 0.2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | est | 2045 | 0.2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | est | 2050 | 0.2
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | lower | 2025 | 0.15
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | lower | 2050 | 0.15
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | upper | 2025 | 0.25
111 9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | upper | 2050 | 0.25
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | est | 2025 | 0.8
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | est | 2030 | 0.8
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | est | 2035 | 0.8
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | est | 2040 | 0.8
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | est | 2045 | 0.8
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | est | 2050 | 0.8
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | lower | 2025 | 0.75
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | lower | 2050 | 0.75
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | upper | 2025 | 0.85
111 9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | upper | 2050 | 0.85
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2025 | 0.2
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2030 | 0.2
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2035 | 0.2
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2040 | 0.2
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2045 | 0.2
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2050 | 0.2
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2025 | 0.1
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2050 | 0.1
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2025 | 0.3
111 10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2050 | 0.3
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
111 10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2025 | 0.5
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2030 | 0.5
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2035 | 0.5
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2040 | 0.5
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2045 | 0.5
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2050 | 0.5
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | lower | 2025 | 0.4
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | lower | 2050 | 0.4
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | upper | 2025 | 0.6
111 10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | upper | 2050 | 0.6
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2025 | 24
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2030 | 24
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2035 | 23
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2040 | 22
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2045 | 21
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2050 | 20
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2025 | 18
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2050 | 15
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2025 | 31
111 10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2050 | 26
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2025 | 1.5
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2030 | 1.5
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2035 | 1.5
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2040 | 1.5
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2045 | 1.5
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | ctrl | 2050 | 1.5
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2025 | 1
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | lower | 2050 | 1
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2025 | 2
111 10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.capex/year |  |  | 2 | upper | 2050 | 2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.2
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.15
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.15
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.25
111 10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.25
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.8
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.8
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.8
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.8
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.8
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.8
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.75
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.75
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.85
111 10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.85
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2025 | 25
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2030 | 25
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2035 | 24
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2040 | 23
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2045 | 22
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2050 | 21
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2025 | 19
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2050 | 16
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2025 | 33
111 10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2050 | 27
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2025 | 155
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2030 | 155
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2035 | 148
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2040 | 142
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2045 | 135
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2050 | 129
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2025 | 119
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2050 | 99
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2025 | 202
111 10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2050 | 168
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2025 | 60
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2030 | 60
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2035 | 58
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2040 | 55
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2045 | 53
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | ctrl | 2050 | 50
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2025 | 46
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | lower | 2050 | 38
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2025 | 78
111 10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2020 | 1,2,3,4 | 1 | upper | 2050 | 65
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Lower | 2020 | 0.00425
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Lower | 2050 | 0.00425
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Upper | 2020 | 0.00575
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Upper | 2050 | 0.00575
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | ctrl | 2015 | 0.005
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | ctrl | 2020 | 0.005
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | ctrl | 2030 | 0.005
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | ctrl | 2050 | 0.005
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Lower | 2020 | 0.7
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Lower | 2050 | 0.7
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Upper | 2020 | 1.5
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Upper | 2050 | 1.5
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2015 | 1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2020 | 1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2030 | 1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | ctrl | 2050 | 1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Lower | 2020 | 0.01
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Lower | 2050 | 0.01
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Upper | 2020 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Upper | 2050 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | ctrl | 2015 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | ctrl | 2020 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | ctrl | 2030 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | ctrl | 2050 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Lower | 2020 | 0.01
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Lower | 2050 | 0.01
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Upper | 2020 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Upper | 2050 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | ctrl | 2015 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | ctrl | 2020 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | ctrl | 2030 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | ctrl | 2050 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Lower | 2020 | 0.01
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Lower | 2050 | 0.01
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Upper | 2020 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Upper | 2050 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | ctrl | 2015 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | ctrl | 2020 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | ctrl | 2030 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | ctrl | 2050 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Lower | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Lower | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Upper | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Upper | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | ctrl | 2015 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | ctrl | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | ctrl | 2030 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | ctrl | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Lower | 2020 | 0
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Lower | 2050 | 0
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Upper | 2020 | 0.12
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Upper | 2050 | 0.12
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | ctrl | 2015 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | ctrl | 2020 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | ctrl | 2030 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | ctrl | 2050 | 0.1
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2015 | 50
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2020 | 50
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2030 | 50
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2050 | 50
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Lower | 2020 | 0.05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Lower | 2050 | 0.05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Upper | 2020 | 0.4
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Upper | 2050 | 0.4
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | ctrl | 2015 | 0.2
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | ctrl | 2020 | 0.2
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | ctrl | 2030 | 0.2
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | ctrl | 2050 | 0.2
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | Lower | 2020 | 0.10292
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | Lower | 2050 | 0.10292
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | Upper | 2020 | 0.15438
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | Upper | 2050 | 0.15438
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | ctrl | 2015 | 0.12865
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | ctrl | 2020 | 0.12865
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | ctrl | 2030 | 0.12865
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 | 0 | 2 | ctrl | 2050 | 0.12865
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | Lower | 2020 | 9.1875
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | Lower | 2050 | 9.1875
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | Upper | 2020 | 13.7813
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | Upper | 2050 | 13.7813
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | ctrl | 2015 | 11.4844
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | ctrl | 2020 | 11.4844
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | ctrl | 2030 | 11.4844
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [E, F] | 2 | ctrl | 2050 | 11.4844
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Lower | 2020 | 1.9056
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Lower | 2050 | 1.9056
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Upper | 2020 | 2.8583
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Upper | 2050 | 2.8583
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2015 | 2.382
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2020 | 2.382
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2030 | 2.382
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2050 | 2.382
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Lower | 2020 | 0.99532
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Lower | 2050 | 0.99532
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Upper | 2020 | 1.493
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Upper | 2050 | 1.493
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2015 | 1.2441
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2020 | 1.2441
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2030 | 1.2441
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2050 | 1.2441
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Lower | 2020 | 3.5729
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Lower | 2050 | 3.5729
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Upper | 2020 | 5.3594
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | Upper | 2050 | 5.3594
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2015 | 4.4662
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2020 | 4.4662
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2030 | 4.4662
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 2 | ctrl | 2050 | 4.4662
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | Lower | 2020 | 0.57847
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | Lower | 2050 | 0.57847
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | Upper | 2020 | 0.86771
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | Upper | 2050 | 0.86771
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | ctrl | 2015 | 0.72309
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | ctrl | 2020 | 0.72309
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | ctrl | 2030 | 0.72309
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [E, G] | 1 | ctrl | 2050 | 0.72309
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | Lower | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | Lower | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | Upper | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | Upper | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | ctrl | 2015 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | ctrl | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | ctrl | 2030 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | EUR/MW/m | 2020 | i |  | ctrl | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | Lower | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | Lower | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | Upper | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | Upper | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | ctrl | 2015 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | ctrl | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | ctrl | 2030 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | EUR/MW | 2020 | [B, J] |  | ctrl | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | Lower | 2020 | 7443.609
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | Lower | 2050 | 0
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | Upper | 2020 | 47851.7723
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | Upper | 2050 | 0
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | ctrl | 2015 | 28711.0634
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | ctrl | 2020 | 28711.0634
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | ctrl | 2030 | 28711.0634
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | EUR/MW | 2020 | [C, K] | 2 | ctrl | 2050 | 28711.0634
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.65
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.65
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.85
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.85
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2015 | 0.75
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2020 | 0.75
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2030 | 0.75
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2050 | 0.75
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.15
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.35
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.35
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2015 | 0.25
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2020 | 0.25
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2030 | 0.25
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2050 | 0.25
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2015 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2020 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2030 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2050 | -
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | Lower | 2020 | 9.5743e-06
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | Lower | 2050 | 9.5743e-06
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | Upper | 2020 | 1.4361e-05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | Upper | 2050 | 1.4361e-05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | ctrl | 2015 | 1.1968e-05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | ctrl | 2020 | 1.1968e-05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | ctrl | 2030 | 1.1968e-05
112 6 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 | 0 | 2 | ctrl | 2050 | 1.1968e-05
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2020 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2050 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2020 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2050 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2015 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2020 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2030 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2050 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2020 | 0.3
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2050 | 0.3
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2020 | 0.5
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2050 | 0.5
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2015 | 0.4
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2020 | 0.4
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2030 | 0.4
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2050 | 0.4
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 0.05
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 0.05
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 0.3
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 0.3
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 0.26307
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 0.26307
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 0.26307
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 0.26307
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2015 | 50
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2020 | 50
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2030 | 50
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2050 | 50
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | Lower | 2020 | 138.2385
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | Lower | 2050 | 138.2385
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | Upper | 2020 | 159.5059
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | Upper | 2050 | 159.5059
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2015 | 148.8722
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2020 | 148.8722
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2030 | 148.8722
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2050 | 148.8722
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Lower | 2020 | 638.0236
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Lower | 2050 | 638.0236
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Upper | 2020 | 957.0354
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Upper | 2050 | 957.0354
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2015 | 797.5295
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2020 | 797.5295
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2030 | 797.5295
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2050 | 797.5295
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Lower | 2020 | 1488.7218
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Lower | 2050 | 1488.7218
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Upper | 2020 | 1914.0709
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Upper | 2050 | 1914.0709
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2015 | 1701.3963
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2020 | 1701.3963
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2030 | 1701.3963
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2050 | 1701.3963
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2020 | 51.0419
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2050 | 51.0419
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2020 | 62.3845
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2050 | 62.3845
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2015 | 56.7132
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2020 | 56.7132
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2030 | 56.7132
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2050 | 56.7132
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2020 | 65.3974
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2050 | 65.3974
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2020 | 79.9302
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2050 | 79.9302
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2015 | 72.6638
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2020 | 72.6638
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2030 | 72.6638
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2050 | 72.6638
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 47.8518
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 58.4855
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 53.1686
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.7
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.7
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.9
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.9
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2015 | 0.8
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2020 | 0.8
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2030 | 0.8
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2050 | 0.8
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.1
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.1
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.3
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.3
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2015 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2020 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2030 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2050 | 0.2
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2015 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2020 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2030 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2050 | -
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Lower | 2020 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Lower | 2050 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Upper | 2020 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Upper | 2050 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2015 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2020 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2030 | 0
112 7 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2050 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2020 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2050 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2020 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2050 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2015 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2020 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2030 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2050 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2020 | 0.3
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2050 | 0.3
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2020 | 0.5
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2050 | 0.5
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2015 | 0.4
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2020 | 0.4
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2030 | 0.4
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2050 | 0.4
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 0.05
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 0.05
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 0.3
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 0.3
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 0.26307
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 0.26307
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 0.26307
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 0.26307
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2015 | 50
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2020 | 50
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2030 | 50
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2050 | 50
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | Lower | 2020 | 148.8722
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | Lower | 2050 | 148.8722
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | Upper | 2020 | 180.7734
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | Upper | 2050 | 180.7734
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2015 | 159.5059
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2020 | 159.5059
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2030 | 159.5059
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2050 | 159.5059
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Lower | 2020 | 265.8432
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Lower | 2050 | 265.8432
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Upper | 2020 | 393.4479
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Upper | 2050 | 393.4479
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2015 | 329.6455
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2020 | 329.6455
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2030 | 329.6455
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2050 | 329.6455
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Lower | 2020 | 1488.7218
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Lower | 2050 | 1488.7218
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Upper | 2020 | 1914.0709
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Upper | 2050 | 1914.0709
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2015 | 1701.3963
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2020 | 1701.3963
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2030 | 1701.3963
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2050 | 1701.3963
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2020 | 57.4221
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2050 | 57.4221
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2020 | 70.1826
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2050 | 70.1826
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2015 | 63.8024
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2020 | 63.8024
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2030 | 63.8024
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2050 | 63.8024
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2020 | 82.9431
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2050 | 82.9431
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2020 | 101.3749
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2050 | 101.3749
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2015 | 92.159
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2020 | 92.159
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2030 | 92.159
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2050 | 92.159
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 51.0419
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 62.3845
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 56.7132
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.7
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.7
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.9
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.9
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2015 | 0.8
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2020 | 0.8
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2030 | 0.8
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2050 | 0.8
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.1
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.1
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.3
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.3
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2015 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2020 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2030 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2050 | 0.2
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2015 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2020 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2030 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2050 | -
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Lower | 2020 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Lower | 2050 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Upper | 2020 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Upper | 2050 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2015 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2020 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2030 | 0
112 8 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2050 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Lower | 2020 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Lower | 2050 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Upper | 2020 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Upper | 2050 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | ctrl | 2015 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | ctrl | 2020 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | ctrl | 2030 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | ctrl | 2050 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2020 | 0.3
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2050 | 0.3
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2020 | 0.5
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2050 | 0.5
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 0.4
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 0.4
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 0.4
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 0.4
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Lower | 2020 | 50
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Lower | 2050 | 50
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Upper | 2020 | 80
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Upper | 2050 | 80
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2015 | 50
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2020 | 50
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2030 | 50
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2050 | 50
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | Lower | 2020 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | Lower | 2050 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | Upper | 2020 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | Upper | 2050 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | ctrl | 2015 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | ctrl | 2020 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | ctrl | 2030 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 1 | ctrl | 2050 | 10.6337
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | Lower | 2020 | 17.014
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | Lower | 2050 | 17.014
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | Upper | 2020 | 25.5209
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | Upper | 2050 | 25.5209
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | ctrl | 2015 | 21.2675
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | ctrl | 2020 | 21.2675
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | ctrl | 2030 | 21.2675
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 1 | ctrl | 2050 | 21.2675
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | 0 |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | Lower | 2020 | 12760.4726
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | Lower | 2050 | 12760.4726
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | Upper | 2020 | 19140.7089
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | Upper | 2050 | 19140.7089
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | ctrl | 2015 | 15950.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | ctrl | 2020 | 15950.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | ctrl | 2030 | 15950.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E | 1 | ctrl | 2050 | 15950.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2020 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2050 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2020 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2050 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2015 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2020 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2030 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2050 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2020 | 68.9066
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2050 | 68.9066
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2020 | 84.2191
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2050 | 84.2191
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2015 | 76.5628
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2020 | 76.5628
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2030 | 76.5628
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2050 | 76.5628
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2020 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2050 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2020 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2050 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2015 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2020 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2030 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2050 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2020 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2050 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2020 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2050 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2015 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2020 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2030 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2050 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2020 | 99.5317
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2050 | 99.5317
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2020 | 121.6498
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2050 | 121.6498
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2015 | 110.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2020 | 110.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2030 | 110.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2050 | 110.5908
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2020 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Lower | 2050 | 61.2503
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2020 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | Upper | 2050 | 74.8614
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2015 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2020 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2030 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | 0 | 1 | ctrl | 2050 | 68.0559
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Lower | 2020 | 0.7
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Lower | 2050 | 0.7
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Upper | 2020 | 0.9
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Upper | 2050 | 0.9
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | ctrl | 2015 | 0.8
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | ctrl | 2020 | 0.8
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | ctrl | 2030 | 0.8
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | ctrl | 2050 | 0.8
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Lower | 2020 | 0.1
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Lower | 2050 | 0.1
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Upper | 2020 | 0.3
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Upper | 2050 | 0.3
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | ctrl | 2015 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | ctrl | 2020 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | ctrl | 2030 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | ctrl | 2050 | 0.2
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | Lower | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | Lower | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | Upper | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | Upper | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2015 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2020 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2030 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | F |  | ctrl | 2050 | -
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | Lower | 2020 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | Lower | 2050 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | Upper | 2020 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | Upper | 2050 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | ctrl | 2015 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | ctrl | 2020 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | ctrl | 2030 | 0
112 9 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 1 | ctrl | 2050 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2015 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2020 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2030 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | ctrl | 2050 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2020 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2050 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2020 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2050 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2015 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2020 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2030 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | ctrl | 2050 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2020 | 0.3
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2050 | 0.3
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2020 | 0.5
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2050 | 0.5
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2015 | 0.4
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2020 | 0.4
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2030 | 0.4
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2050 | 0.4
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 0.05
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 0.05
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 0.3
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 0.3
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2015 | 0.26307
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2020 | 0.26307
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2030 | 0.26307
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | ctrl | 2050 | 0.26307
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2015 | 50
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2020 | 50
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2030 | 50
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | ctrl | 2050 | 50
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | Lower | 2020 | 255.2095
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | Lower | 2050 | 255.2095
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | Upper | 2020 | 319.0118
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | Upper | 2050 | 319.0118
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2015 | 287.1106
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2020 | 287.1106
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2030 | 287.1106
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | EUR/MWh/year | 2020 | 0 | 2 | ctrl | 2050 | 287.1106
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Lower | 2020 | 786.8958
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Lower | 2050 | 786.8958
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Upper | 2020 | 1169.71
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | Upper | 2050 | 1169.71
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2015 | 978.3029
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2020 | 978.3029
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2030 | 978.3029
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | 2 | ctrl | 2050 | 978.3029
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Lower | 2020 | 1488.7218
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Lower | 2050 | 1488.7218
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Upper | 2020 | 1914.0709
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | Upper | 2050 | 1914.0709
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2015 | 1701.3963
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2020 | 1701.3963
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2030 | 1701.3963
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | 0 | 2 | ctrl | 2050 | 1701.3963
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | E |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2020 | 47.8518
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2050 | 47.8518
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2020 | 58.4855
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2050 | 58.4855
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2015 | 53.1686
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2020 | 53.1686
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2030 | 53.1686
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2050 | 53.1686
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | 0 |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2020 | 60.6122
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Lower | 2050 | 60.6122
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2020 | 74.0816
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | Upper | 2050 | 74.0816
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2015 | 67.3469
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2020 | 67.3469
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2030 | 67.3469
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | G |  | ctrl | 2050 | 67.3469
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2020 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Lower | 2050 | 44.6617
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2020 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | Upper | 2050 | 54.5865
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2015 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2020 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2030 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | F |  | ctrl | 2050 | 49.6241
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.7
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.7
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.9
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.9
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2015 | 0.8
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2020 | 0.8
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2030 | 0.8
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | ctrl | 2050 | 0.8
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.1
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.1
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.3
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.3
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2015 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2020 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2030 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | ctrl | 2050 | 0.2
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | EUR/MW | 2020 | H |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Lower | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | Upper | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2015 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2020 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2030 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | EUR/MW | 2020 | I |  | ctrl | 2050 | -
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Lower | 2020 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Lower | 2050 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Upper | 2020 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | Upper | 2050 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2015 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2020 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2030 | 0
112 1 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | 2 | ctrl | 2050 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Lower | 2025 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Lower | 2050 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Upper | 2025 | 2
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Upper | 2050 | 2
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | ctrl | 2020 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | ctrl | 2025 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | ctrl | 2030 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | ctrl | 2035 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | ctrl | 2040 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | ctrl | 2050 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2025 | 1.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2050 | 1.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2025 | 4
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2050 | 4
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 2.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 2.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 2.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Lower | 2025 | 0.8
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Lower | 2050 | 0.8
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Upper | 2025 | 1.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Upper | 2050 | 1.2
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | ctrl | 2020 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | ctrl | 2025 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | ctrl | 2030 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | ctrl | 2035 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | ctrl | 2040 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | ctrl | 2050 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Lower | 2025 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Lower | 2050 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Upper | 2025 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Upper | 2050 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | ctrl | 2020 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | ctrl | 2025 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | ctrl | 2030 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | ctrl | 2035 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | ctrl | 2040 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | ctrl | 2050 | 0
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2025 | 0.8
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2050 | 0.8
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2025 | 1.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2050 | 1.2
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2020 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2025 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2030 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2035 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2040 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2050 | 1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2025 | 0.2
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2050 | 0.2
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2025 | 0.375
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2050 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2020 | 0.25
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2025 | 0.25
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2030 | 0.25
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2035 | 0.25
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2040 | 0.25
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2050 | 0.25
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2025 | 0.08
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2050 | 0.08
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2025 | 0.15
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2050 | 0.12
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2020 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2025 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2030 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2035 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2040 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | ctrl | 2050 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Lower | 2025 | 30
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Lower | 2050 | 30
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Upper | 2025 | 60
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Upper | 2050 | 60
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | ctrl | 2020 | 45
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | ctrl | 2025 | 45
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | ctrl | 2030 | 45
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | ctrl | 2035 | 45
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | ctrl | 2040 | 45
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | ctrl | 2050 | 45
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Lower | 2025 | 0.4
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Lower | 2050 | 0.4
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Upper | 2025 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Upper | 2050 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | ctrl | 2020 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | ctrl | 2025 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | ctrl | 2030 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | ctrl | 2035 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | ctrl | 2040 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | ctrl | 2050 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | Lower | 2025 | 50
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | Lower | 2050 | 50
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | Upper | 2025 | 200
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | Upper | 2050 | 200
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | ctrl | 2020 | 100
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | ctrl | 2025 | 100
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | ctrl | 2030 | 100
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | ctrl | 2035 | 100
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | ctrl | 2040 | 100
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | EUR/MW/km/year | 2020 |  |  | ctrl | 2050 | 100
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2025 | 50.7489
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2050 | 50.7489
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2025 | 75.0024
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2050 | 75.0024
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2020 | 55.9207
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2025 | 63.1948
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2030 | 63.1948
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2035 | 63.1948
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2040 | 63.1948
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2050 | 63.1948
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2025 | 15.8655
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2050 | 15.8655
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2025 | 23.4058
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2050 | 23.4058
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2020 | 17.477
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2025 | 19.7504
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2030 | 19.7504
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2035 | 19.7504
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2040 | 19.7504
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2050 | 19.7504
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2025 | 9.5484
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2050 | 9.5484
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2025 | 14.0843
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2050 | 14.0843
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2020 | 10.5204
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2025 | 11.8888
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2030 | 11.8888
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2035 | 11.8888
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2040 | 11.8888
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2050 | 11.8888
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2025 | 25.4138
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Lower | 2050 | 25.4138
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2025 | 37.4085
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | Upper | 2050 | 37.4085
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2020 | 27.9431
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2025 | 31.5779
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2030 | 31.5779
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2035 | 31.5779
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2040 | 31.5779
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [C, D] | [1, 3] | ctrl | 2050 | 31.5779
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Lower | 2025 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Lower | 2050 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Upper | 2025 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Upper | 2050 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | ctrl | 2020 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | ctrl | 2025 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | ctrl | 2030 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | ctrl | 2035 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | ctrl | 2040 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | ctrl | 2050 | 0.1
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Lower | 2025 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Lower | 2050 | 0.5
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Upper | 2025 | 0.7
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Upper | 2050 | 0.7
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | ctrl | 2020 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | ctrl | 2025 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | ctrl | 2030 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | ctrl | 2035 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | ctrl | 2040 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | ctrl | 2050 | 0.6
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Lower | 2025 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Lower | 2050 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Upper | 2025 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Upper | 2050 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | ctrl | 2020 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | ctrl | 2025 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | ctrl | 2030 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | ctrl | 2035 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | ctrl | 2040 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | ctrl | 2050 | 0.3
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | Lower | 2025 | 0.038487
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | Lower | 2050 | 0.038487
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | Upper | 2025 | 1.7494
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | Upper | 2050 | 1.7494
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | ctrl | 2020 | 0.10634
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | ctrl | 2025 | 0.11663
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | ctrl | 2030 | 0.11663
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | ctrl | 2035 | 0.11663
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | ctrl | 2040 | 0.11663
113_11 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | EUR/MWh/km | 2020 |  | [1, 4] | ctrl | 2050 | 0.11663
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | Lower | 2025 | 77089.0006
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | Lower | 2050 | 77089.0006
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | Upper | 2025 | 168194.1831
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | Upper | 2050 | 168194.1831
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2020 | 122287.8884
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2025 | 140161.8193
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2030 | 140161.8193
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2035 | 140161.8193
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2040 | 140161.8193
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2050 | 140161.8193
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | Lower | 2025 | 70110.2592
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | Lower | 2050 | 70110.2592
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | Upper | 2025 | 152967.8384
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | Upper | 2050 | 152967.8384
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2020 | 111654.0923
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2025 | 127473.1986
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2030 | 127473.1986
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2035 | 127473.1986
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2040 | 127473.1986
113_11 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | EUR/MW | 2020 |  | 1 | ctrl | 2050 | 127473.1986
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Lower | 2025 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Lower | 2050 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Upper | 2025 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Upper | 2050 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2020 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2025 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2030 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2035 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2040 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2050 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Lower | 2025 | 0.18
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Lower | 2050 | 0.18
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Upper | 2025 | 0.22
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Upper | 2050 | 0.22
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | ctrl | 2020 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | ctrl | 2025 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | ctrl | 2030 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | ctrl | 2035 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | ctrl | 2040 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | ctrl | 2050 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2025 | 0.5
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2050 | 0.5
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2025 | 3
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2050 | 3
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2020 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2025 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2030 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2035 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2040 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2050 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2025 | 1
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 1
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2025 | 3
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 3
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2025 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2035 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2025 | 10
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2050 | 9
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2025 | 16
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2050 | 14
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2020 | 12.4
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2025 | 12.4
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2030 | 12.4
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2035 | 12.4
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2040 | 12.4
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2050 | 12.4
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2025 | 30
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2050 | 30
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2025 | 60
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2050 | 60
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2020 | 45
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2025 | 45
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2030 | 45
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2035 | 45
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2040 | 45
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2050 | 45
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Lower | 2025 | 750
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Lower | 2050 | 750
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Upper | 2025 | 2000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Upper | 2050 | 2000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2020 | 1000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2025 | 1000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2030 | 1000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2035 | 1000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2040 | 1000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2050 | 1000
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Lower | 2025 | 0.1
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Lower | 2050 | 0.1
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Upper | 2025 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Upper | 2050 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | ctrl | 2020 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | ctrl | 2025 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | ctrl | 2030 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | ctrl | 2035 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | ctrl | 2040 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | ctrl | 2050 | 0.15
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Lower | 2025 | 5.4797
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Lower | 2050 | 5.4797
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Upper | 2025 | 9.0684
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Upper | 2050 | 9.0684
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2020 | 6.4626
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2025 | 7.3032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2030 | 7.3032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2035 | 7.3032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2040 | 7.3032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2050 | 7.3032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2025 | 0.5
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2050 | 0.5
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2025 | 0.7
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2050 | 0.7
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2020 | 0.6
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2025 | 0.6
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2030 | 0.6
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2035 | 0.6
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2040 | 0.6
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2050 | 0.6
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2025 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2050 | 0.2
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2025 | 0.3
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2050 | 0.3
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2020 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2025 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2030 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2035 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2040 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2050 | 0.25
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Lower | 2025 | 1.508
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Lower | 2050 | 1.508
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Upper | 2025 | 3.0161
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Upper | 2050 | 3.0161
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2020 | 2.0107
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2025 | 2.0107
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2030 | 2.0107
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2035 | 2.0107
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2040 | 2.0107
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2050 | 2.0107
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 3242.5827
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 3242.5827
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 6192.4458
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 6192.4458
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 4164.6016
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 4706.3255
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 4706.3255
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 4706.3255
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 4706.3255
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 4706.3255
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 3547.7252
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 3547.7252
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 6678.7487
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 6678.7487
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 4518.7972
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 5106.5942
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 5106.5942
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 5106.5942
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 5106.5942
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 5106.5942
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 3953.0763
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 3953.0763
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 7309.6865
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 7309.6865
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 4987.2013
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 5635.9275
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 5635.9275
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 5635.9275
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 5635.9275
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 5635.9275
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 241.1895
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 241.1895
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 455.9609
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 455.9609
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 308.4523
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 348.5752
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 348.5752
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 348.5752
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 348.5752
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 348.5752
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 646.1684
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 646.1684
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 971.0722
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 971.0722
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 724.6157
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 818.8724
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 818.8724
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 818.8724
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 818.8724
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 818.8724
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 342.0119
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 342.0119
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 576.9283
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 576.9283
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 406.5826
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 459.4701
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 459.4701
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 459.4701
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 459.4701
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 459.4701
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 456.5441
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 456.5441
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 700.0145
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 700.0145
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 515.5657
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 582.6296
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 582.6296
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 582.6296
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 582.6296
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 582.6296
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 1184.4561
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 1184.4561
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 1752.5903
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 1752.5903
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 1308.5602
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 1478.7753
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 1478.7753
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 1478.7753
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 1478.7753
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 1478.7753
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 327.206
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 327.206
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 554.0552
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 554.0552
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 389.9116
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 440.6306
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 440.6306
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 440.6306
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 440.6306
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 440.6306
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2025 | 61998.7032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2050 | 61998.7032
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2025 | 135269.898
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2050 | 135269.898
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2020 | 98736.0339
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2025 | 112724.915
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2030 | 112724.915
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2035 | 112724.915
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2040 | 112724.915
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2050 | 112724.915
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2025 | 160252.0945
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2050 | 160252.0945
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2025 | 349640.9333
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2050 | 349640.9333
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2020 | 255209.4707
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2025 | 291367.4445
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2030 | 263879.9497
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2035 | 263879.9497
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2040 | 263879.9497
113_12 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2050 | 263879.9497
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Lower | 2025 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Lower | 2050 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Upper | 2025 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Upper | 2050 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2020 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2025 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2030 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2035 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2040 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2050 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Lower | 2025 | 0.18
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Lower | 2050 | 0.18
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Upper | 2025 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Upper | 2050 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | ctrl | 2020 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | ctrl | 2025 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | ctrl | 2030 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | ctrl | 2035 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | ctrl | 2040 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | ctrl | 2050 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2025 | 0.5
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2050 | 0.5
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2025 | 3
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2050 | 3
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2020 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2025 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2030 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2035 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2040 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2050 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2025 | 1
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 1
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2025 | 3
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 3
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2025 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2035 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2025 | 5
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2050 | 4
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2025 | 9
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2050 | 8
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2020 | 7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2025 | 7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2030 | 7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2035 | 7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2040 | 7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2050 | 7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2025 | 30
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2050 | 30
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2025 | 60
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2050 | 60
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2020 | 45
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2025 | 45
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2030 | 45
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2035 | 45
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2040 | 45
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2050 | 45
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Lower | 2025 | 750
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Lower | 2050 | 750
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Upper | 2025 | 2000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Upper | 2050 | 2000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2020 | 1000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2025 | 1000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2030 | 1000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2035 | 1000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2040 | 1000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2050 | 1000
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2025 | 0.1
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2050 | 0.1
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2025 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2050 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2020 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2025 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2030 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2035 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2040 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2050 | 0.15
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Lower | 2025 | 5.0474
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Lower | 2050 | 5.0474
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Upper | 2025 | 8.3655
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Upper | 2050 | 8.3655
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2020 | 5.968
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2025 | 6.7443
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2030 | 6.7443
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2035 | 6.7443
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2040 | 6.7443
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2050 | 6.7443
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2025 | 0.5
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2050 | 0.5
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2025 | 0.7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2050 | 0.7
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2020 | 0.6
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2025 | 0.6
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2030 | 0.6
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2035 | 0.6
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2040 | 0.6
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2050 | 0.6
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2025 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2050 | 0.2
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2025 | 0.3
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2050 | 0.3
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2020 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2025 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2030 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2035 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2040 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2050 | 0.25
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Lower | 2025 | 1.508
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Lower | 2050 | 1.508
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Upper | 2025 | 3.0161
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Upper | 2050 | 3.0161
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2020 | 2.0107
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2025 | 2.0107
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2030 | 2.0107
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2035 | 2.0107
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2040 | 2.0107
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2050 | 2.0107
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 3804.7675
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 3804.7675
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 7431.9167
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 7431.9167
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 4961.2182
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 5606.5644
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 5606.5644
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 5606.5644
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 5606.5644
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 5606.5644
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 4135.3976
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 4135.3976
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 7883.1671
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 7883.1671
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 5333.929
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 6027.7568
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 6027.7568
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 6027.7568
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 6027.7568
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 6027.7568
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 4627.3368
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 4627.3368
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 8482.0584
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 8482.0584
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 5826.9859
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 6584.9497
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 6584.9497
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 6584.9497
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 6584.9497
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 6584.9497
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | Lower | 2025 | 6264.0232
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | Lower | 2050 | 6264.0232
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | Upper | 2025 | 9918.3185
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | Upper | 2050 | 9918.3185
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | ctrl | 2020 | 7159.8328
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | ctrl | 2025 | 8091.1709
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | ctrl | 2030 | 8091.1709
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | ctrl | 2035 | 8091.1709
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | ctrl | 2040 | 8091.1709
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J, K] | [1, 3] | ctrl | 2050 | 8091.1709
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 262.3075
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 262.3075
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 506.8973
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 506.8973
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 338.688
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 382.7439
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 382.7439
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 382.7439
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 382.7439
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 382.7439
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 691.7201
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 691.7201
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 1035.2719
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 1035.2719
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 773.1749
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 873.7481
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 873.7481
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 873.7481
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 873.7481
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 873.7481
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 372.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 372.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 624.7824
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 624.7824
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 441.2294
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 498.6238
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 498.6238
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 498.6238
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 498.6238
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 498.6238
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | Lower | 2025 | 2305.633
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | Lower | 2050 | 2305.633
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | Upper | 2025 | 3393.1957
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | Upper | 2050 | 3393.1957
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | ctrl | 2020 | 2532.9797
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | ctrl | 2025 | 2862.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | ctrl | 2030 | 2862.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | ctrl | 2035 | 2862.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | ctrl | 2040 | 2862.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | EUR/m | 2020 | [B, E, G, L] | [1, 3] | ctrl | 2050 | 2862.4651
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 488.4229
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 488.4229
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 749.2944
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 749.2944
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 551.4741
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 623.2089
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 623.2089
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 623.2089
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 623.2089
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 623.2089
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 1258.996
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 1258.996
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 1863.1035
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 1863.1035
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 1390.4364
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 1571.3019
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 1571.3019
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 1571.3019
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 1571.3019
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 1571.3019
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 303.189
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 303.189
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 559.8538
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 559.8538
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 380.2063
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 429.6629
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 429.6629
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 429.6629
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 429.6629
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 429.6629
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2025 | 61998.7032
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2050 | 61998.7032
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2025 | 135269.898
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2050 | 143842.3191
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2020 | 98736.0339
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2025 | 112724.915
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2030 | 112724.915
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2035 | 112724.915
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2040 | 112724.915
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2050 | 112724.915
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2025 | 160252.0945
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2050 | 160252.0945
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2025 | 349640.9333
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2050 | 349640.9333
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2020 | 255209.4707
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2025 | 291367.4445
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2030 | 291367.4445
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2035 | 291367.4445
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2040 | 291367.4445
113_13 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2050 | 291367.4445
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Lower | 2025 | 0.1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Lower | 2050 | 0.1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Upper | 2025 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Upper | 2050 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2020 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2025 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2030 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2035 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2040 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | ctrl | 2050 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Lower | 2025 | 0.1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Lower | 2050 | 0.1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Upper | 2025 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Upper | 2050 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | ctrl | 2020 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | ctrl | 2025 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | ctrl | 2030 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | ctrl | 2035 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | ctrl | 2040 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | ctrl | 2050 | 0.17
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2025 | 0.5
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2050 | 0.5
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2025 | 3
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2050 | 3
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2020 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2025 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2030 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2035 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2040 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | ctrl | 2050 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2025 | 0.5
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2025 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2025 | 1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2035 | 1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2025 | 12
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2050 | 10
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2025 | 24
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2050 | 20
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2020 | 18
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2025 | 18
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2030 | 18
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2035 | 18
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2040 | 18
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | ctrl | 2050 | 18
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2025 | 30
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2050 | 30
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2025 | 60
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2050 | 60
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2020 | 45
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2025 | 45
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2030 | 45
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2035 | 45
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2040 | 45
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | ctrl | 2050 | 45
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Lower | 2025 | 750
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Lower | 2050 | 750
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Upper | 2025 | 2000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | Upper | 2050 | 2000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2020 | 1000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2025 | 1000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2030 | 1000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2035 | 1000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2040 | 1000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | M | 1 | ctrl | 2050 | 1000
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2025 | 0.1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2050 | 0.1
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2025 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2050 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2020 | 0.15
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2025 | 0.15
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2030 | 0.15
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2035 | 0.15
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2040 | 0.15
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | ctrl | 2050 | 0.15
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Lower | 2025 | 3.9965
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Lower | 2050 | 3.9965
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Upper | 2025 | 6.6191
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | Upper | 2050 | 6.6191
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2020 | 4.7197
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2025 | 5.3336
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2030 | 5.3336
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2035 | 5.3336
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2040 | 5.3336
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | MEUR/km2 | 2020 | [D, E] | [1, 3] | ctrl | 2050 | 5.3336
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2025 | 0.5
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2050 | 0.5
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2025 | 0.7
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2050 | 0.7
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2020 | 0.6
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2025 | 0.6
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2030 | 0.6
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2035 | 0.6
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2040 | 0.6
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | ctrl | 2050 | 0.6
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2025 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2050 | 0.2
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2025 | 0.3
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2050 | 0.3
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2020 | 0.25
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2025 | 0.25
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2030 | 0.25
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2035 | 0.25
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2040 | 0.25
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | ctrl | 2050 | 0.25
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Lower | 2025 | 1.3121
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Lower | 2050 | 1.3121
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Upper | 2025 | 2.6241
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | Upper | 2050 | 2.6241
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2020 | 1.5951
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2025 | 1.7494
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2030 | 1.7494
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2035 | 1.7494
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2040 | 1.7494
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | M | [1, 4] | ctrl | 2050 | 1.7494
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 2706.7547
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 2706.7547
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 5231.3553
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 5231.3553
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 3504.3785
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 3960.2217
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 3960.2217
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 3960.2217
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 3960.2217
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 3960.2217
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 2951.1919
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 2951.1919
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 5592.5358
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 5592.5358
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 3783.9591
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 4276.1697
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 4276.1697
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 4276.1697
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 4276.1697
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 4276.1697
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2025 | 3295.6762
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Lower | 2050 | 3295.6762
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2025 | 6066.1745
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | Upper | 2050 | 6066.1745
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2020 | 4153.7518
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2025 | 4694.0644
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2030 | 4694.0644
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2035 | 4694.0644
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2040 | 4694.0644
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | EUR/unit | 2020 | [B, E, F, J] | [1, 3] | ctrl | 2050 | 4694.0644
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 188.8114
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 188.8114
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 361.0718
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 361.0718
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 242.6776
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 274.2447
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 274.2447
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 274.2447
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 274.2447
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 274.2447
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 501.7082
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 501.7082
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 752.3791
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 752.3791
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 561.6715
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 634.7327
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 634.7327
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 634.7327
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 634.7327
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 634.7327
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 267.9289
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 267.9289
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 450.6415
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 450.6415
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 317.9295
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 359.2852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 359.2852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 359.2852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 359.2852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 359.2852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 354.3626
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 354.3626
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 543.4908
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 543.4908
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 400.1399
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 452.1894
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 452.1894
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 452.1894
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 452.1894
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 452.1894
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 916.2945
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 916.2945
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 1355.8852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 1355.8852
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 1012.1237
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 1143.779
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 1143.779
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 1143.779
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 1143.779
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 1143.779
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2025 | 253.3243
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Lower | 2050 | 253.3243
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2025 | 431.3804
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | Upper | 2050 | 431.3804
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2020 | 302.329
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2025 | 341.6554
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2030 | 341.6554
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2035 | 341.6554
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2040 | 341.6554
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | EUR/m | 2020 | [B, E, G] | [1, 3] | ctrl | 2050 | 341.6554
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2025 | 59307.9389
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2050 | 59307.9389
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2025 | 127088.4405
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2050 | 127088.4405
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2020 | 92764.2348
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2025 | 105907.0338
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2030 | 105907.0338
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2035 | 105907.0338
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2040 | 105907.0338
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2050 | 105907.0338
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2025 | 158154.4384
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Lower | 2050 | 158154.4384
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2025 | 338902.3681
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | Upper | 2050 | 338902.3681
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2020 | 247371.1906
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2025 | 282418.6401
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2030 | 282418.6401
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2035 | 282418.6401
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2040 | 282418.6401
113_14 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | EUR/MW | 2020 | I | 1 | ctrl | 2050 | 282418.6401
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2020 | 0.5
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2020 | 2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Lower | 2020 | 0.74826
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Lower | 2050 | 0.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Upper | 2020 | 3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Upper | 2050 | 2.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | ctrl | 2020 | 0.93532
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | ctrl | 2030 | 0.84179
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | ctrl | 2050 | 0.74826
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 8.2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 7.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 16.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 13.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 10
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 9.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 8.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 6.7
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 13.4
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 11.2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 8.2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 7.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 6.8
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 2.4
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 2.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 4.8
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 4
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 2.9
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 2.7
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 2.4
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 5.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 4.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 10.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 8.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 6.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 5.8
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 5.2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 3.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 3.2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 7.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 6.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 4.5
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 4.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 3.7
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 1.8
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 1.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 3.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 2.2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 2
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 1.8
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 1.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 1.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 2.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 2.1
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 1.6
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 1.5
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 1.3
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2020 | 45
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2050 | 45
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2020 | 55
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2050 | 55
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2020 | 50
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2030 | 50
H2 70 | Main distribution line-H2-70 bar | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2050 | 50
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Lower | 2020 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Lower | 2050 | 0.11697
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Upper | 2020 | 1.0634
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Upper | 2050 | 1.0634
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | ctrl | 2020 | 0.54232
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | ctrl | 2030 | 0.26584
H2 70 | Main distribution line-H2-70 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | ctrl | 2050 | 0.19938
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 3.6155
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 3.2965
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 5.1042
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 4.6788
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 4.0408
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 3.8281
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 3.6155
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 1.5951
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 1.4887
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 2.2331
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 2.0204
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 1.8077
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 1.7014
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 1.5951
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 0.42535
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.42535
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 0.53169
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 0.42535
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 0.42535
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 0.42535
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 0.42535
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 1.0634
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.95704
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 1.3824
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 1.276
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 1.0634
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 1.0634
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 1.0634
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 0.74436
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.63802
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 0.95704
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 0.8507
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 0.74436
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 0.74436
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 0.74436
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 0.23394
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 0.21267
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2020 | 0.75
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2050 | 0.7
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2020 | 0.8
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2050 | 0.8
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2020 | 0.775
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2030 | 0.775
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2050 | 0.775
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Lower | 2020 | 0.2
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Lower | 2050 | 0.2
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Upper | 2020 | 0.25
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Upper | 2050 | 0.3
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | ctrl | 2020 | 0.225
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | ctrl | 2030 | 0.225
H2 70 | Main distribution line-H2-70 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | ctrl | 2050 | 0.225
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2020 | 0
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2050 | 0
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2020 | 0
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2050 | 0
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2020 | 0
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2030 | 0
H2 70 | Main distribution line-H2-70 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2050 | 0
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2020 | 0.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2020 | 2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Lower | 2020 | 1.47
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Lower | 2050 | 0.9
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Upper | 2020 | 3.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | Upper | 2050 | 2.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | ctrl | 2020 | 2.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | ctrl | 2030 | 1.68
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy demand, compressor filling station [%] | pct. |  | B |  | ctrl | 2050 | 1.47
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 6.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 5.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 12.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 10.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 7.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1-100 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 6.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 5.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 4.6
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 10.4
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 8.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 6.4
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 5.9
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 100-250 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 5.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 2.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 1.9
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 4.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 3.6
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 2.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 2.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 1500-5000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 2.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 4.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 3.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 8.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 6.9
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 5.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 4.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 250-500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 4.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 3.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 2.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 6.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 5.2
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 3.8
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 3.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 500-1500 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 3.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 1.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 1.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 3.4
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 2.8
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 2.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 1.9
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines 5000-20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 1.7
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2020 | 1.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Lower | 2050 | 1.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2020 | 2.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | Upper | 2050 | 2.1
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2020 | 1.5
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2030 | 1.4
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Energy losses, lines above 20000 MW [%/1000 km] | pct./1000km |  | A |  | ctrl | 2050 | 1.3
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2020 | 45
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2050 | 45
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2020 | 55
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2050 | 55
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2020 | 50
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2030 | 50
H2 140 | Main distribution line H2-140 bar | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2050 | 50
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Lower | 2020 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Lower | 2050 | 0.11697
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Upper | 2020 | 1.0634
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | Upper | 2050 | 1.0634
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | ctrl | 2020 | 0.54232
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | ctrl | 2030 | 0.26584
H2 140 | Main distribution line H2-140 bar | Financial data | Fixed O&M [€/km/year/MW] | EUR/km/year/MW | 2020 | E | 0 | ctrl | 2050 | 0.19938
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 3.9345
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 3.5091
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 5.5295
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 4.9979
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 4.3598
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 4.1472
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 0-100 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 3.9345
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 1.7014
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 1.5951
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 2.4458
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 2.2331
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 1.9141
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 1.8077
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 1.7014
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 0.42535
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.42535
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 0.53169
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 0.53169
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 0.42535
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 0.42535
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 1000-4000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 0.42535
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 1.0634
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.95704
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 1.4887
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 1.3824
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 1.1697
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 1.1697
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 1.0634
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 0.74436
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.63802
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 0.95704
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 0.95704
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 0.8507
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 0.74436
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 0.74436
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2020 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Lower | 2050 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2020 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | Upper | 2050 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2020 | 0.24458
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2030 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Investment costs; single line, above 6000 MW [€/MW/m] | EUR/MW/m | 2020 | C | 0 | ctrl | 2050 | 0.21267
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2020 | 0.75
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2050 | 0.7
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2020 | 0.8
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2050 | 0.8
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2020 | 0.775
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2030 | 0.775
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2050 | 0.775
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Lower | 2020 | 0.2
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Lower | 2050 | 0.2
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Upper | 2020 | 0.25
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | Upper | 2050 | 0.3
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | ctrl | 2020 | 0.225
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | ctrl | 2030 | 0.225
H2 140 | Main distribution line H2-140 bar | Financial data | Investments, percentage materials [%] | pct. |  | D | 0 | ctrl | 2050 | 0.225
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2020 | 0
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2050 | 0
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2020 | 0
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2050 | 0
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2020 | 0
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2030 | 0
H2 140 | Main distribution line H2-140 bar | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2050 | 0
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2020 | 0.5
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2020 | 2
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
NH3 | Main distribution line-NH3 | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Lower | 2020 | 0.01
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Lower | 2050 | 0.01
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Upper | 2020 | 0.1
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Upper | 2050 | 0.1
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2020 | <0.1
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2030 | <0.1
NH3 | Main distribution line-NH3 | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2050 | <0.1
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2020 | 45
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2050 | 45
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2020 | 55
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2050 | 55
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2020 | 50
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2030 | 50
NH3 | Main distribution line-NH3 | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2050 | 50
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Lower | 2020 | 53.1686
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Lower | 2050 | 53.1686
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Upper | 2020 | 212.6745
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Upper | 2050 | 212.6745
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2020 | 106.3373
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2030 | 106.3373
NH3 | Main distribution line-NH3 | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2050 | 106.3373
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 9.6502
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 8.8107
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 16.0837
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 13.7055
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 10.7401
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 10.2084
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1-15 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 9.783
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 1.215
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 1.1093
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 2.025
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 1.7256
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 1.3824
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 1.276
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 1.276
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.2424
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.22131
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.404
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.34427
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.31901
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.21267
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 1000-2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.21267
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 6.413
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 5.855
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 10.6883
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 9.1078
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 7.1246
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 6.8056
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 15-30 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 6.4866
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 2.6629
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 2.4313
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 4.4382
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 3.782
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 2.9774
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 2.8711
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 30-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 2.6584
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.69785
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.63714
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 1.1631
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.9911
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.74436
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.74436
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.74436
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.42205
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.38533
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.70341
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.5994
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.42535
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.42535
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.42535
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.19257
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.17582
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.32095
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.27349
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.21267
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.21267
NH3 | Main distribution line-NH3 | Financial data | Investment costs; single line, above 2000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.21267
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2020 | 0.8
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2050 | 0.75
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2020 | 0.9
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2050 | 0.9
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2020 | 0.87
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2030 | 0.8265
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2050 | 0.783
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Lower | 2020 | 0.1
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Lower | 2050 | 0.1
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Upper | 2020 | 0.2
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Upper | 2050 | 0.25
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2020 | 0.13
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2030 | 0.1735
NH3 | Main distribution line-NH3 | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2050 | 0.217
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2020 | 0
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2050 | 0
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2020 | 0
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2050 | 0
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2020 | 0
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2030 | 0
NH3 | Main distribution line-NH3 | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2050 | 0
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2020 | 0.5
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2020 | 2
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
DME | Main distribution line-DME | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Lower | 2020 | 0.01
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Lower | 2050 | 0.01
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Upper | 2020 | 0.1
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Upper | 2050 | 0.1
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2020 | <0.1
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2030 | <0.1
DME | Main distribution line-DME | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2050 | <0.1
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2020 | 45
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2050 | 45
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2020 | 55
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2050 | 55
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2020 | 50
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2030 | 50
DME | Main distribution line-DME | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2050 | 50
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Lower | 2020 | 53.1686
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Lower | 2050 | 53.1686
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Upper | 2020 | 212.6745
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Upper | 2050 | 212.6745
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2020 | 106.3373
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2030 | 106.3373
DME | Main distribution line-DME | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2050 | 106.3373
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 9.3103
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 8.5003
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 15.5171
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 13.2227
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 10.3147
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 9.8894
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 9.464
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 1.1722
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 1.0702
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 1.9537
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 1.6648
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 1.276
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 1.276
DME | Main distribution line-DME | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 1.1697
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.23386
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.21352
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.38977
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.33214
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.21267
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.21267
DME | Main distribution line-DME | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.21267
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 6.1871
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 5.6488
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 10.3118
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 8.787
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 6.9119
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 6.5929
DME | Main distribution line-DME | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 6.2739
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.67327
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.61469
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 1.1221
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.95619
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.74436
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.74436
DME | Main distribution line-DME | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.63802
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 2.5691
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 2.3456
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 4.2819
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 3.6487
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 2.8711
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 2.7648
DME | Main distribution line-DME | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 2.6584
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.40718
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.37176
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.67863
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.57829
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.42535
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.42535
DME | Main distribution line-DME | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.42535
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.18579
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.16962
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.30964
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.26386
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.21267
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.21267
DME | Main distribution line-DME | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.21267
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2020 | 0.8
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2050 | 0.75
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2020 | 0.9
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2050 | 0.9
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2020 | 0.87
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2030 | 0.8265
DME | Main distribution line-DME | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2050 | 0.783
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Lower | 2020 | 0.1
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Lower | 2050 | 0.1
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Upper | 2020 | 0.2
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Upper | 2050 | 0.25
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2020 | 0.13
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2030 | 0.1735
DME | Main distribution line-DME | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2050 | 0.217
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2020 | 0
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2050 | 0
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2020 | 0
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2050 | 0
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2020 | 0
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2030 | 0
DME | Main distribution line-DME | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2050 | 0
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2020 | 0.5
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2020 | 2
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
TOLU | Main distribution line-Toluene | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Lower | 2020 | 0.01
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Lower | 2050 | 0.01
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Upper | 2020 | 0.1
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | Upper | 2050 | 0.1
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2020 | <0.1
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2030 | <0.1
TOLU | Main distribution line-Toluene | Energy/technical data | Energy losses [‰] | ‰ |  | [A, B] |  | ctrl | 2050 | <0.1
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2020 | 45
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | Lower | 2050 | 45
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2020 | 55
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | Upper | 2050 | 55
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2020 | 50
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2030 | 50
TOLU | Main distribution line-Toluene | Energy/technical data | Technical life time [years] | years |  |  |  | ctrl | 2050 | 50
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Lower | 2020 | 53.1686
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Lower | 2050 | 53.1686
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Upper | 2020 | 212.6745
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | Upper | 2050 | 212.6745
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2020 | 106.3373
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2030 | 106.3373
TOLU | Main distribution line-Toluene | Financial data | Fixed O&M [€/km/year] | EUR/km/year | 2020 | E | 0 | ctrl | 2050 | 106.3373
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 8.7729
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 8.0097
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 14.6216
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 12.4595
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 9.783
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 9.3577
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1-20 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 8.9323
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 1.1046
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 1.0085
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 1.841
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 1.5687
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 1.276
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 1.1697
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 100-300 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 1.1697
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.22037
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.20119
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.36728
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.31297
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.21267
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.21267
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 1000-2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.21267
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 5.83
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 5.3228
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 9.7166
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 8.2798
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 6.4866
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 6.1676
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 20-50 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 5.9549
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.63441
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.57922
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 1.0573
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.901
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.74436
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.63802
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 300-500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.63802
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 2.4209
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 2.2102
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 4.0348
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 3.4382
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 2.6584
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 2.5521
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 2.4458
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.38368
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.3503
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.63947
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.54491
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.42535
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.42535
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.42535
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2020 | 0.17506
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Lower | 2050 | 0.15983
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2020 | 0.29177
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | Upper | 2050 | 0.24863
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2020 | 0.21267
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2030 | 0.21267
TOLU | Main distribution line-Toluene | Financial data | Investment costs; single line, above 2500 MW [€/MW/m] | EUR/MW/m | 2020 | [B, C] | 0 | ctrl | 2050 | 0.21267
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2020 | 0.8
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Lower | 2050 | 0.75
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2020 | 0.9
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | Upper | 2050 | 0.9
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2020 | 0.87
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2030 | 0.8265
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage installation [%] | pct. |  | D | 0 | ctrl | 2050 | 0.783
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Lower | 2020 | 0.1
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Lower | 2050 | 0.1
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Upper | 2020 | 0.2
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | Upper | 2050 | 0.25
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2020 | 0.13
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2030 | 0.1735
TOLU | Main distribution line-Toluene | Financial data | Investments, percentage materials [%] | pct. |  | C | 0 | ctrl | 2050 | 0.217
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2020 | 0
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Lower | 2050 | 0
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2020 | 0
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | Upper | 2050 | 0
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2020 | 0
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2030 | 0
TOLU | Main distribution line-Toluene | Financial data | Variable O&M [€/MW/km] | EUR/MW/km | 2020 | 0 | 0 | ctrl | 2050 | 0
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | Lower | 2020 | 10
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | Lower | 2050 | 6
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | Upper | 2020 | 15
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | Upper | 2050 | 12
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | ctrl | 2020 | 12.6667
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | ctrl | 2030 | 10.3
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton CH2] | MJ/km/tonCH2 |  | [A, H] | 5 | ctrl | 2050 | 7.3
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | Lower | 2020 | 0.51092
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | Lower | 2050 | 0.3902
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | Upper | 2020 | 0.72092
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | Upper | 2050 | 0.5902
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | ctrl | 2020 | 0.62092
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | ctrl | 2030 | 0.58824
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton DME] | MJ/km/tonDME |  | [A, H] | 5 | ctrl | 2050 | 0.4902
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | Lower | 2020 | 5
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | Lower | 2050 | 4
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | Upper | 2020 | 10
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | Upper | 2050 | 9
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | ctrl | 2020 | 5.9552
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | ctrl | 2030 | 5.6417
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton LH2] | MJ/km/tonLH2 |  | [A, H] | 5 | ctrl | 2050 | 4.7015
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | Lower | 2020 | 0.56469
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | Lower | 2050 | 0.43265
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | Upper | 2020 | 0.87469
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | Upper | 2050 | 0.73265
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | ctrl | 2020 | 0.67469
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | ctrl | 2030 | 0.63918
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton NH3] | MJ/km/tonNH3 |  | [A, H] | 5 | ctrl | 2050 | 0.53265
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | Lower | 2020 | 0.39
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | Lower | 2050 | 0.3
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | Upper | 2020 | 0.6
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | Upper | 2050 | 0.5
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | ctrl | 2020 | 0.5
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | ctrl | 2030 | 0.5
Road transport | Road transport | Energy/technical data | Energy demand truck [MJ/km/ton toluene] | MJ/km/tontoluene |  | [A, H] | 5 | ctrl | 2050 | 0.4
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | Lower | 2020 | 4
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | Lower | 2050 | 4
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | Upper | 2020 | 12
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | Upper | 2050 | 12
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2020 | 10
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2030 | 10
Road transport | Road transport | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2050 | 10
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | Lower | 2020 | 0
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | Lower | 2050 | 0
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | Upper | 2020 | 0
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | Upper | 2050 | 2.4212
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | ctrl | 2020 | 2.4212
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | ctrl | 2030 | 1.9885
Road transport | Road transport | Financial data | CH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 2.1267 | ctrl | 2050 | 1.6057
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | Lower | 2020 | 0
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | Lower | 2050 | 0
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | Upper | 2020 | 0
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | Upper | 2050 | 117.5632
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | ctrl | 2020 | 117.5632
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | ctrl | 2030 | 82.9431
Road transport | Road transport | Financial data | CH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 2.1267 | ctrl | 2050 | 61.6756
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | Lower | 2020 | 0
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | Lower | 2050 | 0
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | Upper | 2020 | 0
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | Upper | 2050 | 0.11064
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | ctrl | 2020 | 0.11064
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | ctrl | 2030 | 0.11064
Road transport | Road transport | Financial data | DME: Driving cost [€/tonDME/km] | EUR/tonDME/km | 2020 | [E, F, C, H] | 4.2535 | ctrl | 2050 | 0.11064
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | Lower | 2020 | 0
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | Lower | 2050 | 0
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | Upper | 2020 | 0
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | Upper | 2050 | 3.4307
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | ctrl | 2020 | 3.4307
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | ctrl | 2030 | 3.4307
Road transport | Road transport | Financial data | DME: Loading/unloading cost [€/tonDME] | EUR/tonDME | 2020 | [E, F, C, H] | 4.2535 | ctrl | 2050 | 3.4307
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | Lower | 2020 | 0
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | Lower | 2050 | 0
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | Upper | 2020 | 0
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | Upper | 2050 | 1.0394
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | ctrl | 2020 | 1.0394
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | ctrl | 2030 | 1.0634
Road transport | Road transport | Financial data | LH2: Driving cost [€/tonH2/km] | EUR/tonH2/km | 2020 | [E, F, G] | 1.0634 | ctrl | 2050 | 1.0102
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | Lower | 2020 | 0
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | Lower | 2050 | 0
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | Upper | 2020 | 0
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | Upper | 2050 | 55.2954
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | ctrl | 2020 | 55.2954
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | ctrl | 2030 | 47.8518
Road transport | Road transport | Financial data | LH2: Loading/unloading cost [€/tonH2] | EUR/tonH2 | 2020 | [E, F, G] | 1.0634 | ctrl | 2050 | 39.3448
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | Lower | 2020 | 0
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | Lower | 2050 | 0
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | Upper | 2020 | 0
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | Upper | 2050 | 0.12023
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | ctrl | 2020 | 0.12023
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | ctrl | 2030 | 0.11697
Road transport | Road transport | Financial data | NH3: Driving cost [€/tonNH3/km] | EUR/tonNH3/km | 2020 | [E, F, H] | 3.1901 | ctrl | 2050 | 0.10634
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | Lower | 2020 | 0
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | Lower | 2050 | 0
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | Upper | 2020 | 0
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | Upper | 2050 | 3.9345
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | ctrl | 2020 | 3.9345
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | ctrl | 2030 | 3.9345
Road transport | Road transport | Financial data | NH3: Loading/unloading cost [€/tonNH3] | EUR/tonNH3 | 2020 | [E, F, H] | 3.1901 | ctrl | 2050 | 3.9345
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | Lower | 2020 | 0
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | Lower | 2050 | 0
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | Upper | 2020 | 0
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | Upper | 2050 | 0.075773
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | ctrl | 2020 | 0.075773
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | ctrl | 2030 | 0.075773
Road transport | Road transport | Financial data | Toluene: Driving cost [€/tontoluene/km] | EUR/tontoluene/km | 2020 | [E, F, D, H] | 4.2535 | ctrl | 2050 | 0.075773
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | Lower | 2020 | 0
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | Lower | 2050 | 0
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | Upper | 2020 | 0
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | Upper | 2050 | 2.0539
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | ctrl | 2020 | 2.0539
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | ctrl | 2030 | 2.0539
Road transport | Road transport | Financial data | Toluene: Loading/unloading cost [€/tontoluene] | EUR/tontoluene | 2020 | [E, F, D, H] | 4.2535 | ctrl | 2050 | 2.0539
Ship Transport | Ship transport | Energy/technical data | L20: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2020 | 2450
Ship Transport | Ship transport | Energy/technical data | L20: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2030 | 2205
Ship Transport | Ship transport | Energy/technical data | L20: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2050 | 1715
Ship Transport | Ship transport | Energy/technical data | LH2: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2020 | 2250
Ship Transport | Ship transport | Energy/technical data | LH2: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2030 | 2025
Ship Transport | Ship transport | Energy/technical data | LH2: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2050 | 1575
Ship Transport | Ship transport | Energy/technical data | LHC: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2020 | 2450
Ship Transport | Ship transport | Energy/technical data | LHC: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2030 | 2205
Ship Transport | Ship transport | Energy/technical data | LHC: Energy demand [MJ/km] | MJ/km |  | [A, F] |  | ctrl | 2050 | 1715
Ship Transport | Ship transport | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2020 | 20
Ship Transport | Ship transport | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2030 | 20
Ship Transport | Ship transport | Energy/technical data | Technical life time [years] | years |  |  | 1 | ctrl | 2050 | 20
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | ctrl | 2020 | 9.5704
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | ctrl | 2030 | 9.5704
Ship Transport | Ship transport | Financial data | L20: Fixed O&M cost [€/tonL20/y] | EUR/tonL20/y | 2020 | E | 0 | ctrl | 2050 | 9.5704
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | ctrl | 2020 | 1860.9023
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | ctrl | 2030 | 1978.8327
Ship Transport | Ship transport | Financial data | L20: Investment cost [€/tonL20] | EUR/tonL20 | 2020 | [B, C] | [2, 3] | ctrl | 2050 | 1978.8327
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | ctrl | 2020 | 1.8077
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | ctrl | 2030 | 1.8077
Ship Transport | Ship transport | Financial data | L20: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | ctrl | 2050 | 1.8077
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | ctrl | 2020 | 79.753
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | ctrl | 2030 | 74.4361
Ship Transport | Ship transport | Financial data | LH2: Fixed O&M cost [€/tonH2/y] | EUR/tonH2/y | 2020 | E | 0 | ctrl | 2050 | 53.1686
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | ctrl | 2020 | 15950.5908
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | ctrl | 2030 | 14887.2181
Ship Transport | Ship transport | Financial data | LH2: Investment cost [€/tonH2] | EUR/tonH2 | 2020 | G | [2, 3] | ctrl | 2050 | 10633.7272
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | ctrl | 2020 | 7.2309
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | ctrl | 2030 | 6.3802
Ship Transport | Ship transport | Financial data | LH2: Port cost [€/tonH2] | EUR/tonH2 | 2020 | 0 | 3.1901 | ctrl | 2050 | 4.2535
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | ctrl | 2020 | 4.2535
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | ctrl | 2030 | 4.2535
Ship Transport | Ship transport | Financial data | LHC: Fixed O&M cost [€/tonLHC/y] | EUR/tonLHC/y | 2020 | E | 0 | ctrl | 2050 | 4.2535
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | ctrl | 2020 | 733.7272
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | ctrl | 2030 | 780.2255
Ship Transport | Ship transport | Financial data | LHC: Investment cost [€/tonLHC] | EUR/tonLHC | 2020 | D | 0 | ctrl | 2050 | 780.2255
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | Lower | 2020 | 0
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | Lower | 2050 | 0
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | Upper | 2020 | 0
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | Upper | 2050 | 0
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | ctrl | 2020 | 1.4887
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | ctrl | 2030 | 1.4887
Ship Transport | Ship transport | Financial data | LHC: Port cost [€/tonLHC] | EUR/tonLHC | 2020 | 0 | 3.1901 | ctrl | 2050 | 1.4887

## Notes
ws | description
111 1 el Main distri50-60kVcabl | 9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 1 el Main distri50-60kVcabl | A. Energy losses are estimated from total energy loss on transmission levels in the voltage range 20kV to 130 kV in Sweden. Transmission lines/cables accounts for approximately 60% of the losses and transformers accounts for approximately 40%.
111 1 el Main distri50-60kVcabl | B. Development of energy loss over time depends on several factors. Today, transmission losses typically range between 1% to 3% in Denmark. The variation in transmission losses depends mainly on the amount of power transfer to neighboring countries. The trend in Denmark is towards increasing tra...
111 1 el Main distri50-60kVcabl | C. Cable life length depends on material characteristics and the thermal loading of the cable. Increasing cable area and thus reducing cable temperature leads to longer life length. Today, up to 40 years are realistic life length of a cable with moderate thermal loading. Technological development...
111 1 el Main distri50-60kVcabl | D. Load profile varies significantly between different stations and cables and a general figure is given. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 6 %, the lower scenario is an increase in peak...
111 1 el Main distri50-60kVcabl | E. Construction time ranges normally from 1 to 2 years. In technically complex projects and for long cable stretches, the construction time increases and could stretch up to 5 years.
111 1 el Main distri50-60kVcabl | F. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2. \nF...
111 1 el Main distri50-60kVcabl | G. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
111 1 el Main distri50-60kVcabl | H. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2.For ...
111 1 el Main distri50-60kVcabl | I. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 60 kV. Cost is calculated as the average cost between dense populated areas and city areas. Adjusting factors for each area are: dense populated: 0,94, and city: 1,06. For power range 100-250 MW the cos...
111 1 el Main distri50-60kVcabl | J. Power levels above 100 MW are normally transported at higher voltage levels. In cases where it is motivated to transport higher power levels at 50/60 kV, this is done in parallele cable budles in the same shaft. The cost of two parallel cables can be calculated as the double cost of one cable ...
111 1 el Main distri50-60kVcabl | K. Reinforcement costs depends on where bottlenecks are situated in the grid. Here the reinforcement cost is given for an upgrade of transformer capacity by 40 MVA. Reinforcement of line/cable capacity is in parity with the investment cost in described in row 18-20 and depends on power level and...
111 1 el Main distri50-60kVcabl | L. Station cost is based on a 40 MW station with 2 x 20 MVA transformers (72/12 kV). Station cost depends on a number of factors, such as power rating, redundancy on transformers etc. Station cost have an almost linear relation to the power rating and following relation holds for the power span...
111 1 el Main distri50-60kVcabl | M. Station cost is based on average cost for capacity banks and inductor with a design voltage of 72 kV. It is assumed that the equipment is installed in a existing station.
111 1 el Main distri50-60kVcabl | O. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
111 1 el Main distri50-60kVcabl | P. The percentage of the investment cost allocated to material cost and installation cost varies depending on area type (rural or city) and power level. An average is given here. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installat...
111 1 el Main distri50-60kVcabl | Q. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost multiplied by the average cost of cables per MW and km given in row 18 to 20. It should be noted that the O&M cost in distribution system mainly is attributed to stations since there is practically no m...
111 1 el Main distri50-60kVcabl | R. Variable O&M cost is in very low for electric transmission systems and considered to be negligible
111 1 el Main distri50-60kVcabl | S. Energy losses and auxiliary electricity consumption can be considered negligible
111 3 el distri suburban | 7. Swedish Energy Markets Inspectorate [http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 3 el distri suburban | A. The line losses were calculated using reference [1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 3 el distri suburban | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 3 el distri suburban | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 3 el distri suburban | D. Calculations for the load profile were based on reference [1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increa...
111 3 el distri suburban | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
111 3 el distri suburban | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
111 3 el distri suburban | G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest powe...
111 3 el distri suburban | H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest po...
111 3 el distri suburban | I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the cur...
111 3 el distri suburban | J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations...
111 3 el distri suburban | K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area [power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In...
111 3 el distri suburban | L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased...
111 3 el distri suburban | M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
111 3 el distri suburban | N. Auxiliary electricity consumption can be considered negligible
111 4 el distri city | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 4 el distri city | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 4 el distri city | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 4 el distri city | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 4 el distri city | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
111 4 el distri city | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
111 4 el distri city | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
111 4 el distri city | G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest powe...
111 4 el distri city | H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest po...
111 4 el distri city | I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the cur...
111 4 el distri city | J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations...
111 4 el distri city | K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In...
111 4 el distri city | L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintenance on cables. The O&M cost is assume to be reduced due to increased ...
111 4 el distri city | M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
111 4 el distri city | N. Auxiliary electricity consumption can be considered negligible
111 5 el distri new area | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 5 el distri new area | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 5 el distri new area | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 5 el distri new area | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 5 el distri new area | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
111 5 el distri new area | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
111 5 el distri new area | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
111 5 el distri new area | G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest powe...
111 5 el distri new area | H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest po...
111 5 el distri new area | I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the cur...
111 5 el distri new area | J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations...
111 5 el distri new area | K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In...
111 5 el distri new area | L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased...
111 5 el distri new area | M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
111 5 el distri new area | N. Auxiliary electricity consumption can be considered negligible
111 6 el trans OH | 3. See [50] in text chapter
111 6 el trans OH | 1. Low and high are minus/plus 30%
111 6 el trans OH | 2. 2025 prices: after adding 20% to price from source
111 6 el trans OH | 3. Prices in 2050 assumed to be as prices before 20% increase in 2025
111 6 el trans OH | 4. Prices assumed to decrease linearly from 2030 to 2050
111 6 el trans OH | 5. Estimates, typical values (AC with compensation)
111 6 el trans OH | 6. Estimates,project specific, depending on e.g., length of line
111 6 el trans OH | 7. Estimates, based on stakeholder information
111 6 el trans OH | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 6 el trans OH | 9. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
111 6 el trans OH | 10. Costs are including compensation (AC)
111 6 el trans OH | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 6 el trans OH | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 6 el trans OH | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 6 el trans OH | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 6 el trans OH | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
111 6 el trans OH | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
111 6 el trans OH | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
111 7 el trans AC&DC cables | 2. See [30], [31], [36], [42] in text chapter
111 7 el trans AC&DC cables | 1. Low and high are minus/plus 30%
111 7 el trans AC&DC cables | 2. 2025 prices: adding 20% to price from source
111 7 el trans AC&DC cables | 3. Prices in 2050 assumed to be as prices before 20% increase in 2025
111 7 el trans AC&DC cables | 4. Prices assumed to decrease linearly from 2030 to 2050
111 7 el trans AC&DC cables | 5. Estimates, typical values.
111 7 el trans AC&DC cables | 6. Estimates, project specific, depending on e.g., length of cable
111 7 el trans AC&DC cables | 7. Estimates, typical values (AC cables with compensation)
111 7 el trans AC&DC cables | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 7 el trans AC&DC cables | 9. 220 kV with capacity of about 500 MW
111 7 el trans AC&DC cables | 10. 525 kV bipole with capacity 1500-2000 MW
111 7 el trans AC&DC cables | 11. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
111 7 el trans AC&DC cables | 12. Costs are including compensation (AC)
111 7 el trans AC&DC cables | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 7 el trans AC&DC cables | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 7 el trans AC&DC cables | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 7 el trans AC&DC cables | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 7 el trans AC&DC cables | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
111 7 el trans AC&DC cables | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
111 7 el trans AC&DC cables | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
111 8 el substations | 2. See [30], [31], [36], [42] in text chapter
111 8 el substations | 1. 2025 prices: adding 20% to "year of source " prices
111 8 el substations | 2. Low and high: minus/plus 30%
111 8 el substations | 3. Prices in 2050 assumed to be as prices before 20% increase in 2025
111 8 el substations | 4. Prices assumed to decrease linearly from 2030 to 2050
111 8 el substations | 5. Estimates, typical values. AC substation includes transformers, switchgear, powerlines, compensation, control equipment etc.
111 8 el substations | 6. Estimates, project specific, depends on size and location of station. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc
111 8 el substations | 7. Estimates, based on stakeholder information
111 8 el substations | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 8 el substations | 9. 220 kV substation, capacity in the range of 500 MW
111 8 el substations | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
111 8 el substations | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 8 el substations | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 8 el substations | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 8 el substations | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 8 el substations | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
111 8 el substations | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
111 8 el substations | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
111 9 el transformers | 2. See [30], [31], [36], [42] in text chapter
111 9 el transformers | 1. 2025 prices: adding 20% to price from source
111 9 el transformers | 2. Low and high: minus/plus 30%
111 9 el transformers | 3. Prices assumed to decrease linearly from 2030 to 2050
111 9 el transformers | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
111 9 el transformers | 5. Estimates, typical values.
111 9 el transformers | 6. Estimates, based on stakeholder information
111 9 el transformers | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 9 el transformers | 6. Estimates, project specific, depending on e.g., length of cable
111 9 el transformers | 7. Estimates, typical values (AC cables with compensation)
111 9 el transformers | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 9 el transformers | 9. 220 kV with capacity of about 500 MW
111 9 el transformers | 10. 525 kV bipole with capacity 1500-2000 MW
111 9 el transformers | 11. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
111 9 el transformers | 12. Costs are including compensation (AC)
111 9 el transformers | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 9 el transformers | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 9 el transformers | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 9 el transformers | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 9 el transformers | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
111 9 el transformers | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
111 9 el transformers | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
111 10 el compensation | 2. See [30], [31], [36], [42] in text chapter
111 10 el compensation | 1. Low and high: minus/plus 30%
111 10 el compensation | 2. 2025 prices: adding 20% to price from source
111 10 el compensation | 3. Prices assumed to decrease linearly from 2030 to 2050
111 10 el compensation | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
111 10 el compensation | 5. Estimates, typical values.
111 10 el compensation | 6. Estimates, load of reactive power
111 10 el compensation | 7. Estimates, (partly) based on stakeholder information
111 10 el compensation | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 10 el compensation | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
111 10 el compensation | 9. 220 kV substation, capacity in the range of 500 MW
111 10 el compensation | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
111 10 el compensation | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 10 el compensation | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
111 10 el compensation | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
111 10 el compensation | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
111 10 el compensation | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
111 10 el compensation | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
111 10 el compensation | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
112 6 gas Main distri line | 2. See [30], [31], [36], [42] in text chapter
112 6 gas Main distri line | 1. 2025 prices: adding 20% to price from source
112 6 gas Main distri line | 2. Low and high: minus/plus 30%
112 6 gas Main distri line | 3. Prices assumed to decrease linearly from 2030 to 2050
112 6 gas Main distri line | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
112 6 gas Main distri line | 5. Estimates, typical values.
112 6 gas Main distri line | 6. Estimates, based on stakeholder information
112 6 gas Main distri line | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 6 gas Main distri line | 6. Estimates, project specific, depending on e.g., length of cable
112 6 gas Main distri line | 7. Estimates, typical values (AC cables with compensation)
112 6 gas Main distri line | 2. HMN Naturgas
112 6 gas Main distri line | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
112 6 gas Main distri line | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
112 6 gas Main distri line | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
112 6 gas Main distri line | D. Includes enginering, tender, and construction.
112 6 gas Main distri line | E. Rates include VVM review, landowner compensation and archaeological screening. Based on 20 km, of which 8 % is based on drilling.
112 6 gas Main distri line | F. Data given is for a 50 MW capacity
112 6 gas Main distri line | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
112 6 gas Main distri line | H. Not possible to give general numbers. Depends on kind of reinforcement. Can be calculated based on the other numbers given.
112 6 gas Main distri line | I. Capacity not relevant-too high
112 6 gas Main distri line | J. Type 1 MR stations supplying the transmission system level 2-not part of the scope
112 6 gas Main distri line | K. Type 1 MR stations supplying the transmission system level 2 .The stated costs are the average cost for a 40/4 bar MR station where reheating after expansion is required and a 19/4 bar MR station where reheating is not necessary. The cost is only modestly size dependent. A 40/4 bar station ca...
112 6 gas Main distri line | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
112 6 gas Main distri line | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
112 6 gas Main distri line | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
112 6 gas Main distri line | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
112 6 gas Main distri line | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
112 6 gas Main distri line | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
112 6 gas Main distri line | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
112 7 gas Rural | 2. See [30], [31], [36], [42] in text chapter
112 7 gas Rural | 1. Low and high: minus/plus 30%
112 7 gas Rural | 2. 2025 prices: adding 20% to price from source
112 7 gas Rural | 3. Prices assumed to decrease linearly from 2030 to 2050
112 7 gas Rural | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
112 7 gas Rural | 5. Estimates, typical values.
112 7 gas Rural | 6. Estimates, load of reactive power
112 7 gas Rural | 7. Estimates, (partly) based on stakeholder information
112 7 gas Rural | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 7 gas Rural | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 7 gas Rural | 9. 220 kV substation, capacity in the range of 500 MW
112 7 gas Rural | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
112 7 gas Rural | 2. HMN Naturgas
112 7 gas Rural | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The l...
112 7 gas Rural | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
112 7 gas Rural | C. There is no power consuming parts in the distribution system
112 7 gas Rural | D. Based on given case
112 7 gas Rural | E. Capacity range not relevant for given case
112 7 gas Rural | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
112 7 gas Rural | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
112 7 gas Rural | H. Reinforcement not relevant
112 7 gas Rural | I. No station will be installed for the distribution network
112 7 gas Rural | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
112 7 gas Rural | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
112 7 gas Rural | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
112 7 gas Rural | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
112 8 gas Suburban | 2. See [30], [31], [36], [42] in text chapter
112 8 gas Suburban | 1. 2025 prices: adding 20% to price from source
112 8 gas Suburban | 2. Low and high: minus/plus 30%
112 8 gas Suburban | 3. Prices assumed to decrease linearly from 2030 to 2050
112 8 gas Suburban | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
112 8 gas Suburban | 5. Estimates, typical values.
112 8 gas Suburban | 6. Estimates, based on stakeholder information
112 8 gas Suburban | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 8 gas Suburban | 6. Estimates, project specific, depending on e.g., length of cable
112 8 gas Suburban | 7. Estimates, typical values (AC cables with compensation)
112 8 gas Suburban | 2. HMN Naturgas
112 8 gas Suburban | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
112 8 gas Suburban | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
112 8 gas Suburban | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
112 8 gas Suburban | D. Includes enginering, tender, and construction.
112 8 gas Suburban | 2. HMN Naturgas
112 8 gas Suburban | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. ...
112 8 gas Suburban | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
112 8 gas Suburban | C. There is no power consuming parts in the distribution system
112 8 gas Suburban | D. Based on given case
112 8 gas Suburban | E. Capacity range not relevant for given case
112 8 gas Suburban | F. Stated number is for a Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
112 8 gas Suburban | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
112 8 gas Suburban | H. Reinforcement not relevant
112 8 gas Suburban | I. No station will be installed for the distribution network
112 8 gas Suburban | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
112 8 gas Suburban | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
112 8 gas Suburban | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
112 8 gas Suburban | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
112 9 gas City | 2. See [30], [31], [36], [42] in text chapter
112 9 gas City | 1. Low and high: minus/plus 30%
112 9 gas City | 2. 2025 prices: adding 20% to price from source
112 9 gas City | 3. Prices assumed to decrease linearly from 2030 to 2050
112 9 gas City | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
112 9 gas City | 5. Estimates, typical values.
112 9 gas City | 6. Estimates, load of reactive power
112 9 gas City | 7. Estimates, (partly) based on stakeholder information
112 9 gas City | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 9 gas City | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 9 gas City | 9. 220 kV substation, capacity in the range of 500 MW
112 9 gas City | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
112 9 gas City | 1. HMN Naturgas
112 9 gas City | A. For the defined case "New distribution in existing densely populated areas, city centres etc." it is assessed the natural gas based heating will be designed with one boiler and heat is distributied to the endusers by a locel district heating sytem. This means that the local natural gas system...
112 9 gas City | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
112 9 gas City | C. There is no power consuming parts in the distribution system
112 9 gas City | D. Based on given case
112 9 gas City | E. Stated number is for a service line supplying 1,5 MW.
112 9 gas City | F. Not relavant, see note A
112 9 gas City | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
112 9 gas City | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
112 9 gas City | H. Reinforcement not relevant
112 9 gas City | I. No station will be installed for the distribution network
112 9 gas City | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
112 9 gas City | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
112 9 gas City | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
112 9 gas City | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
112 1 gas New area | 2. See [30], [31], [36], [42] in text chapter
112 1 gas New area | 1. 2025 prices: adding 20% to price from source
112 1 gas New area | 2. Low and high: minus/plus 30%
112 1 gas New area | 3. Prices assumed to decrease linearly from 2030 to 2050
112 1 gas New area | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
112 1 gas New area | 5. Estimates, typical values.
112 1 gas New area | 6. Estimates, based on stakeholder information
112 1 gas New area | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
112 1 gas New area | 6. Estimates, project specific, depending on e.g., length of cable
112 1 gas New area | 7. Estimates, typical values (AC cables with compensation)
112 1 gas New area | 2. HMN Naturgas
112 1 gas New area | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
112 1 gas New area | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
112 1 gas New area | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
112 1 gas New area | D. Includes enginering, tender, and construction.
112 1 gas New area | 2. HMN Naturgas
112 1 gas New area | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
112 1 gas New area | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
112 1 gas New area | C. There are no power consuming parts in the distribution system
112 1 gas New area | D. Based on given case
112 1 gas New area | E. Capacity range not relevant for given case
112 1 gas New area | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
112 1 gas New area | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
112 1 gas New area | H. Reinforcement not relevant
112 1 gas New area | I. No station will be installed for the distribution network
112 1 gas New area | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
112 1 gas New area | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
112 1 gas New area | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
112 1 gas New area | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
113_11 DH transmission | 2. See [30], [31], [36], [42] in text chapter
113_11 DH transmission | 1. Low and high: minus/plus 30%
113_11 DH transmission | 2. 2025 prices: adding 20% to price from source
113_11 DH transmission | 3. Prices assumed to decrease linearly from 2030 to 2050
113_11 DH transmission | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
113_11 DH transmission | 5. Estimates, typical values.
113_11 DH transmission | 6. Estimates, load of reactive power
113_11 DH transmission | 7. Estimates, (partly) based on stakeholder information
113_11 DH transmission | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
113_11 DH transmission | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
113_11 DH transmission | 9. 220 kV substation, capacity in the range of 500 MW
113_11 DH transmission | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
113_11 DH transmission | 4. Consolidated with statistics from Danish District Heating Association 2020
113_11 DH transmission | A. The loss is per trench km of transmission pipeline pair.
113_11 DH transmission | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
113_11 DH transmission | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
113_11 DH transmission | D. Two district heating pipes were chosen for each interval (one for the lowest effect level and one for the highest). The average of these two are stated in the table. For cost interpolation: P = a * C^b, where P = cost in €/MW/m, C = capacity in MW, a = 330 and b =-0,571.
113_11 DH transmission | E. Depends on the scale of the transmission grid and supply strategy of reserve capacity. Therefore, it is not possible to generalize these costs.
113_11 DH transmission | F. Soft costs include design, planning, tender, permits, supervision, etc.
113_11 DH transmission | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
113_11 DH transmission | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
113_11 DH transmission | H. Reinforcement not relevant
113_11 DH transmission | I. No station will be installed for the distribution network
113_11 DH transmission | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
113_11 DH transmission | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
113_11 DH transmission | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
113_11 DH transmission | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
113_12 DH_Distribu Suburb | 2. See [30], [31], [36], [42] in text chapter
113_12 DH_Distribu Suburb | 1. 2025 prices: adding 20% to price from source
113_12 DH_Distribu Suburb | 2. Low and high: minus/plus 30%
113_12 DH_Distribu Suburb | 3. Prices assumed to decrease linearly from 2030 to 2050
113_12 DH_Distribu Suburb | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
113_12 DH_Distribu Suburb | 5. Estimates, typical values.
113_12 DH_Distribu Suburb | 6. Estimates, based on stakeholder information
113_12 DH_Distribu Suburb | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
113_12 DH_Distribu Suburb | 6. Estimates, project specific, depending on e.g., length of cable
113_12 DH_Distribu Suburb | 7. Estimates, typical values (AC cables with compensation)
113_12 DH_Distribu Suburb | 2. HMN Naturgas
113_12 DH_Distribu Suburb | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
113_12 DH_Distribu Suburb | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
113_12 DH_Distribu Suburb | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
113_12 DH_Distribu Suburb | D. Includes enginering, tender, and construction.
113_12 DH_Distribu Suburb | 2. HMN Naturgas
113_12 DH_Distribu Suburb | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
113_12 DH_Distribu Suburb | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
113_12 DH_Distribu Suburb | 4. Consolidated with statistics from Danish District Heating Association 2020
113_12 DH_Distribu Suburb | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
113_12 DH_Distribu Suburb | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities
113_12 DH_Distribu Suburb | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
113_12 DH_Distribu Suburb | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on an area of scattered single-family houses of 1-2 floors with a heat density of 10 GWh/year/km2.
113_12 DH_Distribu Suburb | E. A paved area is assumed for the distribution network. For service lines 50 % unpaved and 50 % paved area is asumed.
113_12 DH_Distribu Suburb | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
113_12 DH_Distribu Suburb | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
113_12 DH_Distribu Suburb | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
113_12 DH_Distribu Suburb | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
113_12 DH_Distribu Suburb | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
113_12 DH_Distribu Suburb | K. Service lines above 100 kW are not relevant in the specific area type.
113_12 DH_Distribu Suburb | L. Single lines above 25 MW are not relevant in the specific area type.
113_12 DH_Distribu Suburb | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
113_13 DH_Distribu City | 2. See [30], [31], [36], [42] in text chapter
113_13 DH_Distribu City | 1. Low and high: minus/plus 30%
113_13 DH_Distribu City | 2. 2025 prices: adding 20% to price from source
113_13 DH_Distribu City | 3. Prices assumed to decrease linearly from 2030 to 2050
113_13 DH_Distribu City | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
113_13 DH_Distribu City | 5. Estimates, typical values.
113_13 DH_Distribu City | 6. Estimates, load of reactive power
113_13 DH_Distribu City | 7. Estimates, (partly) based on stakeholder information
113_13 DH_Distribu City | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
113_13 DH_Distribu City | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
113_13 DH_Distribu City | 9. 220 kV substation, capacity in the range of 500 MW
113_13 DH_Distribu City | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
113_13 DH_Distribu City | 4. Consolidated with statistics from Danish District Heating Association 2020
113_13 DH_Distribu City | A. The loss is per trench km of transmission pipeline pair.
113_13 DH_Distribu City | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
113_13 DH_Distribu City | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
113_13 DH_Distribu City | 4. Consolidated with statistics from Danish District Heating Association 2020
113_13 DH_Distribu City | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
113_13 DH_Distribu City | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
113_13 DH_Distribu City | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
113_13 DH_Distribu City | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
113_13 DH_Distribu City | E. A paved area is assumed for the distribution network as well as for service lines.
113_13 DH_Distribu City | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
113_13 DH_Distribu City | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
113_13 DH_Distribu City | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
113_13 DH_Distribu City | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
113_13 DH_Distribu City | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
113_13 DH_Distribu City | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
113_13 DH_Distribu City | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
113_13 DH_Distribu City | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
113_14 DH_Distribu New area | 2. See [30], [31], [36], [42] in text chapter
113_14 DH_Distribu New area | 1. 2025 prices: adding 20% to price from source
113_14 DH_Distribu New area | 2. Low and high: minus/plus 30%
113_14 DH_Distribu New area | 3. Prices assumed to decrease linearly from 2030 to 2050
113_14 DH_Distribu New area | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
113_14 DH_Distribu New area | 5. Estimates, typical values.
113_14 DH_Distribu New area | 6. Estimates, based on stakeholder information
113_14 DH_Distribu New area | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
113_14 DH_Distribu New area | 6. Estimates, project specific, depending on e.g., length of cable
113_14 DH_Distribu New area | 7. Estimates, typical values (AC cables with compensation)
113_14 DH_Distribu New area | 2. HMN Naturgas
113_14 DH_Distribu New area | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
113_14 DH_Distribu New area | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
113_14 DH_Distribu New area | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
113_14 DH_Distribu New area | D. Includes enginering, tender, and construction.
113_14 DH_Distribu New area | 2. HMN Naturgas
113_14 DH_Distribu New area | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
113_14 DH_Distribu New area | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
113_14 DH_Distribu New area | 4. Consolidated with statistics from Danish District Heating Association 2020
113_14 DH_Distribu New area | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
113_14 DH_Distribu New area | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
113_14 DH_Distribu New area | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
113_14 DH_Distribu New area | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
113_14 DH_Distribu New area | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
113_14 DH_Distribu New area | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
113_14 DH_Distribu New area | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
113_14 DH_Distribu New area | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
113_14 DH_Distribu New area | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
113_14 DH_Distribu New area | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
113_14 DH_Distribu New area | K. Service lines above 100 kW are not relevant in the specific area type.
113_14 DH_Distribu New area | L. Single lines above 25 MW are not relevant in the specific area type.
113_14 DH_Distribu New area | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
113_14 DH_Distribu New area | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.
H2 70 | 2. See [30], [31], [36], [42] in text chapter
H2 70 | 1. Low and high: minus/plus 30%
H2 70 | 2. 2025 prices: adding 20% to price from source
H2 70 | 3. Prices assumed to decrease linearly from 2030 to 2050
H2 70 | References:. \n . \n <none>
H2 70 | References:. \n . \n <none>
H2 70 | 7. Estimates, (partly) based on stakeholder information
H2 70 | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
H2 70 | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
H2 70 | 9. 220 kV substation, capacity in the range of 500 MW
H2 70 | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
H2 70 | 4. Consolidated with statistics from Danish District Heating Association 2020
H2 70 | A. The loss is per trench km of transmission pipeline pair.
H2 70 | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
H2 70 | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
H2 70 | 4. Consolidated with statistics from Danish District Heating Association 2020
H2 70 | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
H2 70 | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
H2 70 | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
H2 70 | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
H2 70 | E. A paved area is assumed for the distribution network as well as for service lines.
H2 70 | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
H2 70 | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H2 70 | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
H2 70 | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
H2 70 | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
H2 70 | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
H2 70 | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
H2 70 | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
H2 140 | 2. See [30], [31], [36], [42] in text chapter
H2 140 | 1. 2025 prices: adding 20% to price from source
H2 140 | 2. Low and high: minus/plus 30%
H2 140 | 3. Prices assumed to decrease linearly from 2030 to 2050
H2 140 | A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on cost of booster compressor vs pipe material cost. \n Curently, the optimum seems to be: velosity (m/s)≈4.4*Q^0.1, dPdL(bar/km)≈1.28*Q^(-0.75), Q=energy flow (MW)
H2 140 | B. Energy to compress from 35 barg to 140 barg. This value can be lowered by only compress to curent operation pressure in transmission line using outtake from interstages compressors
H2 140 | C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
H2 140 | D. Installation cost is ~80% for small pipes and ~75% for large pipes
H2 140 | E. Fixed operation cost is per pipelength and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
H2 140 | E. Fixed operation cost is per pipelength and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
H2 140 | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
H2 140 | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
H2 140 | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
H2 140 | D. Includes enginering, tender, and construction.
H2 140 | 2. HMN Naturgas
H2 140 | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
H2 140 | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
H2 140 | 4. Consolidated with statistics from Danish District Heating Association 2020
H2 140 | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
H2 140 | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
H2 140 | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
H2 140 | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
H2 140 | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
H2 140 | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
H2 140 | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H2 140 | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
H2 140 | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
H2 140 | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
H2 140 | K. Service lines above 100 kW are not relevant in the specific area type.
H2 140 | L. Single lines above 25 MW are not relevant in the specific area type.
H2 140 | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
H2 140 | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.
NH3 | 2. See [30], [31], [36], [42] in text chapter
NH3 | 1. Low and high: minus/plus 30%
NH3 | 2. 2025 prices: adding 20% to price from source
NH3 | A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
NH3 | B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
NH3 | C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
NH3 | D. Position drilling is assumed to be able to reduce the installation cost. However, the factor is judged minor as increased safety may outrage this saving
NH3 | E. Fixed operation cost is only per pipelengt (i.e. is not divided with capacity) as size have a relatively little impact on maintenance cost. 1% of CAPEX is applied.
NH3 | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
NH3 | 9. 220 kV substation, capacity in the range of 500 MW
NH3 | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
NH3 | 4. Consolidated with statistics from Danish District Heating Association 2020
NH3 | A. The loss is per trench km of transmission pipeline pair.
NH3 | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
NH3 | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
NH3 | 4. Consolidated with statistics from Danish District Heating Association 2020
NH3 | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
NH3 | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
NH3 | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
NH3 | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
NH3 | E. A paved area is assumed for the distribution network as well as for service lines.
NH3 | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
NH3 | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
NH3 | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
NH3 | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
NH3 | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
NH3 | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
NH3 | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
NH3 | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
DME | 2. See [30], [31], [36], [42] in text chapter
DME | 1. 2025 prices: adding 20% to price from source
DME | 2. Low and high: minus/plus 30%
DME | A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
DME | B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
DME | C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
DME | D. Position drilling is assumed to be able to reduce the installation cost. However, the factor is judged minor as increased safety may outrage this saving
DME | E. Fixed operation cost is only per pipelengt (i.e. is not divided with capacity) as size have a relatively little impact on maintenance cost. 1% of CAPEX is applied.
DME | E. Fixed operation cost is per pipelength and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
DME | E. Fixed operation cost is per pipelength and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
DME | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
DME | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
DME | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
DME | D. Includes enginering, tender, and construction.
DME | 2. HMN Naturgas
DME | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
DME | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
DME | 4. Consolidated with statistics from Danish District Heating Association 2020
DME | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
DME | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
DME | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
DME | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
DME | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
DME | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
DME | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
DME | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
DME | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
DME | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
DME | K. Service lines above 100 kW are not relevant in the specific area type.
DME | L. Single lines above 25 MW are not relevant in the specific area type.
DME | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
DME | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.
TOLU | 2. See [30], [31], [36], [42] in text chapter
TOLU | 1. Low and high: minus/plus 30%
TOLU | 2. 2025 prices: adding 20% to price from source
TOLU | A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
TOLU | B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
TOLU | C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
TOLU | D. Position drilling is assumed to be able to reduce the installation cost. However, the factor is judged minor as increased safety may outrage this saving
TOLU | E. Fixed operation cost is only per pipelengt (i.e. is not divided with capacity) as size have a relatively little impact on maintenance cost. 1% of CAPEX is applied.
TOLU | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
TOLU | 9. 220 kV substation, capacity in the range of 500 MW
TOLU | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
TOLU | 4. Consolidated with statistics from Danish District Heating Association 2020
TOLU | A. The loss is per trench km of transmission pipeline pair.
TOLU | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
TOLU | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
TOLU | 4. Consolidated with statistics from Danish District Heating Association 2020
TOLU | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
TOLU | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
TOLU | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
TOLU | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
TOLU | E. A paved area is assumed for the distribution network as well as for service lines.
TOLU | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
TOLU | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
TOLU | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
TOLU | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
TOLU | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
TOLU | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
TOLU | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
TOLU | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
Road transport | 2. See [30], [31], [36], [42] in text chapter
Road transport | 1. 2025 prices: adding 20% to price from source
Road transport | 2. Low and high: minus/plus 30%
Road transport | A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
Road transport | B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
Road transport | C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
Road transport | 5. Network for Transport Measures (NTM) database, 2020
Road transport | A. Fuel for propulation based on 50-60 tonne truck with capacity of 45-50 m3. Myltiply tank volume with density to get transported mass (density is given in Table 1 except for CH2 which is between 25-42 kg/m3 depending on tank pressure). Tanker assumed full one way and empty return (except for to...
Road transport | B. Technical lifetime of truck (puller) will depend on the distance driven, 4-10 years. Lifetime trailer 10 years or more.
Road transport | C. Numbers based on LPG transport
Road transport | D. Numbers based on diesel transport, but the fuel concumption is based on full cargo tank on the round trip.
Road transport | E. Capital cost of truck is split into the fixed and variable cost based on relative time spend on loading/unloading and on driving.
Road transport | F. Cost is based on: CAPEX Truck + Tanker is 450-1000 k€ (LHC tank is the cheapest and CH2 the most expensive), 8000 h/year operation, 60 km/h average speed, fuel cost of 1.25 €/kg, fuel LHV=42.5 MJ/kg, Annual fixed O&M is 5% capital cost
Road transport | G. Improvements: Faster loading time, lower CAPEX, and longer distance per fuel. For CH2, also increased pressure in tank
Road transport | H. Fuel for propulation: \n For LHC, L20 and LH2: 19 MJ/km in 2020, 18 MJ/km in 2030 and 15 MJ/km in 2050\n For CH2: 24 MJ/km in 2020, 23 MJ/km in 2030 and 20 MJ/km in 2050
Road transport | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
Road transport | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
Road transport | 4. Consolidated with statistics from Danish District Heating Association 2020
Road transport | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
Road transport | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
Road transport | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
Road transport | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
Road transport | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
Road transport | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
Road transport | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
Road transport | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
Road transport | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
Road transport | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
Road transport | K. Service lines above 100 kW are not relevant in the specific area type.
Road transport | L. Single lines above 25 MW are not relevant in the specific area type.
Road transport | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
Road transport | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.
Ship Transport | 2. See [30], [31], [36], [42] in text chapter
Ship Transport | 1. Low and high: minus/plus 30%
Ship Transport | 3. Shipping CO₂-UK cost estimation study, 2018
Ship Transport | A. Energy based on fuel LHV which is approximated by: 0.023*Mcargo+1400 for L20 and LHC. For LH2 the weight of the cargo is much less (do to the low weight of H2) why the weight of the entire ship have been used instead
Ship Transport | B. Investment cost based on: Cost [€/t] = 4000-0.05*Mcargo, where Mcargo is design capacity of ship
Ship Transport | C. CAPEX of LPG carrier see https://www.seatrade-maritime.com/tankers/euronav-buys-another-scrubber-fitted-resale-vlcc-newbuild
Ship Transport | D. CAPEX of tanker see BRS group annual review 2019
Ship Transport | E. Fixed O&M is assumed to be ~5% of annual CAPEX
Ship Transport | F. It is assumed that the efficiency of the combustion engine is improved so it is 90% in 2030 and 70% in 2050 of the efficiency in 2020. \nThe 70% is based on the difference between the efficiency of a traditional combustion engine and a fuel cell engine.\nThe 90% is based on natural replacement...
Ship Transport | G. Assumed cost reduction after LH2 tanker is commercialized
Ship Transport | 9. 220 kV substation, capacity in the range of 500 MW
Ship Transport | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
Ship Transport | 4. Consolidated with statistics from Danish District Heating Association 2020
Ship Transport | A. The loss is per trench km of transmission pipeline pair.
Ship Transport | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
Ship Transport | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
Ship Transport | 4. Consolidated with statistics from Danish District Heating Association 2020
Ship Transport | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
Ship Transport | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
Ship Transport | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
Ship Transport | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
Ship Transport | E. A paved area is assumed for the distribution network as well as for service lines.
Ship Transport | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
Ship Transport | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
Ship Transport | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
Ship Transport | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
Ship Transport | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
Ship Transport | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
Ship Transport | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
Ship Transport | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.

## Ref
ws | description
111 1 el Main distri50-60kVcabl | 1. U.S. Energy Information Administration (http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3)
111 1 el Main distri50-60kVcabl | 2. energinet.dk (http://www.energinet.dk/DA/KLIMA-OG-MILJOE/Energinetdks-miljoepaavirkninger/Miljoepaavirkninger-ved-transport-af-el/Sider/Tab-i-elnettet.aspx)
111 1 el Main distri50-60kVcabl | 3. Svenska Kraftnät, Nätuvecklingsplan 2016 – 2025, Oktober 2015 (http://www.svk.se/siteassets/om-oss/rapporter/natutvecklingsplan-2016-2025.pdf)
111 1 el Main distri50-60kVcabl | 4. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
111 1 el Main distri50-60kVcabl | 5. Svenska Kraftnät, Technology (http://www.svk.se/en/grid-development/the-construction-process/technology/)
111 1 el Main distri50-60kVcabl | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
111 1 el Main distri50-60kVcabl | 7. PEX Guiden, Ericsson
111 1 el Main distri50-60kVcabl | 8. Standard value list for the Swedish Energy Markets Inspectorate (2015 value) (http://ei.se/sv/el/Elnat-och-natprisreglering/forhandsreglering-av-elnatstariffer-ar-2016-2019/dokument-elnatsreglering/normvardeslista-elnat-2016-2019/)
111 1 el Main distri50-60kVcabl | 9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 3 el distri suburban | 1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen [Statistics from Swedish utility companies) from 2014 [http://www.ei.se/sv/Publikationer/Arsrapporter/)
111 3 el distri suburban | 2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, [2001).
111 3 el distri suburban | 3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution [http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
111 3 el distri suburban | 4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
111 3 el distri suburban | 5. Sweco, Project data
111 3 el distri suburban | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
111 3 el distri suburban | 7. Swedish Energy Markets Inspectorate [http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 4 el distri city | 1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
111 4 el distri city | 2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
111 4 el distri city | 3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
111 4 el distri city | 4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
111 4 el distri city | 5. Sweco, Project data
111 4 el distri city | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
111 4 el distri city | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 5 el distri new area | 1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
111 5 el distri new area | 2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
111 5 el distri new area | 3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
111 5 el distri new area | 4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
111 5 el distri new area | 5. Sweco, Project data
111 5 el distri new area | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
111 5 el distri new area | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
111 6 el trans OH | 1. Netzentwicklungsplan Strom (German TSOs), version 2021
111 6 el trans OH | 2. See [30], [31], [36], [42] in text chapter
111 6 el trans OH | 3. See [50] in text chapter
111 7 el trans AC&DC cables | 1. Netzentwicklungsplan Strom (German TSOs), version 2023
111 7 el trans AC&DC cables | 2. See [30], [31], [36], [42] in text chapter
111 8 el substations | 1. Netzentwicklungsplan Strom (German TSOs), version 2023
111 8 el substations | 2. See [30], [31], [36], [42] in text chapter
111 9 el transformers | 1. Netzentwicklungsplan Strom (German TSOs), version 2021
111 9 el transformers | 2. See [30], [31], [36], [42] in text chapter
111 10 el compensation | 1. Netzentwicklungsplan Strom (German TSOs), version 2021
111 10 el compensation | 2. See [30], [31], [36], [42] in text chapter
112 6 gas Main distri line | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
112 6 gas Main distri line | 2. HMN Naturgas
112 7 gas Rural | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
112 7 gas Rural | 2. HMN Naturgas
112 8 gas Suburban | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
112 8 gas Suburban | 2. HMN Naturgas
112 9 gas City | 1. HMN Naturgas
112 1 gas New area | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
112 1 gas New area | 2. HMN Naturgas
113_11 DH transmission | 1. Based on Ramboll experience figures
113_11 DH transmission | 2. LOGSTOR A/S
113_11 DH transmission | 3. Consolidated with data from Danish District Heating Association
113_11 DH transmission | 4. Consolidated with statistics from Danish District Heating Association 2020
113_12 DH_Distribu Suburb | 1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
113_12 DH_Distribu Suburb | 2. Ramboll experience and technical data from LOGSTOR A/S
113_12 DH_Distribu Suburb | 3. Consolidated with data from Danish District Heating Association
113_12 DH_Distribu Suburb | 4. Consolidated with statistics from Danish District Heating Association 2020
113_13 DH_Distribu City | 1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
113_13 DH_Distribu City | 2. Ramboll experience and technical data from LOGSTOR A/S
113_13 DH_Distribu City | 3. Consolidated with data from Danish District Heating Association
113_13 DH_Distribu City | 4. Consolidated with statistics from Danish District Heating Association 2020
113_14 DH_Distribu New area | 1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
113_14 DH_Distribu New area | 2. Ramboll experience and technical data from LOGSTOR A/S
113_14 DH_Distribu New area | 3. Consolidated with data from Danish District Heating Association
113_14 DH_Distribu New area | 4. Consolidated with statistics from Danish District Heating Association 2020
NH3 | 1
NH3 | 2
DME | 1
DME | 2
TOLU | 1
TOLU | 2
Road transport | 1. Air Liquide A/S
Road transport | 2. Everfuel A/S
Road transport | 3. Give Svaergods A/S
Road transport | 4. Fjellerad Transport Aps
Road transport | 5. Network for Transport Measures (NTM) database, 2020
Ship Transport | 1. The Basics of the Tanker Shipping Market, Euronav, 2017
Ship Transport | 2. Torm annual report 2018
Ship Transport | 3. Shipping CO₂-UK cost estimation study, 2018

## 111 1 el Main distri50-60kVcabl
Technology | NOT updated in 2025 | Energy Transport Electricity Main distribution, electricity cables
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, lines 20-100 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, lines above 100 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, stations type 1 [%] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 | [A, B] | [1, 2, 3, 4]
| Energy losses, stations type 2 [%] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [A, B, S]
| Auxiliary electricity consumption [%] of energy transmitted | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [A, B, S] | 4
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 40 | 50 | C | 5
| Typical load profile [-] | 45% | 45% | 45% | 45% | 45% | 45% | 42.3% | 54% | D
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 5 | 1 | 5 | E
Financial data
| Investment costs; single line, 0-50 MW [€/MW/m] | 6.3802 | 6.3802 | 6.3802 | 6.3802 | 6.1061 | 6.7846 | 5.8438 | 7.2145 | [F, G] | [6, 7]
| Investment costs; single line, 50-100 MW [€/MW/m] | 4.1472 | 4.1472 | 4.1472 | 4.1472 | 3.969 | 4.41 | 3.7984 | 4.6894 | [H, G] | [6, 7]
| Investment costs; single line, 100-250 MW [€/MW/m] | 3.2965 | 3.2965 | 3.2965 | 3.2965 | 3.1548 | 3.5054 | 3.0193 | 3.7275 | [I, G] | [6, 7]
| Investment costs; single line, 250-500 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 6
| Investment costs; single line, 500-1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 7
| Investment costs; single line, above 1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 8
| Reinforcement costs [€/MW] | 16801.2889 | 16801.2889 | 16801.2889 | 16801.2889 | 17044.1948 | 17866.0323 | 17290.6125 | 18998.2513 | [K, O] | 6
| Investment costs; type 1 station [€/MW] | 80816.3266 | 80816.3266 | 80816.3266 | 80816.3266 | 81984.7345 | 85937.8768 | 83170.0348 | 91383.9937 | [L, O] | 8
| Investment costs; type 2 station [€/MW] | 4759.6563 | 4759.6563 | 4759.6563 | 4759.6563 | 4828.4694 | 5061.2886 | 4898.2773 | 5382.0363 | [M, O]
| Investments, percentage installation | 42% | 42% | 42% | 42% | 37.37% | 42% | 32.96% | 42% | P | 6
| Investments, percentage materials | 58% | 58% | 58% | 58% | 58% | 62.63% | 58% | 67.04% | P | 6
| Fixed O&M [€/MW/km/year] | 24.9898 | 26.2015 | 27.4719 | 28.8039 | 26.0952 | 26.5735 | 25.1642 | 26.5735 | Q | 9
| Variable O&M [€/MWh/km] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | R
Technology-specific data
References:
1. U.S. Energy Information Administration (http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3)
2. energinet.dk (http://www.energinet.dk/DA/KLIMA-OG-MILJOE/Energinetdks-miljoepaavirkninger/Miljoepaavirkninger-ved-transport-af-el/Sider/Tab-i-elnettet.aspx)
3. Svenska Kraftnät, Nätuvecklingsplan 2016 – 2025, Oktober 2015 (http://www.svk.se/siteassets/om-oss/rapporter/natutvecklingsplan-2016-2025.pdf)
4. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
5. Svenska Kraftnät, Technology (http://www.svk.se/en/grid-development/the-construction-process/technology/)
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. PEX Guiden, Ericsson
8. Standard value list for the Swedish Energy Markets Inspectorate (2015 value) (http://ei.se/sv/el/Elnat-och-natprisreglering/forhandsreglering-av-elnatstariffer-ar-2016-2019/dokument-elnatsreglering/normvardeslista-elnat-2016-2019/)
9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. Energy losses are estimated from total energy loss on transmission levels in the voltage range 20kV to 130 kV in Sweden. Transmission lines/cables accounts for approximately 60% of the losses and transformers accounts for approximately 40%.
B. Development of energy loss over time depends on several factors. Today, transmission losses typically range between 1% to 3% in Denmark. The variation in transmission losses depends mainly on the amount of power transfer to neighboring countries. The trend in Denmark is towards increasing transfer and thus increasing losses. The uncertainty span for 2020 mainly takes changes in power transfer into account, where the lower bound corresponds to a reduction of power transfer to a 1998 level, and the upper bound corresponds to a continued increase in losses stemming from increased power transfer. Technology development with introduction of e.g. super conducting transformers and super conducting power lines could lead to reduced losses on transmission level. Other factors, such as load control/optimization could also reduce losses in generators due to increased load factor. This technology development is not anticipated to have effect before 2020, but is possible in a second upgrade of electricity system in 2050.
C. Cable life length depends on material characteristics and the thermal loading of the cable. Increasing cable area and thus reducing cable temperature leads to longer life length. Today, up to 40 years are realistic life length of a cable with moderate thermal loading. Technological development on cable materials is anticipated to give an increase in cable life length. This in combination with low thermal loadings could give life length of up to 50 years in the future.
D. Load profile varies significantly between different stations and cables and a general figure is given. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 20%.
E. Construction time ranges normally from 1 to 2 years. In technically complex projects and for long cable stretches, the construction time increases and could stretch up to 5 years.
F. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2. For power range 0-50 MW the costs is calculated as the average cost of two cables types with cross section areas 240 mm2 and 630 mm2,, corresponding to power levels of 20-35 MW and 50-60 MW respectively. The cost per MV decreases with increasing power level. The interval 20-35 MW has a cost of 6,7 €/MW/m and the interval 50-60 MW a cost of 4,2 €/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9. Power level below 20MW is not considered for this voltage level.
G. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
H. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2.For power range 50-100 MW the costs is calculated as the average cost for three cables with cross section areas 630 mm2, 800mm2 and 1000 mm2, corresponding to power levels of 50-60 MW, 69 MW and 76 MW respectively. The cost per MV decreases with increasing power level. The power interval 50-60 MW has a cost of 4,2 €/MW/m, at power level of 69 MW the cost is 3,6 €/MW/m and at the power level 76 the cost is 3,4 €/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9.
I. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 60 kV. Cost is calculated as the average cost between dense populated areas and city areas. Adjusting factors for each area are: dense populated: 0,94, and city: 1,06. For power range 100-250 MW the costs is given for a cable with cross section area of 1200 mm2, corresponding to a power level of 100 MW. Power levels above 100 MW are not considered for this voltage level.
J. Power levels above 100 MW are normally transported at higher voltage levels. In cases where it is motivated to transport higher power levels at 50/60 kV, this is done in parallele cable budles in the same shaft. The cost of two parallel cables can be calculated as the double cost of one cable reduced with 60 800 EUR per kilometer.
K. Reinforcement costs depends on where bottlenecks are situated in the grid. Here the reinforcement cost is given for an upgrade of transformer capacity by 40 MVA. Reinforcement of line/cable capacity is in parity with the investment cost in described in row 18-20 and depends on power level and cable length.
L. Station cost is based on a 40 MW station with 2 x 20 MVA transformers (72/12 kV). Station cost depends on a number of factors, such as power rating, redundancy on transformers etc. Station cost have an almost linear relation to the power rating and following relation holds for the power span 20-126 MW: Station cost (EUR) = 16 000 (€/MW) x Power rating (MW) + 2 350 000 (EUR). Using a single transformer instead of two reduces the cost by a factor 0,86-0,87.
M. Station cost is based on average cost for capacity banks and inductor with a design voltage of 72 kV. It is assumed that the equipment is installed in a existing station.
O. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
P. The percentage of the investment cost allocated to material cost and installation cost varies depending on area type (rural or city) and power level. An average is given here. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
Q. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost multiplied by the average cost of cables per MW and km given in row 18 to 20. It should be noted that the O&M cost in distribution system mainly is attributed to stations since there is practically no maintenaince on cables. The O&M cost is assumed to be reduced over time by an annual factor of 1-1,8% due to increased efficiency. Upper uncertainty bounds for 2020 and 2050 corresponds to no efficiency increase in O&M and lower bounds corresponds to a continuous annual efficiency increase of 1,8%
R. Variable O&M cost is in very low for electric transmission systems and considered to be negligible
S. Energy losses and auxiliary electricity consumption can be considered negligible

## 111 2 el distri Rural
Technology | NOT updated in 2025 | Energy Transport Electricity Distribution, Rural
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 4.5 | 5.25 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D | [1, 5]
| - Residential | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D
| - Commercial | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] Rural | 183.9635 | 183.9635 | 183.9635 | 183.9635 | 165.5671 | 183.9635 | 140.0698 | 218.9165 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 557.2073 | 557.2073 | 557.2073 | 557.2073 | 501.4866 | 557.2073 | 451.3379 | 557.2073 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 1501.4823 | 1501.4823 | 1501.4823 | 1501.4823 | 1351.3341 | 1501.4823 | 1216.2006 | 1501.4823 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 1683.319 | 1683.319 | 1683.319 | 1683.319 | 1514.9871 | 1683.319 | 1363.4884 | 1683.319 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 3982.3308 | 3982.3308 | 3982.3308 | 3982.3308 | 3584.0977 | 3982.3308 | 3225.688 | 3982.3308 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 43.5983 | 43.5983 | 43.5983 | 43.5983 | 39.3448 | 43.5983 | 35.4103 | 43.5983 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 93.5768 | 93.5768 | 93.5768 | 93.5768 | 90.3867 | 93.5768 | 81.348 | 93.5768 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 11690.7197 | 12228.7863 | 11176.328 | 12228.7863 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 71777.6585 | 71777.6585 | 71777.6585 | 71777.6585 | 68619.4415 | 71777.6585 | 65600.1861 | 71777.6585 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 62% | 62% | 62% | 62% | 57.35% | 62% | 52.56% | 62% | K | 6
| Investments, percentage materials [cables] | 38% | 38% | 38% | 38% | 38% | 42.65% | 42% | 38% | K | 6
| Investments, percentage installation [stations] | 22% | 22% | 22% | 22% | 18.86% | 22% | 16.61% | 19% | K | 6
| Investments, percentage materials [stations] | 78% | 78% | 78% | 78% | 78% | 81% | 78% | 81% | K | 6
| Fixed O&M [€/MW/year] | 1730.968 | 1706.7345 | 1682.8402 | 1659.2804 | 1699.8106 | 1730.968 | 1639.1681 | 1730.968 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 19%.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacing the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeable
N. Auxiliary electricity consumption can be considered negligible

## 111 3 el distri suburban
Technology | NOT updated in 2025 | Energy Transport Electricity Distribution, Suburban
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 3 | 3 | 3 | 3 | 3 | 3 | 2.25 | 3 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D | [1, 5]
| - Residential | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| - Commercial | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] Suburban | 409.3985 | 409.3985 | 409.3985 | 409.3985 | 368.4586 | 409.3985 | 331.6128 | 517.8891 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 1527.0032 | 1527.0032 | 1527.0032 | 1527.0032 | 1374.3029 | 1527.0032 | 1236.8726 | 1527.0032 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 4286.4554 | 4286.4554 | 4286.4554 | 4286.4554 | 3857.8099 | 4286.4554 | 3472.0289 | 4286.4554 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 4511.8904 | 4511.8904 | 4511.8904 | 4511.8904 | 4060.7014 | 4511.8904 | 3654.6313 | 4511.8904 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 9640.5371 | 9640.5371 | 9640.5371 | 9640.5371 | 8676.4834 | 9640.5371 | 7808.835 | 9640.5371 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 79.753 | 79.753 | 79.753 | 79.753 | 69.1192 | 79.753 | 62.2073 | 79.753 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 85.0698 | 85.0698 | 85.0698 | 85.0698 | 74.4361 | 85.0698 | 66.9925 | 85.0698 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 136.1117 | 136.1117 | 136.1117 | 136.1117 | 125.478 | 136.1117 | 112.9302 | 136.1117 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 11690.7197 | 12228.7863 | 11176.328 | 12228.7863 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 40408.1633 | 40408.1633 | 40408.1633 | 40408.1633 | 38630.2041 | 40408.1633 | 36930.4751 | 40408.1633 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 80% | 80% | 80% | 80% | 78% | 80% | 78% | 80% | K | 6
| Investments, percentage materials [cables] | 20% | 20% | 20% | 20% | 22% | 20% | 22% | 20% | K | 6
| Investments, percentage installation [stations] | 14% | 14% | 14% | 14% | 13% | 14% | 13% | 14% | K | 6
| Investments, percentage materials [stations] | 86% | 86% | 86% | 86% | 87% | 86% | 87% | 86% | K | 6
| Fixed O&M [€/MW/year] | 2851.2624 | 2811.3448 | 2771.9859 | 2733.1781 | 2799.9397 | 2851.2624 | 2700.0491 | 2851.2624 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen [Statistics from Swedish utility companies) from 2014 [http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, [2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution [http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate [http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference [1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference [1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 26%.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level [a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area [power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level [a decrease by 17,6 %), this will decrease the installation costs.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N. Auxiliary electricity consumption can be considered negligible

## 111 4 el distri city
Technology | NOT updated in 2025 | Energy Transport Electricity Distribution, City
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 1.5 | 2.25 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D | [1, 5]
| - Residential | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D
| - Commercial | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] City | 388.131 | 388.131 | 388.131 | 388.131 | 371.4552 | 412.728 | 334.166 | 531.0492 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 2285.188 | 2285.188 | 2285.188 | 2285.188 | 2187.0059 | 2285.188 | 2093.0422 | 2285.188 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 5974.0279 | 5974.0279 | 5974.0279 | 5974.0279 | 5717.3565 | 5974.0279 | 5471.7128 | 5974.0279 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 6139.9141 | 6139.9141 | 6139.9141 | 6139.9141 | 5876.1154 | 6139.9141 | 5623.6507 | 6139.9141 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 12899.7744 | 12899.7744 | 12899.7744 | 12899.7744 | 12345.5414 | 12899.7744 | 11815.1207 | 12899.7744 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 122.2879 | 122.2879 | 122.2879 | 122.2879 | 106.3373 | 122.2879 | 101.7685 | 122.2879 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 127.6047 | 127.6047 | 127.6047 | 127.6047 | 110.5908 | 127.6047 | 105.8393 | 127.6047 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 179.71 | 179.71 | 179.71 | 179.71 | 163.7594 | 179.71 | 156.7235 | 179.71 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 12431.5923 | 13003.7577 | 12637.7618 | 13003.7577 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 40408.1633 | 40408.1633 | 40408.1633 | 40408.1633 | 41078.3051 | 42968.9384 | 41759.5608 | 45691.9968 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 86% | 86% | 86% | 86% | N/A | N/A | N/A | N/A | K | 6
| Investments, percentage materials [cables] | 14% | 14% | 14% | 14% | N/A | N/A | N/A | N/A | K | 6
| Investments, percentage installation [stations] | 5% | 5% | 5% | 5% | 4% | 5% | 4% | 5% | K | 6
| Investments, percentage materials [stations] | 95% | 95% | 95% | 95% | 96% | 95% | 96% | 95% | K | 6
| Fixed O&M [€/MW/year] | 3240.4576 | 3397.5728 | 3562.3058 | 3735.026 | 3383.7895 | 3445.8142 | 3263.0694 | 3445.8142 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 21%.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decrease the installation costs.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintenance on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N. Auxiliary electricity consumption can be considered negligible

## 111 5 el distri new area
Technology | NOT updated in 2025 | Energy Transport Electricity Distribution, New developed areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 3 | 3 | 3 | 3 | 2.25 | 3 | 2.25 | 3 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D | [1, 5]
| - Residential | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| - Commercial | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] New developed area | 183.9635 | 183.9635 | 183.9635 | 183.9635 | 165.5671 | 183.9635 | 140.0698 | 218.9165 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 557.2073 | 557.2073 | 557.2073 | 557.2073 | 501.4866 | 557.2073 | 451.3379 | 557.2073 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 1501.4823 | 1501.4823 | 1501.4823 | 1501.4823 | 1351.3341 | 1501.4823 | 1216.2006 | 1501.4823 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 1683.319 | 1683.319 | 1683.319 | 1683.319 | 1514.9871 | 1683.319 | 1363.4884 | 1683.319 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 3982.3308 | 3982.3308 | 3982.3308 | 3982.3308 | 3584.0977 | 3982.3308 | 3225.688 | 3982.3308 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 43.5983 | 43.5983 | 43.5983 | 43.5983 | 39.3448 | 43.5983 | 35.4103 | 43.5983 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 93.5768 | 93.5768 | 93.5768 | 93.5768 | 90.3867 | 93.5768 | 81.348 | 93.5768 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 11690.7197 | 12228.7863 | 11176.328 | 12228.7863 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 40408.1633 | 40408.1633 | 40408.1633 | 40408.1633 | 38630.2041 | 40408.1633 | 36930.4751 | 40408.1633 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 80% | 80% | 80% | 80% | 78% | 80% | 78% | 80% | K | 6
| Investments, percentage materials [cables] | 20% | 20% | 20% | 20% | 22% | 20% | 22% | 20% | K | 6
| Investments, percentage installation [stations] | 14% | 14% | 14% | 14% | 13% | 14% | 13% | 14% | K | 6
| Investments, percentage materials [stations] | 86% | 86% | 86% | 86% | 87% | 86% | 87% | 86% | K | 6
| Fixed O&M [€/MW/year] | 1444.3554 | 1424.1344 | 1404.1965 | 1384.5378 | 1418.357 | 1444.3554 | 1367.7557 | 1444.3554 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an increase in peak load of 15 % without the use of smart grid leading to a corresponding decrease in load factor.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decreace the installation costs.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N. Auxiliary electricity consumption can be considered negligible

## 111 6 el trans OH
Technology |  |  | Overhead lines AC, Overhead lines DC
year | no data for 2020 in the new version |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, OH lines AC [%/100 km] at rated power |  | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | 5 | 3
| Energy losses, OH lines DC [%/100 km] at rated power |  | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | 5 | 3
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 4 | 2 | 4 | 6
Financial data
| Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity |  | 0.75 | 0.75 | 0.72 | 0.68 | 0.65 | 0.62 | 0.58 | 0.98 | 0.48 | 0.8 | 1,2,3,4,9,10 | 1
| Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity |  | 0.6 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.46 | 0.78 | 0.38 | 0.65 | 1,2,3,4,9 | 1
| Investments, percentage installation |  | 45% | 45% | 45% | 45% | 45% | 45% | 40% | 50% | 40% | 50% | 7
| Investments, percentage materials |  | 55% | 55% | 55% | 55% | 55% | 55% | 50% | 60% | 50% | 60% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
2. See [30], [31], [36], [42] in text chapter
3. See [50] in text chapter
Notes:
1. Low and high are minus/plus 30%
2. 2025 prices: after adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. Estimates, typical values (AC with compensation)
6. Estimates,project specific, depending on e.g., length of line
7. Estimates, based on stakeholder information
8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
9. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
10. Costs are including compensation (AC)

## 111 7 el trans AC&DC cables
Technology |  |  | Cables AC and DC, Onshore and Offshore
year | no data for 2020 in the new version |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, cables AC [%/100 km] at rated power |  | 5 | 5 | 5 | 5 | 5 | 5 | 2.5 | 7 | 2.5 | 7 | 7
| Energy losses, cables DC [%/100 km] at rated power |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 4 | 2 | 4 | 6
Financial data
| AC onshore cables [kEUR/km/MW], 500 MW capacity |  | 4.51 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 3.47 | 5.86 | 2.88 | 4.88 | 1,2,3,4,9,11,12 | 1
| AC offshore cables [kEUR/km/MW], 500 MW capacity |  | 4.51 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 3.47 | 5.86 | 2.88 | 4.88 | 1,2,3,4,9,11,12 | 1
| DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity |  | 4.07 | 4.07 | 3.91 | 3.74 | 3.57 | 3.4 | 3.13 | 5.29 | 2.62 | 4.42 | 1,2,3,4,10,11 | 1
| DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity |  | 3.22 | 3.22 | 3.09 | 2.95 | 2.82 | 2.68 | 2.48 | 4.19 | 2.06 | 3.48 | 1,2,3,4,10,11 | 1
| Investments, percentage installation |  | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 55% | 45% | 55% | 7
| Investments, percentage materials |  | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 55% | 45% | 55% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2023
2. See [30], [31], [36], [42] in text chapter
Notes:
1. Low and high are minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. Estimates, typical values.
6. Estimates, project specific, depending on e.g., length of cable
7. Estimates, typical values (AC cables with compensation)
8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
9. 220 kV with capacity of about 500 MW
10. 525 kV bipole with capacity 1500-2000 MW
11. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
12. Costs are including compensation (AC)

## 111 8 el substations
Technology |  |  | Substations AC and DC, Onshore and Offshore
year | no data for 2020 in the new version |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, substation [%] |  | 2 | 2 | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | 5
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 | 6
Financial data
| AC onshore substation [MEUR/MW], 500 MW capacity |  | 0.25 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.19 | 0.33 | 0.16 | 0.27 | 1,2,3,4,5,9 | 1
| AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity |  | 0.6 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.46 | 0.78 | 0.38 | 0.65 | 1,2,3,4,5,9 | 1
| DC onshore substation [MEUR/MW], 1500-2000 MW capacity |  | 0.32 | 0.32 | 0.3 | 0.29 | 0.28 | 0.27 | 0.25 | 0.42 | 0.21 | 0.35 | 1,2,3,4,6,10 | 1
| DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity |  | 0.75 | 0.75 | 0.72 | 0.69 | 0.66 | 0.63 | 0.58 | 0.98 | 0.48 | 0.82 | 1,2,3,4,6,10 | 1
| Investments, percentage installation |  | 45% | 45% | 45% | 45% | 45% | 45% | 40% | 50% | 40% | 50% | 7
| Investments, percentage materials |  | 55% | 55% | 55% | 55% | 55% | 55% | 50% | 60% | 50% | 60% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2023
2. See [30], [31], [36], [42] in text chapter
Notes:
1. 2025 prices: adding 20% to "year of source " prices
2. Low and high: minus/plus 30%
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. Estimates, typical values. AC substation includes transformers, switchgear, powerlines, compensation, control equipment etc.
6. Estimates, project specific, depends on size and location of station. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc
7. Estimates, based on stakeholder information
8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
9. 220 kV substation, capacity in the range of 500 MW
10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW

## 111 9 el transformers
Technology |  |  | Transformers
year | no data for 2020 in the new version |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, Transformer [%] |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 5
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | 5
Financial data
| 380/110 kV, 300 MVA [kEUR/MVA] |  | 20.8 | 20.8 | 19.9 | 19.1 | 18.2 | 17.3 | 16 | 27 | 13.31 | 22.49 | 1,2,3,4 | 1
| 380/220 kV, 600 MVA [kEUR/MVA] |  | 16 | 16 | 15.3 | 14.7 | 14 | 13.3 | 12.3 | 20.8 | 10.23 | 17.29 | 1,2,3,4 | 1
| 220/110 kV, 200 MVA [kEUR/MVA] |  | 20.9 | 20.9 | 20 | 19.2 | 18.3 | 17.4 | 16.1 | 27.2 | 13.38 | 22.62 | 1,2,3,4 | 1
| Investments, percentage installation |  | 20% | 20% | 20% | 20% | 20% | 20% | 15% | 25% | 15% | 25% | 6
| Investments, percentage materials |  | 80% | 80% | 80% | 80% | 80% | 80% | 75% | 85% | 75% | 85% | 6
| Additional costs | -: 7
| Fixed O&M [& of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
2. See [30], [31], [36], [42] in text chapter
Notes:
1. 2025 prices: adding 20% to price from source
2. Low and high: minus/plus 30%
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025
5. Estimates, typical values.
6. Estimates, based on stakeholder information
7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here

## 111 10 el compensation
Technology |  |  | Compensation
year | no data for 2020 in the new version |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 6
| Construction time [years] |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | 5
Financial data
| Capacitor bank [kEUR/MVAr] |  | 24 | 24 | 23 | 22 | 21 | 20 | 18 | 31 | 15 | 26 | 1,2,3,4 | 1
| SVC [kEUR/MVAr] |  | 60 | 60 | 58 | 55 | 53 | 50 | 46 | 78 | 38 | 65 | 1,2,3,4 | 1
| Reactor [kEUR/MVAr] |  | 25 | 25 | 24 | 23 | 22 | 21 | 19 | 33 | 16 | 27 | 1,2,3,4 | 1
| STATCOM [kEUR/MVAr] |  | 155 | 155 | 148 | 142 | 135 | 129 | 119 | 202 | 99 | 168 | 1,2,3,4 | 1
| Investments, percentage installation |  | 20% | 20% | 20% | 20% | 20% | 20% | 15% | 25% | 15% | 25% | 7
| Investments, percentage materials |  | 80% | 80% | 80% | 80% | 80% | 80% | 75% | 85% | 75% | 85% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
2. See [30], [31], [36], [42] in text chapter
Notes:
1. Low and high: minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025
5. Estimates, typical values.
6. Estimates, load of reactive power
7. Estimates, (partly) based on stakeholder information
7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here

## Input 111 6 - OH-lines
Go to Index | Go to relevant chapter
OH lines | [5 empty] | 2020 price level |  | Size of data sample | Reference | Comment
|  |  | Original price from source | Original, from source: Low | Original from, source: High | Pice from source | 2025
ACER, pwc, UIC, 2023 | Overhead line (MEUR/km)- AC | 110-150 kV 2 circuits | 0.32499 | 0.22437 | 0.39298 | 0.29053 |  | 3 | 1 | 1.2
|  | 220 kV 1 circuit | 0.41189 | 0.3033 | 0.54291 | 0.36822 |  | 7 | 1 | 1.2
|  | 220 kV 2 circuits | 0.5305 | 0.44169 | 0.67314 | 0.47425 |  | 21 | 1 | 1.2
|  | 330 kV 2 circuits | 0.5736 | 0.52186 | 0.5727 | 0.51278 |  | 5 | 1 | 1.2
|  | 380-400 kV 1 circuit | 0.46529 | 0.29774 | 0.60581 | 0.41595 |  | 18 | 1 | 1.2
|  | 400 kV 2 circuits | 1.261 | 0.5332 | 1.6349 | 1.1273 |  | 45 | 1 | 1.2
Overhead line (kEUR/km/MW)- AC
1100 | MW | 110-150 kV 2 circuits | 0.29545 | 0.20397 | 0.35725 | 0.26412 |  | 3 | 1 | 1.2
1100 | MW | 220 kV 1 circuit | 0.37444 | 0.27573 | 0.49355 | 0.33474 |  | 7 | 1 | 1.2
2200 | MW | 220 kV 2 circuits | 0.24114 | 0.20077 | 0.30597 | 0.21557 |  | 21 | 1 | 1.2
3300 | MW | 330 kV 2 circuits | 0.17382 | 0.15814 | 0.17355 | 0.15539 |  | 5 | 1 | 1.2
2000 | MW | 380-400 kV 1 circuit | 0.23264 | 0.14887 | 0.3029 | 0.20798 |  | 18 | 1 | 1.2
4000 | MW | 400 kV 2 circuits | 0.31524 | 0.1333 | 0.40872 | 0.28182 |  | 45 | 1 | 1.2
Netz, 2021 | Overhead line (MEUR/km)- AC | 380 kV, 2 circuits-AC | 2.5 |  |  | 2.4881 |  |  | 3 | 2
| 4000 MW OH line AC (kEUR/km/MW) | 381 kV, 2 circuits-AC | 0.625 |  |  | 0.62201 | 0.74642 |  | 3 | 2
Netz, 2021 | Overhead line (MEUR/km) DC | 2 circuits; 2 GW per circuit | 2 |  |  | 1.9904 |  |  | 3 | 2
| 4000 MW (kEUR/km/MW) DC | 2 circuits | 0.5 |  |  | 0.49761 | 0.59713 |  | 3 | 2
Balmorel model, 2022 | Overhead line - DC-kEUR/km/MW |  | 0.76 |  |  | 0.73786 |  |  | 2 | 3
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023
2. Balmorel Model assumptions
3. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment | 1. Low and high prices correspond to the 25 and 75 pencentiles of the data sample
2. 2025 prices are calculated by adding 20% to price from source
3. Balmorel 2022 data have already been lifted
OH lines, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
OH lines AC | kEUR/km/MW (4000 MW capacity) | 0.75 | 0.58 | 0.98 | 0.75 | 0.72 | 0.68 | 0.65 | 0.62 | 0.48 | 0.8 | 1 | 1,2,3,4
OH lines DC | kEUR/km/MW (4000 MW capacity) | 0.6 | 0.46 | 0.78 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.38 | 0.65 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment
1. Low and high are minus/plus 30%
2. 2025 prices: after adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050

## Input 111 7 - Cables
Go to Index | Go to relevant chapter
Cables
[7 empty] | 2020 price level |  | Size of data sample | Reference | Comment
|  |  |  | Original price from source | Original from source, low | Original from source , high | Price from source | 2025
ACER, pwc, UIC, 2023 | AC, Onshore underground cable | 110 - 150 kV 1 circuit | mEUR/km | 0.83066 | 0.43 | 0.64 | 0.74259 |  | 14 | 1 | 1
|  | 110 - 150 kV 2 circuits | mEUR/km | 2.2321 | 0.85 | 3.06 | 1.9954 |  | 4 | 1 | 1
|  | 220 - 225 kV 1 circuit | mEUR/km | 1.7784 | 1.23 | 2.11 | 1.5898 |  | 16 | 1 | 1
|  | 220 - 225 kV 2 circuits | mEUR/km | 4.4015 | 4.23 | 4.56 | 3.9349 |  | 4 | 1 | 1
|  | 300 - 500 kV 1 circuit | mEUR/km | 1.309 | 1.05 | 1.39 | 1.1702 |  | 4 | 1 | 1
280 | MW | 110 - 150 kV 1 circuit | kEUR/km/MW | 2.9666 | 1.5357 | 2.2857 | 2.6521 |  | 14 | 1 | 1
560 | MW | 110 - 150 kV 2 circuits | kEUR/km/MW | 3.9858 | 1.5179 | 5.4643 | 3.5632 |  | 4 | 1 | 1
560 | MW | 220 - 225 kV 1 circuit | kEUR/km/MW | 3.1756 | 2.1964 | 3.7679 | 2.8389 |  | 16 | 1 | 1
1120 | MW | 220 - 225 kV 2 circuits | kEUR/km/MW | 3.9299 | 3.7768 | 4.0714 | 3.5133 |  | 4 | 1 | 1
1000 | MW | 300 - 500 kV 1 circuit | kEUR/km/MW | 1.309 | 1.05 | 1.39 | 1.1702 |  | 4 | 1 | 1
Netz, 2023 prices | AC, 220 kV cable system, onshore |  | mEUR/km | 2.1 | [5 empty] | 5
| AC, 220 kV cable system, onshore | 500 MW | kEUR/km/MW | 4.2 |  |  | 3.7547 | 4.5056 |  | 5 | 2.3
AC Offshore cable
NETZ, 2021 prices | AC cable system 220 kV (offshore) Baltic Sea |  | mEUR/km | 2.9 |  |  | 2.8861 |  |  | 2
NETZ, 2023 prices | AC cable system 220 kV (offshore) Baltic Sea |  | mEUR/km | 2.1 |  |  | 1.8773 |  |  | 5
NETZ, 2023 prices | AC cable system 220 kV (offshore) Baltic Sea | 500 MW | kEUR/km/MW | 4.2 |  |  | 3.7547 | 4.5056 |  | 5 | 2.3
NETZ, 2021 prices | AC cable system 155 kV (offshore) Nord Sea |  | mEUR/km | 1.5 |  |  | 1.4928 |  |  | 2
ACER, pwc, UIC, 2023 | AC Offshore cable (132-380 kV) |  | mEUR/km | 2.0065 |  |  | 1.7938 |  | 9 | 1
Balmorel, 2022 prices | AC Offshore cable |  | kEUR/km/MW | 1.96 |  |  | 1.9023 |  |  | 3
NETZ, 2021 prices | DC onshore cable, 525 kV Nord Sea |  | mEUR/km | 6.5 |  |  | 6.4689 |  |  | 2
NETZ, 2023 prices | DC onshore cable, 525 kV Nord Sea and Baltic Sea |  | mEUR/km | 7.6 |  |  | 6.7942 |  |  | 5
NETZ, 2023 prices | DC cable system 525 kV (onshore) (bipole) | 2000 MW | kEUR/km/MW) | 3.8 |  |  | 3.4 | 4.07 |  | 5 | 2.4
Balmorel, 2022 prices | DC onshore cables |  | kEUR/(km*MW) | 1.7386 |  |  | 1.6875 |  |  | 3
ACER 2023 prices | DC offshore cable (300-500 kV) |  | mEUR/km | 1.1084 |  |  | 0.99092 |  | 6 | 1
| Offshore transmission cable, 150-320 kV (AC?, DC?- unclear) |  | mEUR/km | 3.2893 |  |  | 2.9406 |  | 7 | 1
NETZ 2021 prices | DC offshore cable system, 525 kV Nord Sea |  | mEUR/km | 4 |  |  | 3.9809 |  |  | 2
NETZ 2023 prices | DC offshore cable system, 525 kV Nord Sea and Baltic Sea |  | mEUR/km | 6 |  |  | 5.3638 |  |  | 5
NETZ 2023 prices | DC offshore cable system, 525 kV (bipole) | 2000 MW | kEUR/km/MW | 3 |  |  | 2.68 | 3.22 |  | 5 | 2.4
NETZ 2021 prices | DC offshore cable system, 525 kV Nord Sea and Baltic Sea |  | mEUR/km | 2 |  |  | 1.9904 |  |  | 2
2024 ENTSO-E planning prices | DC offshore cables |  | kEUR/(km*MW) | 1.618 |  |  | 1.4038 |  |  | 4
Tyndp 2022-project promoters (2022 prices) | DC offshore cables |  | kEUR/(km*MW) | 1.7 |  |  | 1.65 |  |  | 6
DNV2021 prices | DC offshore cables
| 0,5 GW 525 kV Cable |  | mEUR/km | 1.64 |  |  | 1.6322 |  |  | 7
| 1 GW 525 kV Cable |  | mEUR/km | 1.89 |  |  | 1.881 |  |  | 7
| 1,5 GW 525 kV Cable |  | mEUR/km | 2.14 |  |  | 2.1298 |  |  | 7
| 2 GW 525 kV cable |  | mEUR/km | 2.47 |  |  | 2.4582 |  |  | 7
DNV2021 prices | DC offshore cables
| 0,5 GW 525 kV Cable |  | kEUR/km/MW | 3.28 |  |  | 3.28 |  |  | 7
| 1 GW 525 kV Cable |  | kEUR/km/MW | 1.89 |  |  | 1.89 |  |  | 7
| 1,5 GW 525 kV Cable |  | kEUR/km/MW | 1.4267 |  |  | 1.4267 |  |  | 7
| 2 GW 525 kV cable |  | kEUR/km/MW | 1.235 |  |  | 1.235 |  |  | 7
Balmorel 2022 prices | DC offshore cables |  | kEUR/(km*MW) | 2.1272 |  |  | 2.0646 |  |  | 3
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023, https://www.acer.europa.eu/sites/default/files/documents/Publications/UIC_report_2023.pdf
2. Netzentwicklungsplan Strom (German TSOs), version 2021
3. Balmorel model data
4. ENTSO-E planning prices for TYNDP 2024
5. Netzentwicklungsplan Strom (German TSOs), version 2023
6. TYNDP 2022 project sheets (from project promoters)
7. Screening of possible hub concepts to integrate offshore wind capacity in the North Sea, DNV for DEA, 2021
Comments | 1. Low and High values are 25 and 75 percentiles of the sample
2. Shown 2025 prices estimated by adding 20 % to price from source
3. 220 kV with capacity of about 500 MW
4. 525 kV bipole with capacity 1500-2000 MW
Cables, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
AC onshore cables | kEUR/km/MW (500 MW capacity) | 4.51 | 3.47 | 5.86 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 2.88 | 4.88 | 1 | 1,2,3,4
AC offshore cables | kEUR/km/MW (500 MW capacity) | 4.51 | 3.47 | 5.86 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 2.88 | 4.88 | 1 | 1,2,3,4
DC onshore cables | kEUR/km/MW (1500-2000 MW capacity) | 4.07 | 3.13 | 5.29 | 4.07 | 3.91 | 3.74 | 3.57 | 3.4 | 2.62 | 4.42 | 1 | 1,2,3,4
DC offshore cables | kEUR/km/MW (1500-2000 MW capacity) | 3.22 | 2.48 | 4.19 | 3.22 | 3.09 | 2.95 | 2.82 | 2.68 | 2.06 | 3.48 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2023
Comment
1. Low and high are minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050

## Input 111 8 - Substations
Go to Index | Go to relevant chapter
Substations | [6 empty] | 2020 price level
|  |  |  | Original price from source | Original, low | Original, high | Price from source | 2025 | Size of data sample | Reference | Comment
ACER, 2023 prices | Onshore AC substation | 0-5 bays, all | mEUR/asset | 5.307 | 2.2 | 6.7 | 4.7443 |  | 77 | 1 | 1
|  | New/AIS/maximum 5 bays |  | 11.7127 | 3.59 | 16.91 | 10.4708 |  | 24 | 1
|  | New/GIS/maximum 5 bays |  | 13.619 | 5.4 | 15.99 | 12.175 |  | 8 | 1
|  | Refurbishment or Upgrade/AIS/maximum 5 bays |  | 3.4011 | 2.12 | 4.3 | 3.0405 |  | 28 | 1
|  | Refurbishment or Upgrade/GIS/maximum 5 bays |  | 4.4476 | 1 | 6.4 | 3.976 |  | 13 | 1
|  | 6-9 bays, all |  | 12.586 | 7.88 | 16.41 | 11.2516 |  | 62 | 1
|  | New/AIS/from 6 to 9 bays |  | 12.1413 | 8.18 | 16.68 | 10.854 |  | 24 | 1
|  | New/GIS/from 6 to 9 bays |  | 9.8208 | 7.82 | 11.53 | 8.7795 |  | 20 | 1
|  | Refurbishment or Upgrade/AIS/from 6 to 9 bays |  | 15.3779 | 6.81 | 23.44 | 13.7474 |  | 14 | 1
|  | 10-60 bays, all |  | 29.845 | 19.26 | 40.33 | 26.6807 |  | 23 | 1
|  | 10-60 bays , New |  | 43.572 | 22.72 | 58.86 | 38.9523 |  | 13 | 1
|  | 10-60 bays Refurbishment/upgrade |  | 29.8453 | 20.88 | 41.92 | 26.681 |  | 10 | 1
ACER, 2023 prices | Onshore AC substation | All | kEUR/kV | 31.248 | 16.683 | 43.45 | 27.9349 |  | 118 | 1 | 3
|  | AIS New |  | 31.72 | 18.52 | 43.62 | 28.3569 |  | 48 | 1 | 4
|  | AIS updated/Refurbished |  | 27.566 | 12.33 | 45.26 | 24.6433 |  | 33 | 1
|  | GIS New |  | 35.105 | 27.68 | 42.31 | 31.383 |  | 26 | 1 | 5
ACER, 2023 prices | Onshore AC substation | All | kEUR/MVA | 68.823 | 37.58 | 93.13 | 61.526 |  | 44 | 1 | 2
|  | AIS New |  | 65.884 | 43.41 | 81.89 | 58.8986 |  | 19 | 1
|  | AIS updated/Refurbished |  | 50.028 | 23.46 | 70.73 | 44.7238 |  | 16 | 1
|  | GIS New |  | 123.678 | 93.48 | 133.74 | 110.565 |  | 8 | 1
ACER, 2023 prices | Onshore AC substation | 220-275 kV | mEUR/bay | 1.206 | 0.84 | 1.52 | 1.0781 |  | 48 | 1
|  | 300-330 kV |  | 1.21 | 1.05 | 1.37 | 1.0817 |  | 4 | 1
|  | 380-400 kV |  | 3.382 | 1.15 | 5.24 | 3.0234 |  | 56 | 1
Netz, 2023 | AC onshore substation, 220 kV |  | mEUR/MW | 0.24 |  |  | 0.21455 | 0.25 |  | 4 | 7.8
ACER, 2023 prices | AC Offshore substation |  | mEUR/asset | 133.0696 | 104.73 | 154.83 | 118.9608 |  | 6 | 1
Netz, 2023 | AC offshore substation, 220 kV (with platform) |  | mEUR/MW | 0.56 |  |  | 0.50063 | 0.6 |  | 4 | 7.8
NETZ, 2021 prices | AC (Offshore +Onshore station)/2 | Baltic Sea | mEUR/MW | 0.35 |  |  | 0.34833 |  |  | 2 | 6
NETZ, 2023 prices | AC (Offshore +Onshore station)/2 | 220 kV, AC, Baltic SEA | mEUR/MW | 0.4 |  |  | 0.35759 |  |  | 4 | 6
NETZ, 2021 prices | DC (offshore +onshore station)/2, 320 kV (with AC/DC converter ) | North Sea | mEUR/MW | 0.5 |  |  | 0.49761 |  |  | 2 | 6 | -
NETZ, 2021 prices | DC (onshore +offshore station)/2, 525 kV (with AC/DC converter) | North Sea | mEUR/MW | 0.38 |  |  | 0.37818 |  |  | 2 | 6
NETZ, 2023 prices | DC onshore 525 kV station with converter (AC/DC) | North Sea and Baltic Sea | mEUR/MW | 0.3 |  |  | 0.26819 | 0.32 |  | 4 | 7.9
NETZ, 2023 prices | DC offshore station 525 kV with converter (AC/DC), incl. platform | North Sea and Baltic Sea | mEUR/MW | 0.7 |  |  | 0.62578 | 0.75 |  | 4 | 7.9
ENTSO-E-planning prices 2024 | Onshore DC station with converter (AC/DC) |  | mEUR/MW | 0.25 |  |  | 0.22 |  |  | 5
Tyndp 2022-project promoters | Onshore DC station with converter (AC/DC) |  | mEUR/MW | 0.15 |  |  | 0.14 |  |  | 6
DNV 2021 prices | Onshore DC station with converter (AC/DC) | 1 GW, 525 kV | mEUR/MW | 0.18 |  |  | 0.18 |  |  | 7
Balmorel 2022 prices | One DC/AC substation |  | mEUR/MW | 0.23547 |  |  | 0.22855 |  |  | 3
| Offshore platform AC (no substation) |  | mEUR/MW | 0.1523 |  |  | 0.14782 |  |  | 3
| Offshore platform DC (no substation) |  | mEUR/MW | 0.46813 |  |  | 0.45437 |  |  | 3
Comments
1. Substation bay: A set of equipment which connects a circuit into a substation.
2. MVA: Mega Volt Ampere measures the size of transformers/substations
3. kV is busbar rating
4. AIS: Air insulated substation (typical open air station).
5.GIS: In a gas insulated substation (GIS) the major conducting structures are contained within a sealed environment with a dielectric gas (SF6)
6.Half of one offshore + one onshore station
7. Prices for 2025 by adding 20% to price from source
8. 220 kV substation, capacity in the range of 500 MW
9. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023, https://www.acer.europa.eu/sites/default/files/documents/Publications/UIC_report_2023.pdf
2. Netzentwicklungsplan Strom (German TSOs), version 2021
3. Balmorel model data
4. Netzentwicklungsplan Strom (German TSOs), version 2023
5. ENTSO-E planning prices for TYNDP 2024
6. TYNDP 2022 project sheets (from project promoters)
7. Screening of possible hub concepts to integrate offshore wind capacity in the North Sea, DNV for DEA, 2021
Substations, 2020 price level
|  | Price from source | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
AC onshore substation | MEUR/MW (500 MW capacity) | 0.21 | 0.25 | 0.19 | 0.33 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.16 | 0.27 | 1 | 1,2,3,4,5
AC offshore substation, incl. platform | MEUR/MW (500 MW capacity) | 0.5 | 0.6 | 0.46 | 0.78 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.38 | 0.65 | 1 | 1,2,3,4,5
DC onshore substation with converter (AC/DC) | MEUR/MW (1500-2000 MW capacity) | 0.27 | 0.32 | 0.25 | 0.42 | 0.32 | 0.3 | 0.29 | 0.28 | 0.27 | 0.21 | 0.35 | 1 | 1,2,3,4,6
DC offshore substation with converter (AC/DC), incl. platform | MEUR/MW (1500-2000 MW capacity) | 0.63 | 0.75 | 0.58 | 0.98 | 0.75 | 0.72 | 0.69 | 0.66 | 0.63 | 0.48 | 0.82 | 1 | 1,2,3,4,6
References
1. Netzentwicklungsplan Strom (German TSOs), version 2023
Comment
1. 2025 prices: adding 20% to "year of source " prices
2. Low and high: minus/plus 30%
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. AC substation includes transformers, switchgear, powerlines, compensation, control equipment etc.
| 6. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc | DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc

## Input 111 9 - Transformers
Go to Index | Go to relevant chapter
Transformers | [5 empty] | 2020 price level
|  |  | Original price from source | Original low | Original high | Price from source | 2025 | Size of data sample | Reference | Comment
ACER, 2023 prices | 150/60 kV | mEUR/asset | 1.2123 | 1.1 | 1.27 | 1.0837 |  | 3 | 1 | 1
| 220/66 kV | mEUR/asset | 1.5361 | 1.34 | 1.72 | 1.3732 |  | 12 | 1 | 1
| 400/110 kV | mEUR/asset | 4.36 | 3.63 | 4.73 | 3.8977 |  | 15 | 1 | 1
| 400/220 kV | mEUR/asset | 4.6312 | 2.94 | 6.18 | 4.1402 |  | 7 | 1 | 1
| 150/60 kV | kEUR/MVA | 63.8 | 51.26 | 88.79 | 57.0356 |  | 3 | 1 | 1
| 220/66 kV | kEUR/MVA | 97.7 | 82.66 | 108.7 | 87.3413 |  | 12 | 1 | 1
| 400/110 kV | kEUR/MVA | 76.8 | 57.39 | 92.83 | 68.6573 |  | 15 | 1 | 1
| 400/220 kV | kEUR/MVA | 28.2 | 22.75 | 34.46 | 25.2101 |  | 7 | 1 | 1
DNV, 2021 prices | 210/30 kV, 700 MVA | mEUR/asset | 7.5 |  |  | 7.4642 |  |  | 2
| 210/30 kV, 500 MVA | mEUR/asset | 5.1 |  |  | 5.0756 |  |  | 2
| 210/30 kV, 700 MVA | kEUR/MVA | 10.7143 |  |  | 10.6631 |  |  | 2
| 210/30 kV, 500 MVA | kEUR/MVA | 10.2 |  |  | 10.1513 |  |  | 2
NETZ, 2021 prices
| 380/110 kV, 300 MVA | kEUR/MVA | 17.3333 |  |  | 17.2505 | 20.8 |  | 3 | 2
| 380/220 kV, 600 MVA | kEUR/MVA | 13.3333 |  |  | 13.2696 | 16 |  | 3 | 2
| 220/110 kV, 200 MVA | kEUR/MVA | 17.5 |  |  | 17.4164 | 20.9 |  | 3 | 2
Comments
1. Low and high are the 25 and 75 percentiles of the sample
2. 2025 prices obtained by adding 20% to price from source
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023
2. Screening of possible hub concepts to integrate offshore wind capacity in the North Sea, DNV for DEA, 2021
3. Netzentwicklungsplan Strom (German TSOs), version 2021
Transformers, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
380/110 kV, 300 MVA | kEUR/MVA | 20.8 | 16 | 27 | 20.8 | 19.9 | 19.1 | 18.2 | 17.3 | 13.31 | 22.49 | 1 | 1,2,3,4
380/220 kV, 600 MVA | kEUR/MVA | 16 | 12.3 | 20.8 | 16 | 15.3 | 14.7 | 14 | 13.3 | 10.23 | 17.29 | 1 | 1,2,3,4
220/110 kV, 200 MVA | kEUR/MVA | 20.9 | 16.1 | 27.2 | 20.9 | 20 | 19.2 | 18.3 | 17.4 | 13.38 | 22.62 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment
1. 2025 prices: adding 20% to price from source
2. Low and high: minus/plus 30%
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025

## Input 111 10 - Compensation
Go to Index | Go to relevant chapter
Compensation | Year of source: 2022 prices (price level 2020)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV | Reference | Comment
| Reactor (kEUR/MVAr) | 13.4929 | 13.4929 | 13.4929 | 13.4929 | 13.4929 | 13.4929 | 20.7682 | 29.9985 | 1 | 1,2,3
| Capacitor bank (kEUR/MVAr) | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 1 | 1,2,3
| SVC, Static VAr compensator (kEUR/MVAr) | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 1 | 1,2,3
| STATCOM (kEUR/MVAr) | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 1 | 1,2,3
Comments
1. MVAr: MVA reactive power
2. Unit costs include all material, shipping, foundation, and installation costs, taxes (not specified) and contingency
3. Original prices in 2022 US$: exchange rate in 2022 is 0,951 EUR/$;
References
1. Transmission Cost Estimation Guide For MTEP22, April 2022 (DRAFT)
Compensation | 2025 prices (price level 2020)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV | Reference | Comment
| Reactor (kEUR/MVAr) | 16.1915 | 16.1915 | 16.1915 | 16.1915 | 16.1915 | 16.1915 | 24.9219 | 35.9983 | 1 | 1,2,3,4
| Capacitor bank (kEUR/MVAr) | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 1 | 1,2,3,4
| SVC, Static VAr compensator (kEUR/MVAr) | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 1 | 1,2,3,4
| STATCOM (kEUR/MVAr) | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 1 | 1,2,3,4
References
1. Transmission Cost Estimation Guide For MTEP22, April 2022 (DRAFT)
Comments
1. MVAr: MVA reactive power
2. Unit costs include all material, shipping, foundation, and installation costs, taxes (not specified) and contingency
3. Original prices in 2022 US$: exchange rate in 2022 is 0,951 EUR/$;
4. Prices in 2025: addition of 20% to price from source
Compensation
Price level 2020
|  |  | Unit | Price, original from source | Price from source | 2025 | Reference | Comment
Netz,2021 | 380 kV, 100 MVAr | Capacitor bank | kEUR/MVAr | 20 | 19.9045 | 24 | 1 | 1
Netz,2021 | 380 kV, SVC | SVC | kEUR/MVAr | 50 | 49.7611 | 60 | 1 | 1
Netz,2021 | 380 kV, 100 MVAr | Reactor | kEUR/MVAr | 21 | 20.8997 | 25 | 1 | 1
Netz,2021 | 380 kV | STATCOM | kEUR/MVAr | 130 | 129.379 | 155 | 1 | 1
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment:
1. 2025 prices by adding 20% to price from source
Compensation, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
Capacitor bank | kEUR/MVAr | 24 | 18 | 31 | 24 | 23 | 22 | 21 | 20 | 15 | 26 | 1 | 1,2,3,4
SVC | kEUR/MVAr | 60 | 46 | 78 | 60 | 58 | 55 | 53 | 50 | 38 | 65 | 1 | 1,2,3,4
Reactor | kEUR/MVAr | 25 | 19 | 33 | 25 | 24 | 23 | 22 | 21 | 16 | 27 | 1 | 1,2,3,4
STATCOM | kEUR/MVAr | 155 | 119 | 202 | 155 | 148 | 142 | 135 | 129 | 99 | 168 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment
1. Low and high: minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025

## 112 6 gas Main distri line
Technology |  | Energy Transport, Natural Gas Main distribution line
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A | 1
| Energy losses, lines 20-100 MW [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A
| Energy losses, lines above 100 MW [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A
Energy losses, stations type 1 [%] | bar: Est to -
| Energy losses, stations type 2 [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.12 | 0 | 0.12 | C | 2
| Auxiliary electricity consumption [%] of energy transmitted | 0.005 | 0.005 | 0.005 | 0.005 | 0.00425 | 0.00575 | 0.00425 | 0.00575 |  | 2
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
| Typical load profile [-] | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.4 | 0.05 | 0.4 |  | 2
| Construction time [years] | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.7 | 1.5 | D | 2
Financial data
| Investment costs; single line, 0-50 MW [€/MW/m] | 11.4844 | 11.4844 | 11.4844 | 11.4844 | 9.1875 | 13.7813 | 9.1875 | 13.7813 | [E, F] | 2
| Investment costs; single line, 50-100 MW [€/MW/m] | 4.4662 | 4.4662 | 4.4662 | 4.4662 | 3.5729 | 5.3594 | 3.5729 | 5.3594 | [E, G] | 2
| Investment costs; single line, 100-250 MW [€/MW/m] | 2.382 | 2.382 | 2.382 | 2.382 | 1.9056 | 2.8583 | 1.9056 | 2.8583 | [E, G] | 2
| Investment costs; single line, 250-500 MW [€/MW/m] | 1.2441 | 1.2441 | 1.2441 | 1.2441 | 0.99532 | 1.493 | 0.99532 | 1.493 | [E, G] | 2
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.72309 | 0.72309 | 0.72309 | 0.72309 | 0.57847 | 0.86771 | 0.57847 | 0.86771 | [E, G] | 1
Investment costs; single line, above 1000 MW [€/MW/m] | bar: Est to -
Reinforcement costs [€/MW] | bar: Est to -
| Investment costs; type 1 station [€/MW] | - | - | - | - | - | - | - | - | [B, J]
| Investment costs; type 2 station [€/MW] | 28711.0634 | 28711.0634 | 28711.0634 | 28711.0634 | 7443.609 | 47851.7723 | 0 | 0 | [C, K] | 2
| Investments, percentage installation | 75% | 75% | 75% | 75% | 65% | 85% | 65% | 85% | 0 | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 15% | 35% | 15% | 35% | 0 | 2
| Fixed O&M [€/MW/km/year] | 0.12865 | 0.12865 | 0.12865 | 0.12865 | 0.10292 | 0.15438 | 0.10292 | 0.15438 | 0 | 2
| Variable O&M [€/MWh/km] | 1.1968e-05 | 1.1968e-05 | 1.1968e-05 | 1.1968e-05 | 9.5743e-06 | 1.4361e-05 | 9.5743e-06 | 1.4361e-05 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
D. Includes enginering, tender, and construction.
E. Rates include VVM review, landowner compensation and archaeological screening. Based on 20 km, of which 8 % is based on drilling.
F. Data given is for a 50 MW capacity
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H. Not possible to give general numbers. Depends on kind of reinforcement. Can be calculated based on the other numbers given.
I. Capacity not relevant-too high
J. Type 1 MR stations supplying the transmission system level 2-not part of the scope
K. Type 1 MR stations supplying the transmission system level 2 .The stated costs are the average cost for a 40/4 bar MR station where reheating after expansion is required and a 19/4 bar MR station where reheating is not necessary. The cost is only modestly size dependent. A 40/4 bar station capacity of 10.000 m3/h is 20 % higher than a similar station with a capacity of 5.000 m3/h.

## 112 7 gas Rural
Technology |  | Energy Transport Natural Gas Distribution, New distribution in existing rual areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
Energy losses, stations [%] | bar: Est to -
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
Typical load profile [-] | bar: -
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | Est: N/A; Est: N/A; Est: N/A; Est: N/A; -: D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs [€/MWh/year], Rural | 148.8722 | 148.8722 | 148.8722 | 148.8722 | 138.2385 | 159.5059 | 138.2385 | 159.5059 | 0 | 2
| Investment costs; service line, 0-20 kW [€/unit] | 1701.3963 | 1701.3963 | 1701.3963 | 1701.3963 | 1488.7218 | 1914.0709 | 1488.7218 | 1914.0709 | 0 | 2
Investment costs; service line, 20-50 kW [€/unit] | bar: Est to -
Investment costs; service line, 50-100 kW [€/unit] | bar: Est to -
Investment costs; service line, above 100 kW [€/unit] | bar: Est to -
| Investment costs; single line, 0-50 kW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 50-250 kW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 100-250 kW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 250 kW-1 MW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 1 MW-5 MW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | G
| Investment costs; single line, 5 MW-25 MW [€/m] | 72.6638 | 72.6638 | 72.6638 | 72.6638 | 65.3974 | 79.9302 | 65.3974 | 79.9302 | G
| Investment costs; single line, 25 MW-100 MW [€/m] | - | - | - | - | - | - | - | - | 0
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 2
| Fixed O&M [€/MW/year] | 797.5295 | 797.5295 | 797.5295 | 797.5295 | 638.0236 | 957.0354 | 638.0236 | 957.0354 | 0 | 2
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There is no power consuming parts in the distribution system
D. Based on given case
E. Capacity range not relevant for given case
F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
H. Reinforcement not relevant
I. No station will be installed for the distribution network

## 112 8 gas Suburban
Technology |  | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
Energy losses, stations [%] | bar: Est to -
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
Typical load profile [-] | bar: Est to Upper
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | Est: N/A; Est: N/A; Est: N/A; Est: N/A; -: D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs [€/MWh/year] Suburban | 159.5059 | 159.5059 | 159.5059 | 159.5059 | 148.8722 | 180.7734 | 148.8722 | 180.7734 | 0 | 2
| Investment costs; service line, 0-20 kW [€/unit] | 1701.3963 | 1701.3963 | 1701.3963 | 1701.3963 | 1488.7218 | 1914.0709 | 1488.7218 | 1914.0709 | 0 | 2
Investment costs; service line, 20-50 kW [€/unit] | bar: Est to -
Investment costs; service line, 50-100 kW [€/unit] | bar: Est to -
Investment costs; service line, above 100 kW [€/unit] | bar: Est to -
| Investment costs; single line, 0-50 kW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 50-250 kW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 100-250 kW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 250 kW-1 MW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 1 MW-5 MW [€/m] | 63.8024 | 63.8024 | 63.8024 | 63.8024 | 57.4221 | 70.1826 | 57.4221 | 70.1826 | G
| Investment costs; single line, 5 MW-25 MW [€/m] | 92.159 | 92.159 | 92.159 | 92.159 | 82.9431 | 101.3749 | 82.9431 | 101.3749 | G
| Investment costs; single line, 25 MW-100 MW [€/m] | - | - | - | - | - | - | - | - | 0
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 2
| Fixed O&M [€/MW/year] | 329.6455 | 329.6455 | 329.6455 | 329.6455 | 265.8432 | 393.4479 | 265.8432 | 393.4479 | 0 | 2
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There is no power consuming parts in the distribution system
D. Based on given case
E. Capacity range not relevant for given case
F. Stated number is for a Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H. Reinforcement not relevant
I. No station will be installed for the distribution network

## 112 9 gas City
Technology |  | Energy Transport Natural Gas Distribution, New distribution in existing city areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | - | - | - | - | - | - | - | - | A | 1
| Energy losses, stations [%] | - | - | - | - | - | - | - | - | B | 1
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C | 1
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 1
Typical load profile [-] | bar: -
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 1
Financial data
| Distribution network costs [€/MWh/year] City | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 0 | 1
| Investment costs; service line, 0-20 kW [€/unit] | - | - | - | - | - | - | - | - | 0
| Investment costs; service line, 20-50 kW [€/unit] | - | - | - | - | - | - | - | - | 0
| Investment costs; service line, 50-100 kW [€/unit] | - | - | - | - | - | - | - | - | 0
| Investment costs; service line, above 100 kW [€/unit] | 15950.5908 | 15950.5908 | 15950.5908 | 15950.5908 | 12760.4726 | 19140.7089 | 12760.4726 | 19140.7089 | E | 1
| Investment costs; single line, 0-50 kW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 50-250 kW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 100-250 kW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 250 kW-1 MW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 1 MW-5 MW [€/m] | 76.5628 | 76.5628 | 76.5628 | 76.5628 | 68.9066 | 84.2191 | 68.9066 | 84.2191 | 0 | 1
| Investment costs; single line, 5 MW-25 MW [€/m] | 110.5908 | 110.5908 | 110.5908 | 110.5908 | 99.5317 | 121.6498 | 99.5317 | 121.6498 | 0 | 1
Investment costs; single line, 25 MW-100 MW [€/m] | bar: Est to -
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 1
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 1
| Fixed O&M [€/MW/year] | 21.2675 | 21.2675 | 21.2675 | 21.2675 | 17.014 | 25.5209 | 17.014 | 25.5209 | 0 | 1
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Technology-specific data
References:
1. HMN Naturgas
Notes:
A. For the defined case "New distribution in existing densely populated areas, city centres etc." it is assessed the natural gas based heating will be designed with one boiler and heat is distributied to the endusers by a locel district heating sytem. This means that the local natural gas system will only consist of a A service line with a capacity of 1.5 MW supplying a boiler aswell a meter and a pressure regulator. Therefore losses are neglegted
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There is no power consuming parts in the distribution system
D. Based on given case
E. Stated number is for a service line supplying 1,5 MW.
F. Not relavant, see note A

## 112 1 gas New area
Technology |  | Energy Transport Natural Gas Distribution, New developed residential areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
Energy losses, stations [%] | bar: Est to -
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
Typical load profile [-] | bar: Est to Upper
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | Est: N/A; Est: N/A; Est: N/A; Est: N/A; -: D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs [€/MWh/year] City | 287.1106 | 287.1106 | 287.1106 | 287.1106 | 255.2095 | 319.0118 | 255.2095 | 319.0118 | 0 | 2
| Investment costs; service line, 0-20 kW [€/unit] | 1701.3963 | 1701.3963 | 1701.3963 | 1701.3963 | 1488.7218 | 1914.0709 | 1488.7218 | 1914.0709 | 0 | 2
Investment costs; service line, 20-50 kW [€/unit] | bar: Est to -
Investment costs; service line, 50-100 kW [€/unit] | bar: Est to -
Investment costs; service line, above 100 kW [€/unit] | bar: Est to -
| Investment costs; single line, 0-50 kW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 50-250 kW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 100-250 kW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 250 kW-1 MW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 1 MW-5 MW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | G
| Investment costs; single line, 5 MW-25 MW [€/m] | 67.3469 | 67.3469 | 67.3469 | 67.3469 | 60.6122 | 74.0816 | 60.6122 | 74.0816 | G
| Investment costs; single line, 25 MW-100 MW [€/m] | - | - | - | - | - | - | - | - | 0
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 2
| Fixed O&M [€/MW/year] | 978.3029 | 978.3029 | 978.3029 | 978.3029 | 786.8958 | 1169.71 | 786.8958 | 1169.71 | 0 | 2
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There are no power consuming parts in the distribution system
D. Based on given case
E. Capacity range not relevant for given case
F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H. Reinforcement not relevant
I. No station will be installed for the distribution network

## 113_11 DH transmission
Technology |  | Energy Transport District Heating Transmission
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [% per km] | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 1.5 | 0.8 | 1.2 | A | [1, 2]
| Energy losses, lines 20-100 MW [% per km] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.375 | 0.2 | 0.3 | A | [1, 2]
| Energy losses, lines above 100 MW [% per km] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.15 | 0.08 | 0.12 | A | [1, 2]
| Energy losses, Heat exchanger stations [%] | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 1.5 | 0.8 | 1.2 |  | 1
| Energy losses, Pumping stations [%] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G | 1
| Auxiliary electricity consumption [%] energy transmitted | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 4]
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | B | [1, 2]
| Typical load profile [-] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.6 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 1
Financial data
| Investment costs; single line, 0-50 MW [€/MW/m] | 55.9207 | 63.1948 | 63.1948 | 63.1948 | 63.1948 | 63.1948 | 50.7489 | 75.0024 | 50.7489 | 75.0024 | [C, D] | [1, 3]
| Investment costs; single line, 50-100 MW [€/MW/m] | 27.9431 | 31.5779 | 31.5779 | 31.5779 | 31.5779 | 31.5779 | 25.4138 | 37.4085 | 25.4138 | 37.4085 | [C, D] | [1, 3]
| Investment costs; single line, 100-250 MW [€/MW/m] | 17.477 | 19.7504 | 19.7504 | 19.7504 | 19.7504 | 19.7504 | 15.8655 | 23.4058 | 15.8655 | 23.4058 | [C, D] | [1, 3]
| Investment costs; single line, 250-500 MW [€/MW/m] | 10.5204 | 11.8888 | 11.8888 | 11.8888 | 11.8888 | 11.8888 | 9.5484 | 14.0843 | 9.5484 | 14.0843 | [C, D] | [1, 3]
| Investment costs; single line, 500-1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, above 1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Fixed O&M [€/MW/km/year] | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 200 | 50 | 200
| Variable O&M [€/MWh/km] | 0.10634 | 0.11663 | 0.11663 | 0.11663 | 0.11663 | 0.11663 | 0.038487 | 1.7494 | 0.038487 | 1.7494 |  | [1, 4]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | C | 2
| Investments, percentage materials | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% |  | 2
| Investment, percentage soft cost | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | F | 2
Technology-specific data
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | E
| Investment costs; Heat exchanger station [€/MW] | 122287.8884 | 140161.8193 | 140161.8193 | 140161.8193 | 140161.8193 | 140161.8193 | 77089.0006 | 168194.1831 | 77089.0006 | 168194.1831 |  | 1
| Investment costs; Pump station [€/MW] | 111654.0923 | 127473.1986 | 127473.1986 | 127473.1986 | 127473.1986 | 127473.1986 | 70110.2592 | 152967.8384 | 70110.2592 | 152967.8384 |  | 1
References:
1. Based on Ramboll experience figures
2. LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. The loss is per trench km of transmission pipeline pair.
B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
C. The cost is per trench meter transmission pipeline pair in unpaved areas.
D. Two district heating pipes were chosen for each interval (one for the lowest effect level and one for the highest). The average of these two are stated in the table. For cost interpolation: P = a * C^b, where P = cost in €/MW/m, C = capacity in MW, a = 330 and b =-0,571.
E. Depends on the scale of the transmission grid and supply strategy of reserve capacity. Therefore, it is not possible to generalize these costs.
F. Soft costs include design, planning, tender, permits, supervision, etc.

## 113_12 DH_Distribu Suburb
Technology |  | Energy Transport District Heating Distribution, Suburban
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, network [%] | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 10 | 16 | 9 | 14 | [A, B] | 2
| Auxiliary electricity consumption [%] of energy delivered | 2 | 2 | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 4
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | C | 2
Typical load factor [-]
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.18 | 0.22 | 0.18 | 0.22
| - Commercial | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3
Financial data
| Investments cost, distribution network [M€/km2] | 6.4626 | 7.3032 | 7.3032 | 7.3032 | 7.3032 | 7.3032 | 5.4797 | 9.0684 | 5.4797 | 9.0684 | [D, E] | [1, 3]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | E | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 25% | 25% | 20% | 30% | 20% | 30% | E | 2
| Investment, percentage soft costs percentage | 15% | 15% | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | H | 2
| Fixed O&M [€/MW/year] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 750 | 2000 | 750 | 2000 | M | 1
| Variable O&M [€/MWh] | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 1.508 | 3.0161 | 1.508 | 3.0161 | M | [1, 4]
Technology-specific data
| Investment costs; service line, 0-20 kW [€/unit] | 4164.6016 | 4706.3255 | 4706.3255 | 4706.3255 | 4706.3255 | 4706.3255 | 3242.5827 | 6192.4458 | 3242.5827 | 6192.4458 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 20-50 kW [€/unit] | 4518.7972 | 5106.5942 | 5106.5942 | 5106.5942 | 5106.5942 | 5106.5942 | 3547.7252 | 6678.7487 | 3547.7252 | 6678.7487 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 50-100 kW [€/unit] | 4987.2013 | 5635.9275 | 5635.9275 | 5635.9275 | 5635.9275 | 5635.9275 | 3953.0763 | 7309.6865 | 3953.0763 | 7309.6865 | [B, E, F, J] | [1, 3]
| Investment costs; service line, above 100 kW [€/unit] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | K
| Investment costs; single line, 0-50 kW [€/m] | 308.4523 | 348.5752 | 348.5752 | 348.5752 | 348.5752 | 348.5752 | 241.1895 | 455.9609 | 241.1895 | 455.9609 | [B, E, G] | [1, 3]
| Investment costs; single line, 50-250 kW [€/m] | 389.9116 | 440.6306 | 440.6306 | 440.6306 | 440.6306 | 440.6306 | 327.206 | 554.0552 | 327.206 | 554.0552 | [B, E, G] | [1, 3]
| Investment costs; single line, 100-250 kW [€/m] | 406.5826 | 459.4701 | 459.4701 | 459.4701 | 459.4701 | 459.4701 | 342.0119 | 576.9283 | 342.0119 | 576.9283 | [B, E, G] | [1, 3]
| Investment costs; single line, 250 kW-1 MW [€/m] | 515.5657 | 582.6296 | 582.6296 | 582.6296 | 582.6296 | 582.6296 | 456.5441 | 700.0145 | 456.5441 | 700.0145 | [B, E, G] | [1, 3]
| Investment costs; single line, 1 MW-5 MW [€/m] | 724.6157 | 818.8724 | 818.8724 | 818.8724 | 818.8724 | 818.8724 | 646.1684 | 971.0722 | 646.1684 | 971.0722 | [B, E, G] | [1, 3]
| Investment costs; single line, 5 MW-25 MW [€/m] | 1308.5602 | 1478.7753 | 1478.7753 | 1478.7753 | 1478.7753 | 1478.7753 | 1184.4561 | 1752.5903 | 1184.4561 | 1752.5903 | [B, E, G] | [1, 3]
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Pumping station above 1 MW [€/MW] | 98736.0339 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 61998.7032 | 135269.898 | 61998.7032 | 135269.898 | I | 1
| Pumping station below 1 MW [€/MW] | 255209.4707 | 291367.4445 | 263879.9497 | 263879.9497 | 263879.9497 | 263879.9497 | 160252.0945 | 349640.9333 | 160252.0945 | 349640.9333 | I | 1
References:
1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
2. Ramboll experience and technical data from LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities
C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on an area of scattered single-family houses of 1-2 floors with a heat density of 10 GWh/year/km2.
E. A paved area is assumed for the distribution network. For service lines 50 % unpaved and 50 % paved area is asumed.
F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
K. Service lines above 100 kW are not relevant in the specific area type.
L. Single lines above 25 MW are not relevant in the specific area type.
M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.

## 113_13 DH_Distribu City
Technology |  | Energy Transport District Heating Distribution, City
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, network [%] | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 9 | 4 | 8 | [A, B] | 2
| Auxiliary electricity consumption [%] of energy delivered | 2 | 2 | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 4
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | C | 2
Typical load factor [-]
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.18 | 0.25 | 0.18 | 0.25
| - Commercial | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3
Financial data
| Investments cost, distribution network [M€/km2] | 5.968 | 6.7443 | 6.7443 | 6.7443 | 6.7443 | 6.7443 | 5.0474 | 8.3655 | 5.0474 | 8.3655 | [D, E] | [1, 3]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | E | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 25% | 25% | 20% | 30% | 20% | 30% | E | 2
| Investment, percentage soft costs | 15% | 15% | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | H | 2
| Fixed O&M [€/MW/year] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 750 | 2000 | 750 | 2000 | M | 1
| Variable O&M [€/MWh] | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 1.508 | 3.0161 | 1.508 | 3.0161 | M | [1, 4]
Technology-specific data
| Investment costs; service line, 0-20 kW [€/unit] | 4961.2182 | 5606.5644 | 5606.5644 | 5606.5644 | 5606.5644 | 5606.5644 | 3804.7675 | 7431.9167 | 3804.7675 | 7431.9167 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 20-50 kW [€/unit] | 5333.929 | 6027.7568 | 6027.7568 | 6027.7568 | 6027.7568 | 6027.7568 | 4135.3976 | 7883.1671 | 4135.3976 | 7883.1671 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 50-100 kW [€/unit] | 5826.9859 | 6584.9497 | 6584.9497 | 6584.9497 | 6584.9497 | 6584.9497 | 4627.3368 | 8482.0584 | 4627.3368 | 8482.0584 | [B, E, F, J] | [1, 3]
| Investment costs; service line, above 100 kW [€/unit] | 7159.8328 | 8091.1709 | 8091.1709 | 8091.1709 | 8091.1709 | 8091.1709 | 6264.0232 | 9918.3185 | 6264.0232 | 9918.3185 | [B, E, F, J, K] | [1, 3]
| Investment costs; single line, 0-50 kW [€/m] | 338.688 | 382.7439 | 382.7439 | 382.7439 | 382.7439 | 382.7439 | 262.3075 | 506.8973 | 262.3075 | 506.8973 | [B, E, G] | [1, 3]
| Investment costs; single line, 50-100 kW [€/m] | 380.2063 | 429.6629 | 429.6629 | 429.6629 | 429.6629 | 429.6629 | 303.189 | 559.8538 | 303.189 | 559.8538 | [B, E, G] | [1, 3]
| Investment costs; single line, 100-250 kW [€/m] | 441.2294 | 498.6238 | 498.6238 | 498.6238 | 498.6238 | 498.6238 | 372.4651 | 624.7824 | 372.4651 | 624.7824 | [B, E, G] | [1, 3]
| Investment costs; single line, 250 kW-1 MW [€/m] | 551.4741 | 623.2089 | 623.2089 | 623.2089 | 623.2089 | 623.2089 | 488.4229 | 749.2944 | 488.4229 | 749.2944 | [B, E, G] | [1, 3]
| Investment costs; single line, 1 MW-5 MW [€/m] | 773.1749 | 873.7481 | 873.7481 | 873.7481 | 873.7481 | 873.7481 | 691.7201 | 1035.2719 | 691.7201 | 1035.2719 | [B, E, G] | [1, 3]
| Investment costs; single line, 5 MW-25 MW [€/m] | 1390.4364 | 1571.3019 | 1571.3019 | 1571.3019 | 1571.3019 | 1571.3019 | 1258.996 | 1863.1035 | 1258.996 | 1863.1035 | [B, E, G] | [1, 3]
| Investment costs; single line, 25 MW-100 MW [€/m] | 2532.9797 | 2862.4651 | 2862.4651 | 2862.4651 | 2862.4651 | 2862.4651 | 2305.633 | 3393.1957 | 2305.633 | 3393.1957 | [B, E, G, L] | [1, 3]
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Pumping station above 1 MW [€/MW] | 98736.0339 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 61998.7032 | 135269.898 | 61998.7032 | 143842.3191 | I | 1
| Pumping station below 1 MW [€/MW] | 255209.4707 | 291367.4445 | 291367.4445 | 291367.4445 | 291367.4445 | 291367.4445 | 160252.0945 | 349640.9333 | 160252.0945 | 349640.9333 | I | 1
References:
1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
2. Ramboll experience and technical data from LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
E. A paved area is assumed for the distribution network as well as for service lines.
F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.

## 113_14 DH_Distribu New area
Technology |  | Energy Transport District Heating Distribution, New Area
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, network [%] | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 24 | 10 | 20 | [A, B] | 2
| Auxiliary electricity consumption [%] of energy delivered | 2 | 2 | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 4
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | C | 2
Typical load factor [-]
| - Residential | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.1 | 0.2 | 0.1 | 0.2
| - Commercial | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.1 | 0.2 | 0.1 | 0.2
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investments cost, distribution network [M€/km2] | 4.7197 | 5.3336 | 5.3336 | 5.3336 | 5.3336 | 5.3336 | 3.9965 | 6.6191 | 3.9965 | 6.6191 | [D, E] | [1, 3]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | E | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 25% | 25% | 20% | 30% | 20% | 30% | E | 2
| Investment, percentage soft costs | 15% | 15% | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | H | 2
| Fixed O&M [€/MW/year] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 750 | 2000 | 750 | 2000 | M | 1
| Variable O&M [€/MWh] | 1.5951 | 1.7494 | 1.7494 | 1.7494 | 1.7494 | 1.7494 | 1.3121 | 2.6241 | 1.3121 | 2.6241 | M | [1, 4]
Technology-specific data
| Investment costs; service line, 0-20 kW [€/unit] | 3504.3785 | 3960.2217 | 3960.2217 | 3960.2217 | 3960.2217 | 3960.2217 | 2706.7547 | 5231.3553 | 2706.7547 | 5231.3553 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 20-50 kW [€/unit] | 3783.9591 | 4276.1697 | 4276.1697 | 4276.1697 | 4276.1697 | 4276.1697 | 2951.1919 | 5592.5358 | 2951.1919 | 5592.5358 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 50-100 kW [€/unit] | 4153.7518 | 4694.0644 | 4694.0644 | 4694.0644 | 4694.0644 | 4694.0644 | 3295.6762 | 6066.1745 | 3295.6762 | 6066.1745 | [B, E, F, J] | [1, 3]
| Investment costs; service line, above 100 kW [€/unit] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | K
| Investment costs; single line, 0-50 kW [€/m] | 242.6776 | 274.2447 | 274.2447 | 274.2447 | 274.2447 | 274.2447 | 188.8114 | 361.0718 | 188.8114 | 361.0718 | [B, E, G] | [1, 3]
| Investment costs; single line, 50-250 kW [€/m] | 302.329 | 341.6554 | 341.6554 | 341.6554 | 341.6554 | 341.6554 | 253.3243 | 431.3804 | 253.3243 | 431.3804 | [B, E, G] | [1, 3]
| Investment costs; single line, 100-250 kW [€/m] | 317.9295 | 359.2852 | 359.2852 | 359.2852 | 359.2852 | 359.2852 | 267.9289 | 450.6415 | 267.9289 | 450.6415 | [B, E, G] | [1, 3]
| Investment costs; single line, 250 kW-1 MW [€/m] | 400.1399 | 452.1894 | 452.1894 | 452.1894 | 452.1894 | 452.1894 | 354.3626 | 543.4908 | 354.3626 | 543.4908 | [B, E, G] | [1, 3]
| Investment costs; single line, 1 MW-5 MW [€/m] | 561.6715 | 634.7327 | 634.7327 | 634.7327 | 634.7327 | 634.7327 | 501.7082 | 752.3791 | 501.7082 | 752.3791 | [B, E, G] | [1, 3]
| Investment costs; single line, 5 MW-25 MW [€/m] | 1012.1237 | 1143.779 | 1143.779 | 1143.779 | 1143.779 | 1143.779 | 916.2945 | 1355.8852 | 916.2945 | 1355.8852 | [B, E, G] | [1, 3]
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Pumping station above 1 MW [€/MW] | 92764.2348 | 105907.0338 | 105907.0338 | 105907.0338 | 105907.0338 | 105907.0338 | 59307.9389 | 127088.4405 | 59307.9389 | 127088.4405 | I | 1
| Pumping station below 1 MW [€/MW] | 247371.1906 | 282418.6401 | 282418.6401 | 282418.6401 | 282418.6401 | 282418.6401 | 158154.4384 | 338902.3681 | 158154.4384 | 338902.3681 | I | 1
References:
1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
2. Ramboll experience and technical data from LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
K. Service lines above 100 kW are not relevant in the specific area type.
L. Single lines above 25 MW are not relevant in the specific area type.
M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.

## H2 70
Technology |  | Main distribution line-H2-70 bar
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-100 MW [%/1000 km] | 10 | 9.3 | 8.3 | 8.2 | 16.3 | 7.3 | 13.6 | A
| Energy losses, lines 100-250 MW [%/1000 km] | 8.2 | 7.6 | 6.8 | 6.7 | 13.4 | 6 | 11.2 | A
| Energy losses, lines 250-500 MW [%/1000 km] | 6.3 | 5.8 | 5.2 | 5.1 | 10.3 | 4.6 | 8.6 | A
| Energy losses, lines 500-1500 MW [%/1000 km] | 4.5 | 4.1 | 3.7 | 3.6 | 7.3 | 3.2 | 6.1 | A
| Energy losses, lines 1500-5000 MW [%/1000 km] | 2.9 | 2.7 | 2.4 | 2.4 | 4.8 | 2.1 | 4 | A
| Energy losses, lines 5000-20000 MW [%/1000 km] | 2.2 | 2 | 1.8 | 1.8 | 3.6 | 1.6 | 3 | A
| Energy losses, lines above 20000 MW [%/1000 km] | 1.6 | 1.5 | 1.3 | 1.3 | 2.6 | 1.1 | 2.1 | A
| Energy demand, compressor filling station [%] | 0.93532 | 0.84179 | 0.74826 | 0.74826 | 3 | 0.6 | 2.1 | B
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 0-100 MW [€/MW/m] | 4.0408 | 3.8281 | 3.6155 | 3.6155 | 5.1042 | 3.2965 | 4.6788 | C | 0
| Investment costs; single line, 100-250 MW [€/MW/m] | 1.8077 | 1.7014 | 1.5951 | 1.5951 | 2.2331 | 1.4887 | 2.0204 | C | 0
| Investment costs; single line, 250-500 MW [€/MW/m] | 1.0634 | 1.0634 | 1.0634 | 1.0634 | 1.3824 | 0.95704 | 1.276 | C | 0
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.74436 | 0.74436 | 0.74436 | 0.74436 | 0.95704 | 0.63802 | 0.8507 | C | 0
| Investment costs; single line, 1000-4000 MW [€/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.42535 | 0.53169 | 0.42535 | 0.42535 | C | 0
| Investment costs; single line, above 6000 MW [€/MW/m] | 0.23394 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | C | 0
| Investments, percentage installation [%] | 77.5% | 77.5% | 77.5% | 75% | 80% | 70% | 80% | D | 0
| Investments, percentage materials [%] | 22.5% | 22.5% | 22.5% | 20% | 25% | 20% | 30% | D | 0
| Fixed O&M [€/km/year/MW] | 0.54232 | 0.26584 | 0.19938 | 0.21267 | 1.0634 | 0.11697 | 1.0634 | E | 0
| Variable O&M [€/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
Notes:
References:. . <none>
References:
<none>

## H2 140
Technology |  | Main distribution line H2-140 bar
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-100 MW [%/1000 km] | 7.5 | 7 | 6.3 | 6.2 | 12.3 | 5.5 | 10.3 | A
| Energy losses, lines 100-250 MW [%/1000 km] | 6.4 | 5.9 | 5.3 | 5.2 | 10.4 | 4.6 | 8.7 | A
| Energy losses, lines 250-500 MW [%/1000 km] | 5.1 | 4.7 | 4.2 | 4.1 | 8.3 | 3.7 | 6.9 | A
| Energy losses, lines 500-1500 MW [%/1000 km] | 3.8 | 3.5 | 3.1 | 3.1 | 6.2 | 2.7 | 5.2 | A
| Energy losses, lines 1500-5000 MW [%/1000 km] | 2.7 | 2.5 | 2.2 | 2.2 | 4.3 | 1.9 | 3.6 | A
| Energy losses, lines 5000-20000 MW [%/1000 km] | 2.1 | 1.9 | 1.7 | 1.7 | 3.4 | 1.5 | 2.8 | A
| Energy losses, lines above 20000 MW [%/1000 km] | 1.5 | 1.4 | 1.3 | 1.3 | 2.5 | 1.1 | 2.1 | A
| Energy demand, compressor filling station [%] | 2.1 | 1.68 | 1.47 | 1.47 | 3.7 | 0.9 | 2.5 | B
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 0-100 MW [€/MW/m] | 4.3598 | 4.1472 | 3.9345 | 3.9345 | 5.5295 | 3.5091 | 4.9979 | C | 0
| Investment costs; single line, 100-250 MW [€/MW/m] | 1.9141 | 1.8077 | 1.7014 | 1.7014 | 2.4458 | 1.5951 | 2.2331 | C | 0
| Investment costs; single line, 250-500 MW [€/MW/m] | 1.1697 | 1.1697 | 1.0634 | 1.0634 | 1.4887 | 0.95704 | 1.3824 | C | 0
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.8507 | 0.74436 | 0.74436 | 0.74436 | 0.95704 | 0.63802 | 0.95704 | C | 0
| Investment costs; single line, 1000-4000 MW [€/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.42535 | 0.53169 | 0.42535 | 0.53169 | C | 0
| Investment costs; single line, above 6000 MW [€/MW/m] | 0.24458 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | 0.21267 | C | 0
| Investments, percentage installation [%] | 77.5% | 77.5% | 77.5% | 75% | 80% | 70% | 80% | D | 0
| Investments, percentage materials [%] | 22.5% | 22.5% | 22.5% | 20% | 25% | 20% | 30% | D | 0
| Fixed O&M [€/km/year/MW] | 0.54232 | 0.26584 | 0.19938 | 0.21267 | 1.0634 | 0.11697 | 1.0634 | E | 0
| Variable O&M [€/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
Notes:
A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on cost of booster compressor vs pipe material cost. Curently, the optimum seems to be: velosity (m/s)≈4.4*Q^0.1, dPdL(bar/km)≈1.28*Q^(-0.75), Q=energy flow (MW)
B. Energy to compress from 35 barg to 140 barg. This value can be lowered by only compress to curent operation pressure in transmission line using outtake from interstages compressors
C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
D. Installation cost is ~80% for small pipes and ~75% for large pipes
E. Fixed operation cost is per pipelength and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
References:
<none>

## NH3
Technology |  | Main distribution line-NH3
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses [‰] | <0.1 | <0.1 | <0.1 | 0.01 | 0.1 | 0.01 | 0.1 | [A, B]
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 1-15 MW [€/MW/m] | 10.7401 | 10.2084 | 9.783 | 9.6502 | 16.0837 | 8.8107 | 13.7055 | [B, C] | 0
| Investment costs; single line, 15-30 MW [€/MW/m] | 7.1246 | 6.8056 | 6.4866 | 6.413 | 10.6883 | 5.855 | 9.1078 | [B, C] | 0
| Investment costs; single line, 30-100 MW [€/MW/m] | 2.9774 | 2.8711 | 2.6584 | 2.6629 | 4.4382 | 2.4313 | 3.782 | [B, C] | 0
| Investment costs; single line, 100-300 MW [€/MW/m] | 1.3824 | 1.276 | 1.276 | 1.215 | 2.025 | 1.1093 | 1.7256 | [B, C] | 0
| Investment costs; single line, 300-500 MW [€/MW/m] | 0.74436 | 0.74436 | 0.74436 | 0.69785 | 1.1631 | 0.63714 | 0.9911 | [B, C] | 0
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.42205 | 0.70341 | 0.38533 | 0.5994 | [B, C] | 0
| Investment costs; single line, 1000-2000 MW [€/MW/m] | 0.31901 | 0.21267 | 0.21267 | 0.2424 | 0.404 | 0.22131 | 0.34427 | [B, C] | 0
| Investment costs; single line, above 2000 MW [€/MW/m] | 0.21267 | 0.21267 | 0.21267 | 0.19257 | 0.32095 | 0.17582 | 0.27349 | [B, C] | 0
| Investments, percentage installation [%] | 87% | 82.65% | 78.3% | 80% | 90% | 75% | 90% | D | 0
| Investments, percentage materials [%] | 13% | 17.35% | 21.7% | 10% | 20% | 10% | 25% | C | 0
| Fixed O&M [€/km/year] | 106.3373 | 106.3373 | 106.3373 | 53.1686 | 212.6745 | 53.1686 | 212.6745 | E | 0
| Variable O&M [€/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
References:
1
2
Notes:
A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
D. Position drilling is assumed to be able to reduce the installation cost. However, the factor is judged minor as increased safety may outrage this saving
E. Fixed operation cost is only per pipelengt (i.e. is not divided with capacity) as size have a relatively little impact on maintenance cost. 1% of CAPEX is applied.

## DME
Technology |  | Main distribution line-DME
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses [‰] | <0.1 | <0.1 | <0.1 | 0.01 | 0.1 | 0.01 | 0.1 | [A, B]
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 1-20 MW [€/MW/m] | 10.3147 | 9.8894 | 9.464 | 9.3103 | 15.5171 | 8.5003 | 13.2227 | [B, C] | 0
| Investment costs; single line, 20-50 MW [€/MW/m] | 6.9119 | 6.5929 | 6.2739 | 6.1871 | 10.3118 | 5.6488 | 8.787 | [B, C] | 0
| Investment costs; single line, 50-100 MW [€/MW/m] | 2.8711 | 2.7648 | 2.6584 | 2.5691 | 4.2819 | 2.3456 | 3.6487 | [B, C] | 0
| Investment costs; single line, 100-300 MW [€/MW/m] | 1.276 | 1.276 | 1.1697 | 1.1722 | 1.9537 | 1.0702 | 1.6648 | [B, C] | 0
| Investment costs; single line, 300-500 MW [€/MW/m] | 0.74436 | 0.74436 | 0.63802 | 0.67327 | 1.1221 | 0.61469 | 0.95619 | [B, C] | 0
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.40718 | 0.67863 | 0.37176 | 0.57829 | [B, C] | 0
| Investment costs; single line, 1000-2500 MW [€/MW/m] | 0.21267 | 0.21267 | 0.21267 | 0.23386 | 0.38977 | 0.21352 | 0.33214 | [B, C] | 0
| Investment costs; single line, above 2500 MW [€/MW/m] | 0.21267 | 0.21267 | 0.21267 | 0.18579 | 0.30964 | 0.16962 | 0.26386 | [B, C] | 0
| Investments, percentage installation [%] | 87% | 82.65% | 78.3% | 80% | 90% | 75% | 90% | D | 0
| Investments, percentage materials [%] | 13% | 17.35% | 21.7% | 10% | 20% | 10% | 25% | C | 0
| Fixed O&M [€/km/year] | 106.3373 | 106.3373 | 106.3373 | 53.1686 | 212.6745 | 53.1686 | 212.6745 | E | 0
| Variable O&M [€/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
References:
1
2
Notes:
A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
D. Position drilling is assumed to be able to reduce the installation cost. However, the factor is judged minor as increased safety may outrage this saving
E. Fixed operation cost is only per pipelengt (i.e. is not divided with capacity) as size have a relatively little impact on maintenance cost. 1% of CAPEX is applied.

## TOLU
Technology |  | Main distribution line-Toluene
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses [‰] | <0.1 | <0.1 | <0.1 | 0.01 | 0.1 | 0.01 | 0.1 | [A, B]
| Technical life time [years] | 50 | 50 | 50 | 45 | 55 | 45 | 55
| Construction time [years] | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investment costs; single line, 1-20 MW [€/MW/m] | 9.783 | 9.3577 | 8.9323 | 8.7729 | 14.6216 | 8.0097 | 12.4595 | [B, C] | 0
| Investment costs; single line, 20-50 MW [€/MW/m] | 6.4866 | 6.1676 | 5.9549 | 5.83 | 9.7166 | 5.3228 | 8.2798 | [B, C] | 0
| Investment costs; single line, 50-100 MW [€/MW/m] | 2.6584 | 2.5521 | 2.4458 | 2.4209 | 4.0348 | 2.2102 | 3.4382 | [B, C] | 0
| Investment costs; single line, 100-300 MW [€/MW/m] | 1.276 | 1.1697 | 1.1697 | 1.1046 | 1.841 | 1.0085 | 1.5687 | [B, C] | 0
| Investment costs; single line, 300-500 MW [€/MW/m] | 0.74436 | 0.63802 | 0.63802 | 0.63441 | 1.0573 | 0.57922 | 0.901 | [B, C] | 0
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.42535 | 0.42535 | 0.42535 | 0.38368 | 0.63947 | 0.3503 | 0.54491 | [B, C] | 0
| Investment costs; single line, 1000-2500 MW [€/MW/m] | 0.21267 | 0.21267 | 0.21267 | 0.22037 | 0.36728 | 0.20119 | 0.31297 | [B, C] | 0
| Investment costs; single line, above 2500 MW [€/MW/m] | 0.21267 | 0.21267 | 0.21267 | 0.17506 | 0.29177 | 0.15983 | 0.24863 | [B, C] | 0
| Investments, percentage installation [%] | 87% | 82.65% | 78.3% | 80% | 90% | 75% | 90% | D | 0
| Investments, percentage materials [%] | 13% | 17.35% | 21.7% | 10% | 20% | 10% | 25% | C | 0
| Fixed O&M [€/km/year] | 106.3373 | 106.3373 | 106.3373 | 53.1686 | 212.6745 | 53.1686 | 212.6745 | E | 0
| Variable O&M [€/MW/km] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
References:
1
2
Notes:
A. Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on length of pipe, cost of booster pump vs pipe material cost.
B. Pipes have been calc. using max dP/dL =0.04 bar/km. Higher dP/dL is optimal for short pipes but for long pipes, higher dP/dL will give many intermediate pump-booster stations
C. Estimate includes: installation based on burried pipeline with 8% tunneling, coating, sectionalisation with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting, landowner compensation
D. Position drilling is assumed to be able to reduce the installation cost. However, the factor is judged minor as increased safety may outrage this saving
E. Fixed operation cost is only per pipelengt (i.e. is not divided with capacity) as size have a relatively little impact on maintenance cost. 1% of CAPEX is applied.

## Road transport
Technology |  | Road transport
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy demand truck [MJ/km/ton LH2] | 5.9552 | 5.6417 | 4.7015 | 5 | 10 | 4 | 9 | [A, H] | 5
| Energy demand truck [MJ/km/ton CH2] | 12.6667 | 10.3 | 7.3 | 10 | 15 | 6 | 12 | [A, H] | 5
| Energy demand truck [MJ/km/ton NH3] | 0.67469 | 0.63918 | 0.53265 | 0.56469 | 0.87469 | 0.43265 | 0.73265 | [A, H] | 5
| Energy demand truck [MJ/km/ton DME] | 0.62092 | 0.58824 | 0.4902 | 0.51092 | 0.72092 | 0.3902 | 0.5902 | [A, H] | 5
| Energy demand truck [MJ/km/ton toluene] | 0.5 | 0.5 | 0.4 | 0.39 | 0.6 | 0.3 | 0.5 | [A, H] | 5
| Technical life time [years] | 10 | 10 | 10 | 4 | 12 | 4 | 12 | B
Financial data
| LH2: Loading/unloading cost [€/tonH2] | 55.2954 | 47.8518 | 39.3448 | 0 | 0 | 0 | 55.2954 | [E, F, G] | 1.0634
| LH2: Driving cost [€/tonH2/km] | 1.0394 | 1.0634 | 1.0102 | 0 | 0 | 0 | 1.0394 | [E, F, G] | 1.0634
| CH2: Loading/unloading cost [€/tonH2] | 117.5632 | 82.9431 | 61.6756 | 0 | 0 | 0 | 117.5632 | [E, F, G] | 2.1267
| CH2: Driving cost [€/tonH2/km] | 2.4212 | 1.9885 | 1.6057 | 0 | 0 | 0 | 2.4212 | [E, F, G] | 2.1267
| NH3: Loading/unloading cost [€/tonNH3] | 3.9345 | 3.9345 | 3.9345 | 0% | 0% | 0% | 3.9345 | [E, F, H] | 3.1901
| NH3: Driving cost [€/tonNH3/km] | 0.12023 | 0.11697 | 0.10634 | 0% | 0% | 0% | 0.12023 | [E, F, H] | 3.1901
| DME: Loading/unloading cost [€/tonDME] | 3.4307 | 3.4307 | 3.4307 | 0 | 0 | 0 | 3.4307 | [E, F, C, H] | 4.2535
| DME: Driving cost [€/tonDME/km] | 0.11064 | 0.11064 | 0.11064 | 0 | 0 | 0 | 0.11064 | [E, F, C, H] | 4.2535
| Toluene: Loading/unloading cost [€/tontoluene] | 2.0539 | 2.0539 | 2.0539 | 0 | 0 | 0 | 2.0539 | [E, F, D, H] | 4.2535
| Toluene: Driving cost [€/tontoluene/km] | 0.075773 | 0.075773 | 0.075773 | 0 | 0 | 0 | 0.075773 | [E, F, D, H] | 4.2535
Technology-specific data
References:
1. Air Liquide A/S
2. Everfuel A/S
3. Give Svaergods A/S
4. Fjellerad Transport Aps
5. Network for Transport Measures (NTM) database, 2020
Notes:
A. Fuel for propulation based on 50-60 tonne truck with capacity of 45-50 m3. Myltiply tank volume with density to get transported mass (density is given in Table 1 except for CH2 which is between 25-42 kg/m3 depending on tank pressure). Tanker assumed full one way and empty return (except for toluene/carrier where 80% return load is assumed). For CH2, pressure in tanks are assumed to increase from 350 bar (2020) to 700 bar (2050)
B. Technical lifetime of truck (puller) will depend on the distance driven, 4-10 years. Lifetime trailer 10 years or more.
C. Numbers based on LPG transport
D. Numbers based on diesel transport, but the fuel concumption is based on full cargo tank on the round trip.
E. Capital cost of truck is split into the fixed and variable cost based on relative time spend on loading/unloading and on driving.
F. Cost is based on: CAPEX Truck + Tanker is 450-1000 k€ (LHC tank is the cheapest and CH2 the most expensive), 8000 h/year operation, 60 km/h average speed, fuel cost of 1.25 €/kg, fuel LHV=42.5 MJ/kg, Annual fixed O&M is 5% capital cost
G. Improvements: Faster loading time, lower CAPEX, and longer distance per fuel. For CH2, also increased pressure in tank
H. Fuel for propulation: For LHC, L20 and LH2: 19 MJ/km in 2020, 18 MJ/km in 2030 and 15 MJ/km in 2050 For CH2: 24 MJ/km in 2020, 23 MJ/km in 2030 and 20 MJ/km in 2050

## Ship Transport
Technology |  | Ship transport
year |  | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| LH2: Energy demand [MJ/km] | Est: 2250; Est: 2025; Est: 1575; -: [A, F]
| L20: Energy demand [MJ/km] | Est: 2450; Est: 2205; Est: 1715; -: [A, F]
| LHC: Energy demand [MJ/km] | Est: 2450; Est: 2205; Est: 1715; -: [A, F]
| Technical life time [years] | Est: 20; Est: 20; Est: 20; -: 1
Financial data
| LH2: Investment cost [€/tonH2] | 15950.5908 | 14887.2181 | 10633.7272 | 0 | 0 | 0 | 0 | G | [2, 3]
| L20: Investment cost [€/tonL20] | 1860.9023 | 1978.8327 | 1978.8327 | 0 | 0 | 0 | 0 | [B, C] | [2, 3]
| LHC: Investment cost [€/tonLHC] | 733.7272 | 780.2255 | 780.2255 | 0 | 0 | 0 | 0 | D | 0
| LH2: Fixed O&M cost [€/tonH2/y] | 79.753 | 74.4361 | 53.1686 | 0 | 0 | 0 | 0 | E | 0
| L20: Fixed O&M cost [€/tonL20/y] | 9.5704 | 9.5704 | 9.5704 | 0 | 0 | 0 | 0 | E | 0
| LHC: Fixed O&M cost [€/tonLHC/y] | 4.2535 | 4.2535 | 4.2535 | 0 | 0 | 0 | 0 | E | 0
| LH2: Port cost [€/tonH2] | 7.2309 | 6.3802 | 4.2535 | 0 | 0 | 0 | 0 | 0 | 3.1901
| L20: Port cost [€/tonH2] | 1.8077 | 1.8077 | 1.8077 | 0 | 0 | 0 | 0 | 0 | 3.1901
| LHC: Port cost [€/tonLHC] | 1.4887 | 1.4887 | 1.4887 | 0 | 0 | 0 | 0 | 0 | 3.1901
Technology-specific data
References:
1. The Basics of the Tanker Shipping Market, Euronav, 2017
2. Torm annual report 2018
3. Shipping CO₂-UK cost estimation study, 2018
Notes:
A. Energy based on fuel LHV which is approximated by: 0.023*Mcargo+1400 for L20 and LHC. For LH2 the weight of the cargo is much less (do to the low weight of H2) why the weight of the entire ship have been used instead
B. Investment cost based on: Cost [€/t] = 4000-0.05*Mcargo, where Mcargo is design capacity of ship
C. CAPEX of LPG carrier see https://www.seatrade-maritime.com/tankers/euronav-buys-another-scrubber-fitted-resale-vlcc-newbuild
D. CAPEX of tanker see BRS group annual review 2019
E. Fixed O&M is assumed to be ~5% of annual CAPEX
F. It is assumed that the efficiency of the combustion engine is improved so it is 90% in 2030 and 70% in 2050 of the efficiency in 2020. The 70% is based on the difference between the efficiency of a traditional combustion engine and a fuel cell engine. The 90% is based on natural replacement of old tankers with news tankers that have a more efficient engine (some of them might be fuel cells) and revamp of existing engines
G. Assumed cost reduction after LH2 tanker is commercialized