## Index
INDEX | Technology Data for Energy Transport
1.1 el Main distri50-60kVcabl | Version | 8
1.2 el distri Rural | Cost data for el distribution and gas is in | 2020 | EURO
1.3 el distri suburban | Cost data for el transmission, DH, H2 pipelines and road is in | 2025 | EURO
1.4 el distri city
1.5 el distri new area
1.6 el trans OH-lines
1.7 el trans AC&DC cables | License:
1.8 el substations | This work is licensed under Attribution 4.0 International
1.9 el transformers
1.10 el compensation
Input 1.6 - OH-lines
Input 1.7 - Cables
Input 1.8 - Substations
Input 1.9 - Transformers | Date | Sheet | Change | Notes
Input 1.10 - Compensation | 2025-07-01 | 1.6 - 1.9 | Transmission of electricity added - note that 1.1-1.5 (Distribution of electricity) was not updated. See also additional cost sheet
2.1 gas Main distri line | 2025-02-21 | 3.1 - 3.4 | Updated sheets for Distict heating
2.2 gas Rural | 2023-08-31 | all sheets | update to 2020 prices
2.3 gas Suburban | 2021-11-01 |  | CO2 transport removed and transferred to the Technology Catalogue for Carbon Capture, Transport and Storage
2.4 gas City | 2021-03-01 | 2.1 - 2.5 | Transport of gasses and liquids added
2.5 gas New area | 2020-11-02 |  | CO2 transport added
3.1 DH Transmission
3.2 DH_Distribu Suburb
3.3 DH_Distribu City
3.4 DH_Distribu New area
4.1 H2 pipeline transp. 40barg
4.2 H2 pipeline tranp. 90 barg
4.3 H2 pipeline transp. 140 barg
5.1 H2 road transp.

## alldata_flat
ws | Technology | cat | par | unit | priceyear | note | ref | est | year | val
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Est | 2015 | 1.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Est | 2020 | 1.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Est | 2030 | 1.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Est | 2050 | 1.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2020 | 1
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2050 | 1
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2020 | 5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2050 | 5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2015 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2020 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2030 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2050 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.15
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2015 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2020 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2030 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2050 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.15
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2015 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2020 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2030 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2050 | 0.3
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.6
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.15
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.5
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2015 | 0.2
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2020 | 0.2
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2030 | 0.2
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Est | 2050 | 0.2
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2020 | 0.2
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Lower | 2050 | 0.1
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2020 | 0.25
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | [A, B] | [1, 2, 3, 4] | Upper | 2050 | 0.25
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Est | 2015 | 40
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Est | 2020 | 40
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Est | 2030 | 40
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Est | 2050 | 40
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Lower | 2020 | 35
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Lower | 2050 | 40
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Upper | 2020 | 40
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Technical life time [years] | years |  | C | 5 | Upper | 2050 | 50
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Est | 2015 | 0.45
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Est | 2020 | 0.45
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Est | 2030 | 0.45
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Est | 2050 | 0.45
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Lower | 2020 | 0.45
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Lower | 2050 | 0.423
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Upper | 2020 | 0.45
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Energy/technical data | Typical load profile [-] | - |  | D |  | Upper | 2050 | 0.54
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Est | 2015 | 24.9898
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Est | 2020 | 26.2015
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Est | 2030 | 27.4719
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Est | 2050 | 28.8039
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Lower | 2020 | 26.0952
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Lower | 2050 | 25.1642
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Upper | 2020 | 26.5735
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | Q | 9 | Upper | 2050 | 26.5735
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Est | 2015 | 6.3802
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Est | 2020 | 6.3802
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Est | 2030 | 6.3802
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Est | 2050 | 6.3802
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Lower | 2020 | 6.1061
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Lower | 2050 | 5.8438
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Upper | 2020 | 6.7846
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [F, G] | [6, 7] | Upper | 2050 | 7.2145
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Est | 2015 | 3.2965
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Est | 2020 | 3.2965
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Est | 2030 | 3.2965
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Est | 2050 | 3.2965
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Lower | 2020 | 3.1548
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Lower | 2050 | 3.0193
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Upper | 2020 | 3.5054
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [I, G] | [6, 7] | Upper | 2050 | 3.7275
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Est | 2015 | 4.1472
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Est | 2020 | 4.1472
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Est | 2030 | 4.1472
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Est | 2050 | 4.1472
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Lower | 2020 | 3.969
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Lower | 2050 | 3.7984
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Upper | 2020 | 4.41
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [H, G] | [6, 7] | Upper | 2050 | 4.6894
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Est | 2015 | 80816.3266
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Est | 2020 | 80816.3266
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Est | 2030 | 80816.3266
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Est | 2050 | 80816.3266
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Lower | 2020 | 81984.7345
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Lower | 2050 | 83170.0348
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Upper | 2020 | 85937.8768
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [L, O] | 8 | Upper | 2050 | 91383.9937
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Est | 2015 | 4759.6563
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Est | 2020 | 4759.6563
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Est | 2030 | 4759.6563
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Est | 2050 | 4759.6563
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Lower | 2020 | 4828.4694
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Lower | 2050 | 4898.2773
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Upper | 2020 | 5061.2886
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [M, O] |  | Upper | 2050 | 5382.0363
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Est | 2015 | 0.42
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Est | 2020 | 0.42
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Est | 2030 | 0.42
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Est | 2050 | 0.42
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Lower | 2020 | 0.3737
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Lower | 2050 | 0.32961
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Upper | 2020 | 0.42
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage installation |  |  | P | 6 | Upper | 2050 | 0.42
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Est | 2015 | 0.58
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Est | 2020 | 0.58
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Est | 2030 | 0.58
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Est | 2050 | 0.58
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Lower | 2020 | 0.58
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Lower | 2050 | 0.58
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Upper | 2020 | 0.6263
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Investments, percentage materials |  |  | P | 6 | Upper | 2050 | 0.67039
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Est | 2015 | 16801.2889
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Est | 2020 | 16801.2889
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Est | 2030 | 16801.2889
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Est | 2050 | 16801.2889
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Lower | 2020 | 17044.1948
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Lower | 2050 | 17290.6125
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Upper | 2020 | 17866.0323
1.1 el Main distri50-60kVcabl | Energy Transport Electricity Main distribution, electricity cables | Financial data | Reinforcement costs [€/MW] | €/MW |  | [K, O] | 6 | Upper | 2050 | 18998.2513
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Est | 2015 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Est | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Est | 2030 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Est | 2050 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.3256
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.4664
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.3256
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.4664
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2015 | 1
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2020 | 1
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2030 | 1
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2050 | 1
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 4.5
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 5.25
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2015 | 1.125
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2020 | 1.125
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2030 | 1.125
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2050 | 1.125
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2015 | 40
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2020 | 40
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2030 | 40
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2050 | 40
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2015 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2030 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2050 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.3256
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.44
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.4664
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Est | 2015 | 183.9635
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Est | 2020 | 183.9635
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Est | 2030 | 183.9635
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Est | 2050 | 183.9635
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2020 | 165.5671
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2050 | 140.0698
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2020 | 183.9635
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Distribution network costs [€/MWh/year] Rural | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2050 | 218.9165
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2015 | 1730.968
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2020 | 1706.7345
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2030 | 1682.8402
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2050 | 1659.2804
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2020 | 1699.8106
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2050 | 1639.1681
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2020 | 1730.968
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2050 | 1730.968
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 557.2073
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 557.2073
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 557.2073
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 557.2073
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 501.4866
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 451.3379
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 557.2073
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 557.2073
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 1501.4823
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 1501.4823
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 1501.4823
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 1501.4823
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 1351.3341
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 1216.2006
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 1501.4823
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 1501.4823
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 1683.319
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 1683.319
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 1683.319
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 1683.319
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 1514.9871
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 1363.4884
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 1683.319
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 1683.319
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 3982.3308
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 3982.3308
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 3982.3308
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 3982.3308
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 3584.0977
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 3225.688
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 3982.3308
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 3982.3308
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 43.5983
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 43.5983
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 43.5983
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 43.5983
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 39.3448
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 35.4103
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 43.5983
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 43.5983
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 34.0279
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 30.6251
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 34.0279
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 30.6251
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 38.2814
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 93.5768
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 93.5768
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 93.5768
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 93.5768
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 90.3867
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 81.348
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 93.5768
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 93.5768
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2015 | 71777.6585
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2020 | 71777.6585
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2030 | 71777.6585
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2050 | 71777.6585
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2020 | 68619.4415
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2050 | 65600.1861
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2020 | 71777.6585
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2050 | 71777.6585
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2015 | 0.62
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2020 | 0.62
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2030 | 0.62
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2050 | 0.62
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2020 | 0.57346
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2050 | 0.52557
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2020 | 0.62
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2050 | 0.62
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2015 | 0.22
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2020 | 0.22
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2030 | 0.22
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2050 | 0.22
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.18858
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.16612
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.22
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.19
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2015 | 0.38
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2020 | 0.38
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2030 | 0.38
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2050 | 0.38
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2020 | 0.38
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2050 | 0.42
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2020 | 0.42654
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2050 | 0.38
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2015 | 0.78
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2020 | 0.78
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2030 | 0.78
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2050 | 0.78
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.78
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.78
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.81
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.81
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2015 | 12228.7863
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2020 | 12228.7863
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2030 | 12228.7863
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2050 | 12228.7863
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2020 | 11690.7197
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2050 | 11176.328
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2020 | 12228.7863
1.2 el distri Rural | Energy Transport Electricity Distribution, Rural | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2050 | 12228.7863
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Est | 2015 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Est | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Est | 2030 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Est | 2050 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.432
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.552
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.432
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.552
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2015 | 1
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2020 | 1
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2030 | 1
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2050 | 1
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 2.25
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 3
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2015 | 1.125
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2020 | 1.125
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2030 | 1.125
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2050 | 1.125
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2015 | 40
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2020 | 40
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2030 | 40
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2050 | 40
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2015 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2030 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2050 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.432
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.48
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.552
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Est | 2015 | 409.3985
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Est | 2020 | 409.3985
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Est | 2030 | 409.3985
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Est | 2050 | 409.3985
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2020 | 368.4586
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2050 | 331.6128
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2020 | 409.3985
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2050 | 517.8891
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2015 | 2851.2624
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2020 | 2811.3448
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2030 | 2771.9859
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2050 | 2733.1781
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2020 | 2799.9397
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2050 | 2700.0491
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2020 | 2851.2624
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2050 | 2851.2624
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 9640.5371
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 9640.5371
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 9640.5371
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 9640.5371
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 8676.4834
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 7808.835
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 9640.5371
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 9640.5371
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 1527.0032
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 1527.0032
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 1527.0032
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 1527.0032
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 1374.3029
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 1236.8726
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 1527.0032
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 1527.0032
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 4286.4554
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 4286.4554
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 4286.4554
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 4286.4554
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 3857.8099
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 3472.0289
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 4286.4554
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 4286.4554
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 4511.8904
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 4511.8904
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 4511.8904
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 4511.8904
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 4060.7014
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 3654.6313
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 4511.8904
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 4511.8904
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 85.0698
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 85.0698
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 85.0698
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 85.0698
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 74.4361
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 66.9925
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 85.0698
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 85.0698
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 79.753
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 79.753
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 79.753
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 79.753
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 69.1192
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 62.2073
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 79.753
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 79.753
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 136.1117
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 136.1117
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 136.1117
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 136.1117
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 125.478
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 112.9302
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 136.1117
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 136.1117
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2015 | 40408.1633
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2020 | 40408.1633
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2030 | 40408.1633
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2050 | 40408.1633
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2020 | 38630.2041
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2050 | 36930.4751
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2020 | 40408.1633
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2050 | 40408.1633
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2015 | 0.8
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2020 | 0.8
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2030 | 0.8
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2050 | 0.8
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2020 | 0.78
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2050 | 0.78
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2020 | 0.8
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2050 | 0.8
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2015 | 0.14
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2020 | 0.14
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2030 | 0.14
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2050 | 0.14
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.13
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.13
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.14
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.14
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2015 | 0.2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2020 | 0.2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2030 | 0.2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2050 | 0.2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2020 | 0.22
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2050 | 0.22
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2020 | 0.2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2050 | 0.2
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2015 | 0.86
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2020 | 0.86
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2030 | 0.86
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2050 | 0.86
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.87
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.87
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.86
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.86
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2015 | 12228.7863
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2020 | 12228.7863
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2030 | 12228.7863
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2050 | 12228.7863
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2020 | 11690.7197
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2050 | 11176.328
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2020 | 12228.7863
1.3 el distri suburban | Energy Transport Electricity Distribution, Suburban | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2050 | 12228.7863
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Est | 2015 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Est | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Est | 2030 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Est | 2050 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.45
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.575
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.45
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.575
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2015 | 1
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2020 | 1
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2030 | 1
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2050 | 1
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 1.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 2.25
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2015 | 1.125
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2020 | 1.125
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2030 | 1.125
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2050 | 1.125
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2015 | 40
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2020 | 40
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2030 | 40
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2050 | 40
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2015 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2030 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2050 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.45
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.5
1.4 el distri city | Energy Transport Electricity Distribution, City | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.575
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Est | 2015 | 388.131
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Est | 2020 | 388.131
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Est | 2030 | 388.131
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Est | 2050 | 388.131
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2020 | 371.4552
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2050 | 334.166
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2020 | 412.728
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2050 | 531.0492
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2015 | 3240.4576
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2020 | 3397.5728
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2030 | 3562.3058
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2050 | 3735.026
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2020 | 3383.7895
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2050 | 3263.0694
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2020 | 3445.8142
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2050 | 3445.8142
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 12899.7744
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 12899.7744
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 12899.7744
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 12899.7744
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 12345.5414
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 11815.1207
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 12899.7744
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 12899.7744
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 2285.188
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 2285.188
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 2285.188
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 2285.188
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 2187.0059
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 2093.0422
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 2285.188
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 2285.188
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 5974.0279
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 5974.0279
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 5974.0279
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 5974.0279
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 5717.3565
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 5471.7128
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 5974.0279
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 5974.0279
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 6139.9141
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 6139.9141
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 6139.9141
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 6139.9141
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 5876.1154
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 5623.6507
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 6139.9141
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 6139.9141
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 127.6047
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 127.6047
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 127.6047
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 127.6047
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 110.5908
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 105.8393
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 127.6047
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 127.6047
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 122.2879
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 122.2879
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 122.2879
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 122.2879
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 106.3373
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 101.7685
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 122.2879
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 122.2879
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 179.71
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 179.71
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 179.71
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 179.71
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 163.7594
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 156.7235
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 179.71
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 179.71
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2015 | 40408.1633
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2020 | 40408.1633
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2030 | 40408.1633
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2050 | 40408.1633
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2020 | 41078.3051
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2050 | 41759.5608
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2020 | 42968.9384
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2050 | 45691.9968
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2015 | 0.86
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2020 | 0.86
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2030 | 0.86
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2050 | 0.86
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2015 | 0.05
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2020 | 0.05
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2030 | 0.05
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2050 | 0.05
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.04
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.04
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.05
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.05
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2015 | 0.14
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2020 | 0.14
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2030 | 0.14
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2050 | 0.14
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2015 | 0.95
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2020 | 0.95
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2030 | 0.95
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2050 | 0.95
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.96
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.96
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.95
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.95
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2015 | 12228.7863
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2020 | 12228.7863
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2030 | 12228.7863
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2050 | 12228.7863
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2020 | 12431.5923
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2050 | 12637.7618
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2020 | 13003.7577
1.4 el distri city | Energy Transport Electricity Distribution, City | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2050 | 13003.7577
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Est | 2015 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Est | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Est | 2030 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Est | 2050 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Lower | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Lower | 2050 | 0.432
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Upper | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Commercial |  |  | D |  | Upper | 2050 | 0.552
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.432
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.552
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2015 | 1
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2020 | 1
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2030 | 1
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Est | 2050 | 1
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2020 | 1
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Lower | 2050 | 1
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2020 | 2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Construction time [years] | years |  |  | 5 | Upper | 2050 | 2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 3
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 3
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 3
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 3
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 2.25
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 2.25
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 3
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 3
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2015 | 1.125
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2020 | 1.125
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2030 | 1.125
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Est | 2050 | 1.125
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2020 | 0.75
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Lower | 2050 | 0.75
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2020 | 1.5
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 2 | Upper | 2050 | 1.5
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2015 | 40
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2020 | 40
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2030 | 40
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Est | 2050 | 40
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2020 | 35
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Lower | 2050 | 35
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2020 | 40
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Technical life time [years] | years |  | C | [4, 5] | Upper | 2050 | 50
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2015 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2030 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Est | 2050 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Lower | 2050 | 0.432
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2020 | 0.48
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Energy/technical data | Typical load profile [-] | - |  | D | [1, 5] | Upper | 2050 | 0.552
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Est | 2015 | 183.9635
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Est | 2020 | 183.9635
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Est | 2030 | 183.9635
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Est | 2050 | 183.9635
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2020 | 165.5671
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Lower | 2050 | 140.0698
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2020 | 183.9635
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Distribution network costs [€/MWh/year] New developed area | €/MWh/year |  | [E, F] | [1, 6] | Upper | 2050 | 218.9165
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2015 | 1444.3554
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2020 | 1424.1344
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2030 | 1404.1965
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Est | 2050 | 1384.5378
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2020 | 1418.357
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Lower | 2050 | 1367.7557
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2020 | 1444.3554
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | L | 7 | Upper | 2050 | 1444.3554
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 3982.3308
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 3982.3308
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 3982.3308
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 3982.3308
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 3584.0977
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 3225.688
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 3982.3308
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 3982.3308
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 557.2073
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 557.2073
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 557.2073
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 557.2073
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 501.4866
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 451.3379
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 557.2073
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 557.2073
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 1501.4823
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 1501.4823
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 1501.4823
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 1501.4823
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 1351.3341
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 1216.2006
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 1501.4823
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 1501.4823
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2015 | 1683.319
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2020 | 1683.319
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2030 | 1683.319
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Est | 2050 | 1683.319
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2020 | 1514.9871
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Lower | 2050 | 1363.4884
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2020 | 1683.319
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [G, F] | 6 | Upper | 2050 | 1683.319
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 43.5983
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 43.5983
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 43.5983
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 43.5983
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 39.3448
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 35.4103
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 43.5983
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 43.5983
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 34.0279
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 30.6251
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 34.0279
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 30.6251
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 38.2814
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2015 | 93.5768
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2020 | 93.5768
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2030 | 93.5768
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Est | 2050 | 93.5768
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2020 | 90.3867
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Lower | 2050 | 81.348
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2020 | 93.5768
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [H, F] | 6 | Upper | 2050 | 93.5768
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2015 | 40408.1633
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2020 | 40408.1633
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2030 | 40408.1633
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Est | 2050 | 40408.1633
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2020 | 38630.2041
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Lower | 2050 | 36930.4751
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2020 | 40408.1633
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | J | 6 | Upper | 2050 | 40408.1633
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2015 | 0.8
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2020 | 0.8
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2030 | 0.8
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Est | 2050 | 0.8
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2020 | 0.78
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Lower | 2050 | 0.78
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2020 | 0.8
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [cables] | cables |  | K | 6 | Upper | 2050 | 0.8
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2015 | 0.14
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2020 | 0.14
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2030 | 0.14
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Est | 2050 | 0.14
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2020 | 0.13
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Lower | 2050 | 0.13
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2020 | 0.14
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage installation [stations] | stations |  | K | 6 | Upper | 2050 | 0.14
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2015 | 0.2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2020 | 0.2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2030 | 0.2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Est | 2050 | 0.2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2020 | 0.22
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Lower | 2050 | 0.22
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2020 | 0.2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [cables] | cables |  | K | 6 | Upper | 2050 | 0.2
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2015 | 0.86
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2020 | 0.86
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2030 | 0.86
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Est | 2050 | 0.86
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2020 | 0.87
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Lower | 2050 | 0.87
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2020 | 0.86
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Investments, percentage materials [stations] | stations |  | K | 6 | Upper | 2050 | 0.86
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2015 | 12228.7863
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2020 | 12228.7863
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2030 | 12228.7863
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Est | 2050 | 12228.7863
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2020 | 11690.7197
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Lower | 2050 | 11176.328
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2020 | 12228.7863
1.5 el distri new area | Energy Transport Electricity Distribution, New developed areas | Financial data | Reinforcement costs [€/MW] (Station) | €/MW |  | [I, F, J] | 6 | Upper | 2050 | 12228.7863
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2025 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2030 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2035 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2040 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2045 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2050 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2025 | 2
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2050 | 2
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2025 | 4
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2050 | 4
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2025 | 5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2030 | 5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2035 | 5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2040 | 5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2045 | 5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2050 | 5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2025 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2050 | 3
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2025 | 7
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines AC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2050 | 7
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2025 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2030 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2035 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2040 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2045 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | ctrl | 2050 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2025 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | lower | 2050 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2025 | 2
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Energy losses, OH lines DC [%/100 km] at rated power | pct./100km |  | 5 | 3 | upper | 2050 | 2
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2025 | 1.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2030 | 1.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2035 | 1.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2040 | 1.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2045 | 1.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2050 | 1.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2025 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2050 | 1
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2025 | 2
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2050 | 2
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | ctrl | 2025 | 0.75
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | ctrl | 2030 | 0.75
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | ctrl | 2035 | 0.72
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | ctrl | 2040 | 0.68
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | ctrl | 2045 | 0.65
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | ctrl | 2050 | 0.62
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | lower | 2025 | 0.58
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | lower | 2050 | 0.48
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | upper | 2025 | 0.98
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,10 | 1 | upper | 2050 | 0.8
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | ctrl | 2025 | 0.6
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | ctrl | 2030 | 0.6
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | ctrl | 2035 | 0.58
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | ctrl | 2040 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | ctrl | 2045 | 0.53
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | ctrl | 2050 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | lower | 2025 | 0.46
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | lower | 2050 | 0.38
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | upper | 2025 | 0.78
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9 | 1 | upper | 2050 | 0.65
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.45
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.45
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.45
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.45
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.45
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.45
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.4
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.4
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.55
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.5
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.6
1.6 el trans OH | Overhead lines AC, Overhead lines DC | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.6
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2025 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2030 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2035 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2040 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2045 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2050 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2025 | 2
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2050 | 2
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2025 | 4
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2050 | 4
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2025 | 5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2030 | 5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2035 | 5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2040 | 5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2045 | 5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | ctrl | 2050 | 5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | lower | 2025 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | lower | 2050 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | upper | 2025 | 7
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables AC [%/100 km] at rated power | pct./100km |  | 7 |  | upper | 2050 | 7
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2025 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2030 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2035 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2040 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2045 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | ctrl | 2050 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | lower | 2025 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | lower | 2050 | 1
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | upper | 2025 | 2
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, cables DC [%/100 km] at rated power | pct./100km |  | 5 |  | upper | 2050 | 2
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2025 | 4.51
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2030 | 4.51
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2035 | 4.32
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2040 | 4.13
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2045 | 3.94
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2050 | 3.75
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | lower | 2025 | 3.47
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | lower | 2050 | 2.88
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | upper | 2025 | 5.86
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC offshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | upper | 2050 | 4.88
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2025 | 4.51
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2030 | 4.51
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2035 | 4.32
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2040 | 4.13
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2045 | 3.94
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | ctrl | 2050 | 3.75
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | lower | 2025 | 3.47
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | lower | 2050 | 2.88
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | upper | 2025 | 5.86
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | AC onshore cables [kEUR/km/MW], 500 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,9,11,12 | 1 | upper | 2050 | 4.88
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2025 | 3.22
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2030 | 3.22
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2035 | 3.09
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2040 | 2.95
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2045 | 2.82
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2050 | 2.68
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | lower | 2025 | 2.48
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | lower | 2050 | 2.06
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | upper | 2025 | 4.19
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | upper | 2050 | 3.48
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2025 | 4.07
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2030 | 4.07
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2035 | 3.91
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2040 | 3.74
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2045 | 3.57
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | ctrl | 2050 | 3.4
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | lower | 2025 | 3.13
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | lower | 2050 | 2.62
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | upper | 2025 | 5.29
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity | kEUR/km/MW | 2025 | 1,2,3,4,10,11 | 1 | upper | 2050 | 4.42
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2025 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2030 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2035 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2040 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2045 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2050 | 2.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2025 | 2
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2050 | 2
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2025 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2050 | 3
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.45
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.45
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.55
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.55
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.5
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.45
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.45
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.55
1.7 el trans AC&DC cables | Cables AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2025 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2030 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2035 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2040 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2045 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | ctrl | 2050 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2025 | 1
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | lower | 2050 | 1
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2025 | 3
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Construction time [years] | years |  | 6 |  | upper | 2050 | 3
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2025 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2030 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2035 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2040 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2045 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | ctrl | 2050 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | lower | 2025 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | lower | 2050 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | upper | 2025 | 2.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Energy losses, substation [%] | pct. |  | 5 |  | upper | 2050 | 2.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
1.8 el substations | Substations AC and DC, Onshore and Offshore | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2025 | 0.6
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2030 | 0.6
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2035 | 0.58
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2040 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2045 | 0.53
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2050 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | lower | 2025 | 0.46
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | lower | 2050 | 0.38
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | upper | 2025 | 0.78
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | upper | 2050 | 0.65
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2025 | 0.25
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2030 | 0.25
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2035 | 0.24
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2040 | 0.23
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2045 | 0.22
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | ctrl | 2050 | 0.21
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | lower | 2025 | 0.19
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | lower | 2050 | 0.16
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | upper | 2025 | 0.33
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | AC onshore substation [MEUR/MW], 500 MW capacity | MEUR/MW | 2025 | 1,2,3,4,5,9 | 1 | upper | 2050 | 0.27
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2025 | 0.75
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2030 | 0.75
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2035 | 0.72
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2040 | 0.69
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2045 | 0.66
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2050 | 0.63
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | lower | 2025 | 0.58
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | lower | 2050 | 0.48
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | upper | 2025 | 0.98
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | upper | 2050 | 0.82
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2025 | 0.32
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2030 | 0.32
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2035 | 0.3
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2040 | 0.29
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2045 | 0.28
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | ctrl | 2050 | 0.27
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | lower | 2025 | 0.25
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | lower | 2050 | 0.21
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | upper | 2025 | 0.42
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | DC onshore substation [MEUR/MW], 1500-2000 MW capacity | MEUR/MW | 2025 | 1,2,3,4,6,10 | 1 | upper | 2050 | 0.35
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2025 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2030 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2035 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2040 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2045 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2050 | 1.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2025 | 1
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2050 | 1
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2025 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2050 | 2
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.45
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.45
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.45
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.45
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.45
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.45
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.4
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.4
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.55
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.5
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.6
1.8 el substations | Substations AC and DC, Onshore and Offshore | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.6
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2025 | 0.2
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2030 | 0.2
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2035 | 0.2
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2040 | 0.2
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2045 | 0.2
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2050 | 0.2
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2025 | 0.1
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2050 | 0.1
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2025 | 0.3
1.9 el transformers | Transformers | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2050 | 0.3
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | ctrl | 2025 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | ctrl | 2030 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | ctrl | 2035 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | ctrl | 2040 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | ctrl | 2045 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | ctrl | 2050 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | lower | 2025 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | lower | 2050 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | upper | 2025 | 1
1.9 el transformers | Transformers | Energy/technical data | Energy losses, Transformer [%] | pct. |  | 5 |  | upper | 2050 | 2
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
1.9 el transformers | Transformers | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2025 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2030 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2035 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2040 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2045 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | ctrl | 2050 | 0.5
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2025 | 0.4
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | lower | 2050 | 0.4
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2025 | 0.6
1.9 el transformers | Transformers | Energy/technical data | Typical load profile (-) |  |  | 5 |  | upper | 2050 | 0.6
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 20.9
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 20.9
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 20
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 19.2
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 18.3
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 17.4
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | lower | 2025 | 16.1
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | lower | 2050 | 13.38
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | upper | 2025 | 27.2
1.9 el transformers | Transformers | Financial data | 220/110 kV, 200 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | upper | 2050 | 22.62
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 20.8
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 20.8
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 19.9
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 19.1
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 18.2
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 17.3
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | lower | 2025 | 16
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | lower | 2050 | 13.31
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | upper | 2025 | 27
1.9 el transformers | Transformers | Financial data | 380/110 kV, 300 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | upper | 2050 | 22.49
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 16
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 16
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 15.3
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 14.7
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 14
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 13.3
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | lower | 2025 | 12.3
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | lower | 2050 | 10.23
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | upper | 2025 | 20.8
1.9 el transformers | Transformers | Financial data | 380/220 kV, 600 MVA [kEUR/MVA] | kEUR/MVA | 2025 | 1,2,3,4 | 1 | upper | 2050 | 17.29
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | ctrl | 2025 | 1.5
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | ctrl | 2030 | 1.5
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | ctrl | 2035 | 1.5
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | ctrl | 2040 | 1.5
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | ctrl | 2045 | 1.5
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | ctrl | 2050 | 1.5
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | lower | 2025 | 1
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | lower | 2050 | 1
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | upper | 2025 | 2
1.9 el transformers | Transformers | Financial data | Fixed O&M [& of capex per year] | &ofcapex/year |  |  | 2 | upper | 2050 | 2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | ctrl | 2025 | 0.2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | ctrl | 2030 | 0.2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | ctrl | 2035 | 0.2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | ctrl | 2040 | 0.2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | ctrl | 2045 | 0.2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | ctrl | 2050 | 0.2
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | lower | 2025 | 0.15
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | lower | 2050 | 0.15
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | upper | 2025 | 0.25
1.9 el transformers | Transformers | Financial data | Investments, percentage installation |  |  | 6 |  | upper | 2050 | 0.25
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | ctrl | 2025 | 0.8
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | ctrl | 2030 | 0.8
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | ctrl | 2035 | 0.8
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | ctrl | 2040 | 0.8
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | ctrl | 2045 | 0.8
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | ctrl | 2050 | 0.8
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | lower | 2025 | 0.75
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | lower | 2050 | 0.75
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | upper | 2025 | 0.85
1.9 el transformers | Transformers | Financial data | Investments, percentage materials |  |  | 6 |  | upper | 2050 | 0.85
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2025 | 0.2
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2030 | 0.2
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2035 | 0.2
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2040 | 0.2
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2045 | 0.2
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | ctrl | 2050 | 0.2
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2025 | 0.1
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | lower | 2050 | 0.1
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2025 | 0.3
1.10 el compensation | Compensation | Energy/technical data | Construction time [years] | years |  | 5 |  | upper | 2050 | 0.3
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2025 | 40
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2030 | 40
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2035 | 40
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2040 | 40
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2045 | 40
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | ctrl | 2050 | 40
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2025 | 30
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | lower | 2050 | 30
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2025 | 50
1.10 el compensation | Compensation | Energy/technical data | Technical life time [years] | years |  | 5 |  | upper | 2050 | 50
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2025 | 0.5
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2030 | 0.5
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2035 | 0.5
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2040 | 0.5
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2045 | 0.5
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | ctrl | 2050 | 0.5
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | lower | 2025 | 0.4
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | lower | 2050 | 0.4
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | upper | 2025 | 0.6
1.10 el compensation | Compensation | Energy/technical data | Typical load profile (-) |  |  | 6 |  | upper | 2050 | 0.6
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 24
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 24
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 23
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 22
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 21
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 20
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2025 | 18
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2050 | 15
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2025 | 31
1.10 el compensation | Compensation | Financial data | Capacitor bank [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2050 | 26
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2025 | 1.5
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2030 | 1.5
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2035 | 1.5
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2040 | 1.5
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2045 | 1.5
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | ctrl | 2050 | 1.5
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2025 | 1
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | lower | 2050 | 1
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2025 | 2
1.10 el compensation | Compensation | Financial data | Fixed O&M [% of capex per year] | pct.ofcapex/year |  |  | 2 | upper | 2050 | 2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2025 | 0.2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2030 | 0.2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2035 | 0.2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2040 | 0.2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2045 | 0.2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | ctrl | 2050 | 0.2
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2025 | 0.15
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | lower | 2050 | 0.15
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2025 | 0.25
1.10 el compensation | Compensation | Financial data | Investments, percentage installation |  |  | 7 |  | upper | 2050 | 0.25
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2025 | 0.8
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2030 | 0.8
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2035 | 0.8
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2040 | 0.8
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2045 | 0.8
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | ctrl | 2050 | 0.8
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2025 | 0.75
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | lower | 2050 | 0.75
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2025 | 0.85
1.10 el compensation | Compensation | Financial data | Investments, percentage materials |  |  | 7 |  | upper | 2050 | 0.85
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 25
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 25
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 24
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 23
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 22
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 21
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2025 | 19
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2050 | 16
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2025 | 33
1.10 el compensation | Compensation | Financial data | Reactor [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2050 | 27
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 155
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 155
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 148
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 142
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 135
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 129
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2025 | 119
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2050 | 99
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2025 | 202
1.10 el compensation | Compensation | Financial data | STATCOM [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2050 | 168
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2025 | 60
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2030 | 60
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2035 | 58
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2040 | 55
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2045 | 53
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | ctrl | 2050 | 50
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2025 | 46
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | lower | 2050 | 38
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2025 | 78
1.10 el compensation | Compensation | Financial data | SVC [kEUR/MVAr] | kEUR/MVAr | 2025 | 1,2,3,4 | 1 | upper | 2050 | 65
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Est | 2015 | 0.005
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Est | 2020 | 0.005
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Est | 2030 | 0.005
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Est | 2050 | 0.005
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Lower | 2020 | 0.00425
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Lower | 2050 | 0.00425
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Upper | 2020 | 0.00575
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Auxiliary electricity consumption [%] of energy transmitted | pct. |  |  | 2 | Upper | 2050 | 0.00575
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Est | 2015 | 1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Est | 2020 | 1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Est | 2030 | 1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Est | 2050 | 1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Lower | 2020 | 0.7
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Lower | 2050 | 0.7
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Upper | 2020 | 1.5
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Construction time [years] | years |  | D | 2 | Upper | 2050 | 1.5
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Est | 2015 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Est | 2020 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Est | 2030 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Est | 2050 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Lower | 2020 | 0.01
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Lower | 2050 | 0.01
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Upper | 2020 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 1-20 MW [%] | pct. |  | A | 1 | Upper | 2050 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Est | 2015 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Est | 2020 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Est | 2030 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Est | 2050 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Lower | 2020 | 0.01
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Lower | 2050 | 0.01
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Upper | 2020 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines 20-100 MW [%] | pct. |  | A |  | Upper | 2050 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Est | 2015 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Est | 2020 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Est | 2030 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Est | 2050 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Lower | 2020 | 0.01
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Lower | 2050 | 0.01
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Upper | 2020 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, lines above 100 MW [%] | pct. |  | A |  | Upper | 2050 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Est | 2015 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Est | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Est | 2030 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Est | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Lower | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Lower | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Upper | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 1 [%] | pct. |  | B |  | Upper | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Est | 2015 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Est | 2020 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Est | 2030 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Est | 2050 | 0.1
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Lower | 2020 | 0
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Lower | 2050 | 0
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Upper | 2020 | 0.12
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Energy losses, stations type 2 [%] | pct. |  | C | 2 | Upper | 2050 | 0.12
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2015 | 50
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2020 | 50
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2030 | 50
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2050 | 50
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Est | 2015 | 0.2
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Est | 2020 | 0.2
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Est | 2030 | 0.2
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Est | 2050 | 0.2
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Lower | 2020 | 0.05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Lower | 2050 | 0.05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Upper | 2020 | 0.4
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Energy/technical data | Typical load profile [-] | - |  |  | 2 | Upper | 2050 | 0.4
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Est | 2015 | 0.12865
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Est | 2020 | 0.12865
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Est | 2030 | 0.12865
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Est | 2050 | 0.12865
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Lower | 2020 | 0.10292
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Lower | 2050 | 0.10292
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Upper | 2020 | 0.15438
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  | 0 | 2 | Upper | 2050 | 0.15438
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Est | 2015 | 11.4844
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Est | 2020 | 11.4844
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Est | 2030 | 11.4844
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Est | 2050 | 11.4844
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Lower | 2020 | 9.1875
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Lower | 2050 | 9.1875
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Upper | 2020 | 13.7813
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [E, F] | 2 | Upper | 2050 | 13.7813
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2015 | 2.382
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2020 | 2.382
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2030 | 2.382
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2050 | 2.382
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Lower | 2020 | 1.9056
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Lower | 2050 | 1.9056
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Upper | 2020 | 2.8583
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Upper | 2050 | 2.8583
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2015 | 1.2441
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2020 | 1.2441
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2030 | 1.2441
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2050 | 1.2441
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Lower | 2020 | 0.99532
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Lower | 2050 | 0.99532
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Upper | 2020 | 1.493
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Upper | 2050 | 1.493
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2015 | 4.4662
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2020 | 4.4662
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2030 | 4.4662
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Est | 2050 | 4.4662
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Lower | 2020 | 3.5729
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Lower | 2050 | 3.5729
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Upper | 2020 | 5.3594
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [E, G] | 2 | Upper | 2050 | 5.3594
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Est | 2015 | 0.72309
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Est | 2020 | 0.72309
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Est | 2030 | 0.72309
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Est | 2050 | 0.72309
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Lower | 2020 | 0.57847
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Lower | 2050 | 0.57847
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Upper | 2020 | 0.86771
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, 500-1000 MW [€/MW/m] | €/MW/m |  | [E, G] | 1 | Upper | 2050 | 0.86771
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Est | 2015 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Est | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Est | 2030 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Est | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Lower | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Lower | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Upper | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; single line, above 1000 MW [€/MW/m] | €/MW/m |  | i |  | Upper | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Est | 2015 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Est | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Est | 2030 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Est | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Lower | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Lower | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Upper | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 1 station [€/MW] | €/MW |  | [B, J] |  | Upper | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Est | 2015 | 28711.0634
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Est | 2020 | 28711.0634
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Est | 2030 | 28711.0634
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Est | 2050 | 28711.0634
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Lower | 2020 | 7443.609
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Lower | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Upper | 2020 | 47851.7723
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investment costs; type 2 station [€/MW] | €/MW |  | [C, K] | 2 | Upper | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2015 | 0.75
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2020 | 0.75
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2030 | 0.75
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2050 | 0.75
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.65
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.65
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.85
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.85
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2015 | 0.25
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2020 | 0.25
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2030 | 0.25
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2050 | 0.25
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.15
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.35
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.35
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2015 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2030 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2020 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2050 | -
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Est | 2015 | 1.1968e-05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Est | 2020 | 1.1968e-05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Est | 2030 | 1.1968e-05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Est | 2050 | 1.1968e-05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Lower | 2020 | 9.5743e-06
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Lower | 2050 | 9.5743e-06
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Upper | 2020 | 1.4361e-05
2.1 gas Main distri line | Energy Transport, Natural Gas Main distribution line | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  | 0 | 2 | Upper | 2050 | 1.4361e-05
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2015 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2020 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2030 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2050 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2020 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2050 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2020 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2050 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2015 | 0.4
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2020 | 0.4
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2030 | 0.4
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2050 | 0.4
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2020 | 0.3
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2050 | 0.3
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2020 | 0.5
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2050 | 0.5
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 0.26307
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 0.26307
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 0.26307
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 0.26307
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 0.05
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 0.05
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 0.3
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 0.3
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2015 | 50
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2020 | 50
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2030 | 50
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2050 | 50
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Est | 2015 | 148.8722
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Est | 2020 | 148.8722
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Est | 2030 | 148.8722
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Est | 2050 | 148.8722
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Lower | 2020 | 138.2385
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Lower | 2050 | 138.2385
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Upper | 2020 | 159.5059
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Distribution network costs [€/MWh/year], Rural | €/MWh/year |  | 0 | 2 | Upper | 2050 | 159.5059
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2015 | 797.5295
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2020 | 797.5295
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2030 | 797.5295
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2050 | 797.5295
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Lower | 2020 | 638.0236
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Lower | 2050 | 638.0236
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Upper | 2020 | 957.0354
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Upper | 2050 | 957.0354
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2015 | 1701.3963
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2020 | 1701.3963
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2030 | 1701.3963
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2050 | 1701.3963
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Lower | 2020 | 1488.7218
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Lower | 2050 | 1488.7218
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Upper | 2020 | 1914.0709
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Upper | 2050 | 1914.0709
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2015 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2020 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2030 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2050 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Lower | 2020 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Lower | 2050 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Upper | 2020 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Upper | 2050 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2015 | 56.7132
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2020 | 56.7132
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2030 | 56.7132
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2050 | 56.7132
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Lower | 2020 | 51.0419
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Lower | 2050 | 51.0419
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Upper | 2020 | 62.3845
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Upper | 2050 | 62.3845
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2015 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2020 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2030 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2050 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Lower | 2020 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Lower | 2050 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Upper | 2020 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Upper | 2050 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2015 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2020 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2030 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2050 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Lower | 2020 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Lower | 2050 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Upper | 2020 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Upper | 2050 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2015 | 72.6638
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2020 | 72.6638
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2030 | 72.6638
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2050 | 72.6638
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Lower | 2020 | 65.3974
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Lower | 2050 | 65.3974
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Upper | 2020 | 79.9302
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Upper | 2050 | 79.9302
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2015 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2020 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2030 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2050 | 53.1686
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Lower | 2020 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Lower | 2050 | 47.8518
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Upper | 2020 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Upper | 2050 | 58.4855
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2015 | 0.8
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2020 | 0.8
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2030 | 0.8
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2050 | 0.8
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.7
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.7
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.9
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.9
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2015 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2020 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2030 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2050 | 0.2
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.1
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.1
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.3
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.3
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2015 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2030 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Lower | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Lower | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Upper | 2020 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Upper | 2050 | -
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2015 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2020 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2030 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2050 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Lower | 2020 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Lower | 2050 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Upper | 2020 | 0
2.2 gas Rural | Energy Transport Natural Gas Distribution, New distribution in existing rual areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Upper | 2050 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2015 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2020 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2030 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2050 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2020 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2050 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2020 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2050 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2015 | 0.4
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2020 | 0.4
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2030 | 0.4
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2050 | 0.4
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2020 | 0.3
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2050 | 0.3
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2020 | 0.5
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2050 | 0.5
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 0.26307
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 0.26307
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 0.26307
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 0.26307
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 0.05
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 0.05
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 0.3
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 0.3
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2015 | 50
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2020 | 50
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2030 | 50
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2050 | 50
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Est | 2015 | 159.5059
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Est | 2020 | 159.5059
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Est | 2030 | 159.5059
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Est | 2050 | 159.5059
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Lower | 2020 | 148.8722
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Lower | 2050 | 148.8722
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Upper | 2020 | 180.7734
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Distribution network costs [€/MWh/year] Suburban | €/MWh/year |  | 0 | 2 | Upper | 2050 | 180.7734
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2015 | 329.6455
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2020 | 329.6455
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2030 | 329.6455
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2050 | 329.6455
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Lower | 2020 | 265.8432
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Lower | 2050 | 265.8432
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Upper | 2020 | 393.4479
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Upper | 2050 | 393.4479
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2015 | 1701.3963
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2020 | 1701.3963
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2030 | 1701.3963
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2050 | 1701.3963
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Lower | 2020 | 1488.7218
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Lower | 2050 | 1488.7218
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Upper | 2020 | 1914.0709
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Upper | 2050 | 1914.0709
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2015 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2020 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2030 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2050 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Lower | 2020 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Lower | 2050 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Upper | 2020 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Upper | 2050 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2015 | 63.8024
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2020 | 63.8024
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2030 | 63.8024
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2050 | 63.8024
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Lower | 2020 | 57.4221
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Lower | 2050 | 57.4221
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Upper | 2020 | 70.1826
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Upper | 2050 | 70.1826
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2015 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2020 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2030 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2050 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Lower | 2020 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Lower | 2050 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Upper | 2020 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Upper | 2050 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2015 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2020 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2030 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2050 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Lower | 2020 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Lower | 2050 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Upper | 2020 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Upper | 2050 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2015 | 92.159
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2020 | 92.159
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2030 | 92.159
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2050 | 92.159
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Lower | 2020 | 82.9431
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Lower | 2050 | 82.9431
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Upper | 2020 | 101.3749
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Upper | 2050 | 101.3749
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2015 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2020 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2030 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2050 | 56.7132
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Lower | 2020 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Lower | 2050 | 51.0419
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Upper | 2020 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Upper | 2050 | 62.3845
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2015 | 0.8
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2020 | 0.8
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2030 | 0.8
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2050 | 0.8
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.7
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.7
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.9
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.9
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2015 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2020 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2030 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2050 | 0.2
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.1
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.1
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.3
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.3
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2015 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2030 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Lower | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Lower | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Upper | 2020 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Upper | 2050 | -
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2015 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2020 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2030 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2050 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Lower | 2020 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Lower | 2050 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Upper | 2020 | 0
2.3 gas Suburban | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Upper | 2050 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Est | 2015 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Est | 2020 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Est | 2030 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Est | 2050 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Lower | 2020 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Lower | 2050 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Upper | 2020 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C | 1 | Upper | 2050 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2015 | 0.4
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2020 | 0.4
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2030 | 0.4
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2050 | 0.4
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2020 | 0.3
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2050 | 0.3
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2020 | 0.5
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2050 | 0.5
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B | 1 | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Est | 2015 | 50
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Est | 2020 | 50
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Est | 2030 | 50
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Est | 2050 | 50
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Lower | 2020 | 50
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Lower | 2050 | 50
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Upper | 2020 | 80
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Energy/technical data | Technical life time [years] | years |  |  | 1 | Upper | 2050 | 80
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Est | 2015 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Est | 2020 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Est | 2030 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Est | 2050 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Lower | 2020 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Lower | 2050 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Upper | 2020 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 1 | Upper | 2050 | 10.6337
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Est | 2015 | 21.2675
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Est | 2020 | 21.2675
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Est | 2030 | 21.2675
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Est | 2050 | 21.2675
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Lower | 2020 | 17.014
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Lower | 2050 | 17.014
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Upper | 2020 | 25.5209
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 1 | Upper | 2050 | 25.5209
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | 0 |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | 0 |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Est | 2015 | 15950.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Est | 2020 | 15950.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Est | 2030 | 15950.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Est | 2050 | 15950.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Lower | 2020 | 12760.4726
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Lower | 2050 | 12760.4726
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Upper | 2020 | 19140.7089
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E | 1 | Upper | 2050 | 19140.7089
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Est | 2015 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Est | 2020 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Est | 2030 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Est | 2050 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Lower | 2020 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Lower | 2050 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Upper | 2020 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | 0 | 1 | Upper | 2050 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Est | 2015 | 76.5628
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Est | 2020 | 76.5628
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Est | 2030 | 76.5628
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Est | 2050 | 76.5628
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Lower | 2020 | 68.9066
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Lower | 2050 | 68.9066
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Upper | 2020 | 84.2191
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | 0 | 1 | Upper | 2050 | 84.2191
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2015 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2020 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2030 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2050 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Lower | 2020 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Lower | 2050 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Upper | 2020 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | 0 | 1 | Upper | 2050 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | F |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Est | 2015 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Est | 2020 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Est | 2030 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Est | 2050 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Lower | 2020 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Lower | 2050 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Upper | 2020 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | 0 | 1 | Upper | 2050 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Est | 2015 | 110.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Est | 2020 | 110.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Est | 2030 | 110.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Est | 2050 | 110.5908
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Lower | 2020 | 99.5317
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Lower | 2050 | 99.5317
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Upper | 2020 | 121.6498
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | 0 | 1 | Upper | 2050 | 121.6498
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2015 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2020 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2030 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Est | 2050 | 68.0559
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Lower | 2020 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Lower | 2050 | 61.2503
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Upper | 2020 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | 0 | 1 | Upper | 2050 | 74.8614
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Est | 2015 | 0.8
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Est | 2020 | 0.8
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Est | 2030 | 0.8
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Est | 2050 | 0.8
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Lower | 2020 | 0.7
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Lower | 2050 | 0.7
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Upper | 2020 | 0.9
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage installation |  |  | 0 | 1 | Upper | 2050 | 0.9
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Est | 2015 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Est | 2020 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Est | 2030 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Est | 2050 | 0.2
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Lower | 2020 | 0.1
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Lower | 2050 | 0.1
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Upper | 2020 | 0.3
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Investments, percentage materials |  |  | 0 | 1 | Upper | 2050 | 0.3
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | F |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 1 station [€/MW] | €/MW |  | F |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Est | 2015 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Est | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Est | 2030 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Est | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Lower | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Lower | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Upper | 2020 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Type 2 station [€/MW] | €/MW |  | F |  | Upper | 2050 | -
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Est | 2015 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Est | 2020 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Est | 2030 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Est | 2050 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Lower | 2020 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Lower | 2050 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Upper | 2020 | 0
2.4 gas City | Energy Transport Natural Gas Distribution, New distribution in existing city areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 1 | Upper | 2050 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Est | 2015 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Est | 2020 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Est | 2030 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Est | 2050 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2020 | 0.15
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Lower | 2050 | 0.15
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2020 | 0.25
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | - Residential |  |  | D |  | Upper | 2050 | 0.25
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2015 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2020 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2030 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Est | 2050 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2020 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Lower | 2050 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2020 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  | C |  | Upper | 2050 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2015 | 0.4
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2020 | 0.4
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2030 | 0.4
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Est | 2050 | 0.4
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2020 | 0.3
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Lower | 2050 | 0.3
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2020 | 0.5
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Construction time [years] | years |  |  | 2 | Upper | 2050 | 0.5
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2015 | 0.26307
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2020 | 0.26307
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2030 | 0.26307
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Est | 2050 | 0.26307
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2020 | 0.05
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Lower | 2050 | 0.05
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2020 | 0.3
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, lines [%] | pct. |  | A | 1 | Upper | 2050 | 0.3
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Energy losses, stations [%] | pct. |  | B |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2015 | 50
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2020 | 50
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2030 | 50
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Est | 2050 | 50
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2020 | 50
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Lower | 2050 | 50
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2020 | 80
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Technical life time [years] | years |  |  | 2 | Upper | 2050 | 80
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Energy/technical data | Typical load profile [-] | - |  |  |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Est | 2015 | 287.1106
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Est | 2020 | 287.1106
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Est | 2030 | 287.1106
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Est | 2050 | 287.1106
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Lower | 2020 | 255.2095
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Lower | 2050 | 255.2095
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Upper | 2020 | 319.0118
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Distribution network costs [€/MWh/year] City | €/MWh/year |  | 0 | 2 | Upper | 2050 | 319.0118
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2015 | 978.3029
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2020 | 978.3029
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2030 | 978.3029
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Est | 2050 | 978.3029
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Lower | 2020 | 786.8958
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Lower | 2050 | 786.8958
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Upper | 2020 | 1169.71
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | 0 | 2 | Upper | 2050 | 1169.71
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2015 | 1701.3963
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2020 | 1701.3963
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2030 | 1701.3963
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Est | 2050 | 1701.3963
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Lower | 2020 | 1488.7218
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Lower | 2050 | 1488.7218
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Upper | 2020 | 1914.0709
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | 0 | 2 | Upper | 2050 | 1914.0709
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | E |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2015 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2020 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2030 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Est | 2050 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Lower | 2020 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Lower | 2050 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Upper | 2020 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | F |  | Upper | 2050 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2015 | 53.1686
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2020 | 53.1686
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2030 | 53.1686
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Est | 2050 | 53.1686
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Lower | 2020 | 47.8518
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Lower | 2050 | 47.8518
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Upper | 2020 | 58.4855
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | G |  | Upper | 2050 | 58.4855
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2015 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2020 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2030 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Est | 2050 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Lower | 2020 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Lower | 2050 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Upper | 2020 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | F |  | Upper | 2050 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | 0 |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2015 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2020 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2030 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Est | 2050 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Lower | 2020 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Lower | 2050 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Upper | 2020 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | F |  | Upper | 2050 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2015 | 67.3469
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2020 | 67.3469
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2030 | 67.3469
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Est | 2050 | 67.3469
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Lower | 2020 | 60.6122
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Lower | 2050 | 60.6122
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Upper | 2020 | 74.0816
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | G |  | Upper | 2050 | 74.0816
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2015 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2020 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2030 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Est | 2050 | 49.6241
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Lower | 2020 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Lower | 2050 | 44.6617
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Upper | 2020 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | F |  | Upper | 2050 | 54.5865
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2015 | 0.8
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2020 | 0.8
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2030 | 0.8
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Est | 2050 | 0.8
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2020 | 0.7
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Lower | 2050 | 0.7
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2020 | 0.9
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage installation |  |  | 0 | 2 | Upper | 2050 | 0.9
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2015 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2020 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2030 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Est | 2050 | 0.2
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2020 | 0.1
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Lower | 2050 | 0.1
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2020 | 0.3
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Investments, percentage materials |  |  | 0 | 2 | Upper | 2050 | 0.3
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Reinforcement costs [€/MW] | €/MW |  | H |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 1 station [€/MW] | €/MW |  | I |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2015 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2030 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Est | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Lower | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Lower | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Upper | 2020 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Type 2 station [€/MW] | €/MW |  | I |  | Upper | 2050 | -
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2015 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2020 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2030 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Est | 2050 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Lower | 2020 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Lower | 2050 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Upper | 2020 | 0
2.5 gas New area | Energy Transport Natural Gas Distribution, New developed residential areas | Financial data | Variable O&M [€/MWh] | €/MWh |  | 0 | 2 | Upper | 2050 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Est | 2020 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Est | 2025 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Est | 2030 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Est | 2035 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Est | 2040 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Est | 2050 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Lower | 2025 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Lower | 2050 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Upper | 2025 | 2
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Auxiliary electricity consumption [%] energy transmitted | pct. |  |  | [1, 4] | Upper | 2050 | 2
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2020 | 2.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2025 | 2.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2030 | 2.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2035 | 2.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2040 | 2.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Est | 2050 | 2.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2025 | 1.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Lower | 2050 | 1.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2025 | 4
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Construction time [years] | years |  |  | 1 | Upper | 2050 | 4
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Est | 2020 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Est | 2025 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Est | 2030 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Est | 2035 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Est | 2040 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Est | 2050 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Lower | 2025 | 0.8
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Lower | 2050 | 0.8
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Upper | 2025 | 1.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Heat exchanger stations [%] | pct. |  |  | 1 | Upper | 2050 | 1.2
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Est | 2020 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Est | 2025 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Est | 2030 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Est | 2035 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Est | 2040 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Est | 2050 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Lower | 2025 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Lower | 2050 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Upper | 2025 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, Pumping stations [%] | pct. |  | G | 1 | Upper | 2050 | 0
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2020 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2025 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2030 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2035 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2040 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2050 | 1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2025 | 0.8
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2050 | 0.8
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2025 | 1.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 1-20 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2050 | 1.2
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2020 | 0.25
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2025 | 0.25
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2030 | 0.25
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2035 | 0.25
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2040 | 0.25
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2050 | 0.25
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2025 | 0.2
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2050 | 0.2
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2025 | 0.375
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines 20-100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2050 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2020 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2025 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2030 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2035 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2040 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Est | 2050 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2025 | 0.08
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Lower | 2050 | 0.08
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2025 | 0.15
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Energy losses, lines above 100 MW [% per km] | pct./km |  | A | [1, 2] | Upper | 2050 | 0.12
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Est | 2020 | 45
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Est | 2025 | 45
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Est | 2030 | 45
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Est | 2035 | 45
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Est | 2040 | 45
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Est | 2050 | 45
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Lower | 2025 | 30
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Lower | 2050 | 30
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Upper | 2025 | 60
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Technical life time [years] | years |  | B | [1, 2] | Upper | 2050 | 60
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Est | 2020 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Est | 2025 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Est | 2030 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Est | 2035 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Est | 2040 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Est | 2050 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Lower | 2025 | 0.4
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Lower | 2050 | 0.4
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Upper | 2025 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Energy/technical data | Typical load profile [-] | - |  |  | 1 | Upper | 2050 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Est | 2020 | 100
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Est | 2025 | 100
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Est | 2030 | 100
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Est | 2035 | 100
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Est | 2040 | 100
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Est | 2050 | 100
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Lower | 2025 | 50
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Lower | 2050 | 50
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Upper | 2025 | 200
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Fixed O&M [€/MW/km/year] | €/MW/km/year |  |  |  | Upper | 2050 | 200
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2020 | 55.9207
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2025 | 63.1948
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2030 | 63.1948
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2035 | 63.1948
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2040 | 63.1948
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2050 | 63.1948
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2025 | 50.7489
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2050 | 50.7489
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2025 | 75.0024
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 0-50 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2050 | 75.0024
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2020 | 17.477
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2025 | 19.7504
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2030 | 19.7504
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2035 | 19.7504
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2040 | 19.7504
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2050 | 19.7504
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2025 | 15.8655
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2050 | 15.8655
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2025 | 23.4058
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 100-250 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2050 | 23.4058
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2020 | 10.5204
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2025 | 11.8888
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2030 | 11.8888
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2035 | 11.8888
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2040 | 11.8888
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2050 | 11.8888
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2025 | 9.5484
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2050 | 9.5484
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2025 | 14.0843
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 250-500 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2050 | 14.0843
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2020 | 27.9431
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2025 | 31.5779
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2030 | 31.5779
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2035 | 31.5779
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2040 | 31.5779
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Est | 2050 | 31.5779
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2025 | 25.4138
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Lower | 2050 | 25.4138
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2025 | 37.4085
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment costs; single line, 50-100 MW [€/MW/m] | €/MW/m |  | [C, D] | [1, 3] | Upper | 2050 | 37.4085
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Est | 2020 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Est | 2025 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Est | 2030 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Est | 2035 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Est | 2040 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Est | 2050 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Lower | 2025 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Lower | 2050 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Upper | 2025 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investment, percentage soft cost |  |  | F | 2 | Upper | 2050 | 0.1
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Est | 2020 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Est | 2025 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Est | 2030 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Est | 2035 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Est | 2040 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Est | 2050 | 0.6
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Lower | 2025 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Lower | 2050 | 0.5
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Upper | 2025 | 0.7
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage installation |  |  | C | 2 | Upper | 2050 | 0.7
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Est | 2020 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Est | 2025 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Est | 2030 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Est | 2035 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Est | 2040 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Est | 2050 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Lower | 2025 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Lower | 2050 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Upper | 2025 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Investments, percentage materials |  |  |  | 2 | Upper | 2050 | 0.3
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Est | 2020 | 0.10634
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Est | 2025 | 0.11663
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Est | 2030 | 0.11663
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Est | 2035 | 0.11663
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Est | 2040 | 0.11663
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Est | 2050 | 0.11663
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Lower | 2025 | 0.038487
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Lower | 2050 | 0.038487
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Upper | 2025 | 1.7494
3.1 DH transmission | Energy Transport District Heating Transmission | Financial data | Variable O&M [€/MWh/km] | €/MWh/km |  |  | [1, 4] | Upper | 2050 | 1.7494
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Est | 2020 | 122287.8884
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Est | 2025 | 140161.8193
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Est | 2030 | 140161.8193
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Est | 2035 | 140161.8193
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Est | 2040 | 140161.8193
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Est | 2050 | 140161.8193
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Lower | 2025 | 77089.0006
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Lower | 2050 | 77089.0006
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Upper | 2025 | 168194.1831
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Heat exchanger station [€/MW] | €/MW |  |  | 1 | Upper | 2050 | 168194.1831
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Est | 2020 | 111654.0923
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Est | 2025 | 127473.1986
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Est | 2030 | 127473.1986
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Est | 2035 | 127473.1986
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Est | 2040 | 127473.1986
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Est | 2050 | 127473.1986
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Lower | 2025 | 70110.2592
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Lower | 2050 | 70110.2592
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Upper | 2025 | 152967.8384
3.1 DH transmission | Energy Transport District Heating Transmission | Technology-specific data | Investment costs; Pump station [€/MW] | €/MW |  |  | 1 | Upper | 2050 | 152967.8384
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Est | 2020 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Est | 2025 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Est | 2030 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Est | 2035 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Est | 2040 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Est | 2050 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Lower | 2025 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Lower | 2050 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Upper | 2025 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Commercial |  |  |  |  | Upper | 2050 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Est | 2020 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Est | 2025 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Est | 2030 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Est | 2035 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Est | 2040 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Est | 2050 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Lower | 2025 | 0.18
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Lower | 2050 | 0.18
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Upper | 2025 | 0.22
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | - Residential |  |  |  |  | Upper | 2050 | 0.22
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2020 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2025 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2030 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2035 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2040 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2050 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2025 | 0.5
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2050 | 0.5
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2025 | 3
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2050 | 3
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2020 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2025 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2030 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2035 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2040 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2050 | 2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2025 | 1
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 1
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2025 | 3
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 3
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2020 | 12.4
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2025 | 12.4
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2030 | 12.4
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2035 | 12.4
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2040 | 12.4
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2050 | 12.4
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2025 | 10
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2050 | 9
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2025 | 16
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2050 | 14
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2020 | 45
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2025 | 45
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2030 | 45
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2035 | 45
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2040 | 45
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2050 | 45
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2025 | 30
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2050 | 30
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2025 | 60
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2050 | 60
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2020 | 1000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2025 | 1000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2030 | 1000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2035 | 1000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2040 | 1000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2050 | 1000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Lower | 2025 | 750
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Lower | 2050 | 750
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Upper | 2025 | 2000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Upper | 2050 | 2000
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Est | 2020 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Est | 2025 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Est | 2030 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Est | 2035 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Est | 2040 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Est | 2050 | 0.15
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Lower | 2025 | 0.1
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Lower | 2050 | 0.1
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Upper | 2025 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investment, percentage soft costs percentage |  |  | H | 2 | Upper | 2050 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2020 | 6.4626
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2025 | 7.3032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2030 | 7.3032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2035 | 7.3032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2040 | 7.3032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2050 | 7.3032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Lower | 2025 | 5.4797
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Lower | 2050 | 5.4797
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Upper | 2025 | 9.0684
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Upper | 2050 | 9.0684
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2020 | 0.6
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2025 | 0.6
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2030 | 0.6
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2035 | 0.6
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2040 | 0.6
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2050 | 0.6
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2025 | 0.5
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2050 | 0.5
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2025 | 0.7
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2050 | 0.7
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2020 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2025 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2030 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2035 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2040 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2050 | 0.25
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2025 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2050 | 0.2
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2025 | 0.3
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2050 | 0.3
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2020 | 2.0107
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2025 | 2.0107
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2030 | 2.0107
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2035 | 2.0107
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2040 | 2.0107
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2050 | 2.0107
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Lower | 2025 | 1.508
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Lower | 2050 | 1.508
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Upper | 2025 | 3.0161
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Upper | 2050 | 3.0161
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 4164.6016
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 4706.3255
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 4706.3255
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 4706.3255
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 4706.3255
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 4706.3255
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 3242.5827
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 3242.5827
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 6192.4458
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 6192.4458
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 4518.7972
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 5106.5942
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 5106.5942
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 5106.5942
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 5106.5942
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 5106.5942
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 3547.7252
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 3547.7252
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 6678.7487
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 6678.7487
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 4987.2013
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 5635.9275
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 5635.9275
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 5635.9275
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 5635.9275
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 5635.9275
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 3953.0763
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 3953.0763
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 7309.6865
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 7309.6865
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 308.4523
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 348.5752
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 348.5752
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 348.5752
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 348.5752
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 348.5752
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 241.1895
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 241.1895
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 455.9609
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 455.9609
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 724.6157
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 818.8724
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 818.8724
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 818.8724
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 818.8724
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 818.8724
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 646.1684
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 646.1684
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 971.0722
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 971.0722
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 406.5826
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 459.4701
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 459.4701
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 459.4701
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 459.4701
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 459.4701
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 342.0119
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 342.0119
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 576.9283
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 576.9283
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 515.5657
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 582.6296
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 582.6296
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 582.6296
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 582.6296
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 582.6296
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 456.5441
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 456.5441
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 700.0145
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 700.0145
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 1308.5602
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 1478.7753
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 1478.7753
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 1478.7753
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 1478.7753
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 1478.7753
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 1184.4561
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 1184.4561
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 1752.5903
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 1752.5903
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 389.9116
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 440.6306
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 440.6306
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 440.6306
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 440.6306
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 440.6306
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 327.206
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 327.206
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 554.0552
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 554.0552
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2020 | 98736.0339
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2025 | 112724.915
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2030 | 112724.915
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2035 | 112724.915
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2040 | 112724.915
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2050 | 112724.915
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2025 | 61998.7032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2050 | 61998.7032
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2025 | 135269.898
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2050 | 135269.898
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2020 | 255209.4707
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2025 | 291367.4445
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2030 | 263879.9497
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2035 | 263879.9497
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2040 | 263879.9497
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2050 | 263879.9497
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2025 | 160252.0945
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2050 | 160252.0945
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2025 | 349640.9333
3.2 DH_Distribu Suburb | Energy Transport District Heating Distribution, Suburban | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2050 | 349640.9333
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Est | 2020 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Est | 2025 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Est | 2030 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Est | 2035 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Est | 2040 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Est | 2050 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Lower | 2025 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Lower | 2050 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Upper | 2025 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Commercial |  |  |  |  | Upper | 2050 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Est | 2020 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Est | 2025 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Est | 2030 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Est | 2035 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Est | 2040 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Est | 2050 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Lower | 2025 | 0.18
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Lower | 2050 | 0.18
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Upper | 2025 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | - Residential |  |  |  |  | Upper | 2050 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2020 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2025 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2030 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2035 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2040 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2050 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2025 | 0.5
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2050 | 0.5
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2025 | 3
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2050 | 3
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2020 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2025 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2030 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2035 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2040 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2050 | 2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2025 | 1
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 1
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2025 | 3
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 3
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2020 | 7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2025 | 7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2030 | 7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2035 | 7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2040 | 7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2050 | 7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2025 | 5
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2050 | 4
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2025 | 9
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2050 | 8
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2020 | 45
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2025 | 45
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2030 | 45
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2035 | 45
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2040 | 45
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2050 | 45
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2025 | 30
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2050 | 30
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2025 | 60
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2050 | 60
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2020 | 1000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2025 | 1000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2030 | 1000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2035 | 1000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2040 | 1000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2050 | 1000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Lower | 2025 | 750
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Lower | 2050 | 750
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Upper | 2025 | 2000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Upper | 2050 | 2000
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2020 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2025 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2030 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2035 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2040 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2050 | 0.15
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2025 | 0.1
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2050 | 0.1
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2025 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2050 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2020 | 5.968
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2025 | 6.7443
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2030 | 6.7443
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2035 | 6.7443
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2040 | 6.7443
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2050 | 6.7443
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Lower | 2025 | 5.0474
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Lower | 2050 | 5.0474
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Upper | 2025 | 8.3655
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Upper | 2050 | 8.3655
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2020 | 0.6
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2025 | 0.6
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2030 | 0.6
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2035 | 0.6
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2040 | 0.6
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2050 | 0.6
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2025 | 0.5
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2050 | 0.5
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2025 | 0.7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2050 | 0.7
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2020 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2025 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2030 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2035 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2040 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2050 | 0.25
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2025 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2050 | 0.2
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2025 | 0.3
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2050 | 0.3
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2020 | 2.0107
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2025 | 2.0107
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2030 | 2.0107
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2035 | 2.0107
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2040 | 2.0107
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2050 | 2.0107
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Lower | 2025 | 1.508
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Lower | 2050 | 1.508
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Upper | 2025 | 3.0161
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Upper | 2050 | 3.0161
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 4961.2182
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 5606.5644
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 5606.5644
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 5606.5644
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 5606.5644
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 5606.5644
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 3804.7675
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 3804.7675
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 7431.9167
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 7431.9167
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 5333.929
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 6027.7568
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 6027.7568
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 6027.7568
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 6027.7568
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 6027.7568
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 4135.3976
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 4135.3976
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 7883.1671
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 7883.1671
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 5826.9859
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 6584.9497
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 6584.9497
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 6584.9497
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 6584.9497
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 6584.9497
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 4627.3368
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 4627.3368
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 8482.0584
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 8482.0584
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Est | 2020 | 7159.8328
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Est | 2025 | 8091.1709
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Est | 2030 | 8091.1709
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Est | 2035 | 8091.1709
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Est | 2040 | 8091.1709
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Est | 2050 | 8091.1709
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Lower | 2025 | 6264.0232
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Lower | 2050 | 6264.0232
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Upper | 2025 | 9918.3185
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; service line, above 100 kW [€/unit] | €/unit |  | [B, E, F, J, K] | [1, 3] | Upper | 2050 | 9918.3185
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 338.688
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 382.7439
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 382.7439
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 382.7439
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 382.7439
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 382.7439
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 262.3075
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 262.3075
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 506.8973
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 506.8973
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 773.1749
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 873.7481
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 873.7481
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 873.7481
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 873.7481
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 873.7481
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 691.7201
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 691.7201
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 1035.2719
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 1035.2719
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 441.2294
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 498.6238
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 498.6238
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 498.6238
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 498.6238
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 498.6238
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 372.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 372.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 624.7824
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 624.7824
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Est | 2020 | 2532.9797
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Est | 2025 | 2862.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Est | 2030 | 2862.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Est | 2035 | 2862.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Est | 2040 | 2862.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Est | 2050 | 2862.4651
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Lower | 2025 | 2305.633
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Lower | 2050 | 2305.633
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Upper | 2025 | 3393.1957
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 25 MW-100 MW [€/m] | €/m |  | [B, E, G, L] | [1, 3] | Upper | 2050 | 3393.1957
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 551.4741
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 623.2089
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 623.2089
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 623.2089
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 623.2089
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 623.2089
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 488.4229
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 488.4229
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 749.2944
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 749.2944
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 1390.4364
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 1571.3019
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 1571.3019
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 1571.3019
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 1571.3019
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 1571.3019
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 1258.996
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 1258.996
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 1863.1035
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 1863.1035
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 380.2063
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 429.6629
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 429.6629
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 429.6629
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 429.6629
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 429.6629
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 303.189
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 303.189
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 559.8538
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Investment costs; single line, 50-100 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 559.8538
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2020 | 98736.0339
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2025 | 112724.915
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2030 | 112724.915
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2035 | 112724.915
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2040 | 112724.915
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2050 | 112724.915
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2025 | 61998.7032
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2050 | 61998.7032
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2025 | 135269.898
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2050 | 143842.3191
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2020 | 255209.4707
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2025 | 291367.4445
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2030 | 291367.4445
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2035 | 291367.4445
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2040 | 291367.4445
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2050 | 291367.4445
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2025 | 160252.0945
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2050 | 160252.0945
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2025 | 349640.9333
3.3 DH_Distribu City | Energy Transport District Heating Distribution, City | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2050 | 349640.9333
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Est | 2020 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Est | 2025 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Est | 2030 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Est | 2035 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Est | 2040 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Est | 2050 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Lower | 2025 | 0.1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Lower | 2050 | 0.1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Upper | 2025 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Commercial |  |  |  |  | Upper | 2050 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Est | 2020 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Est | 2025 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Est | 2030 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Est | 2035 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Est | 2040 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Est | 2050 | 0.17
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Lower | 2025 | 0.1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Lower | 2050 | 0.1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Upper | 2025 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | - Residential |  |  |  |  | Upper | 2050 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2020 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2025 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2030 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2035 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2040 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Est | 2050 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2025 | 0.5
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Lower | 2050 | 0.5
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2025 | 3
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Auxiliary electricity consumption [%] of energy delivered | pct. |  |  | 4 | Upper | 2050 | 3
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2020 | 1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2025 | 1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2030 | 1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2035 | 1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2040 | 1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Est | 2050 | 1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2025 | 0.5
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | 0.5
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2025 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | 2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2020 | 18
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2025 | 18
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2030 | 18
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2035 | 18
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2040 | 18
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Est | 2050 | 18
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2025 | 12
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Lower | 2050 | 10
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2025 | 24
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Energy losses, network [%] | pct. |  | [A, B] | 2 | Upper | 2050 | 20
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2020 | 45
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2025 | 45
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2030 | 45
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2035 | 45
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2040 | 45
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Est | 2050 | 45
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2025 | 30
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Lower | 2050 | 30
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2025 | 60
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Energy/technical data | Technical life time [years] | years |  | C | 2 | Upper | 2050 | 60
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2020 | 1000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2025 | 1000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2030 | 1000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2035 | 1000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2040 | 1000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Est | 2050 | 1000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Lower | 2025 | 750
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Lower | 2050 | 750
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Upper | 2025 | 2000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Fixed O&M [€/MW/year] | €/MW/year |  | M | 1 | Upper | 2050 | 2000
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2020 | 0.15
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2025 | 0.15
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2030 | 0.15
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2035 | 0.15
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2040 | 0.15
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Est | 2050 | 0.15
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2025 | 0.1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Lower | 2050 | 0.1
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2025 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investment, percentage soft costs |  |  | H | 2 | Upper | 2050 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2020 | 4.7197
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2025 | 5.3336
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2030 | 5.3336
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2035 | 5.3336
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2040 | 5.3336
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Est | 2050 | 5.3336
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Lower | 2025 | 3.9965
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Lower | 2050 | 3.9965
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Upper | 2025 | 6.6191
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments cost, distribution network [M€/km2] | M€/km2 |  | [D, E] | [1, 3] | Upper | 2050 | 6.6191
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2020 | 0.6
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2025 | 0.6
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2030 | 0.6
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2035 | 0.6
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2040 | 0.6
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Est | 2050 | 0.6
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2025 | 0.5
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Lower | 2050 | 0.5
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2025 | 0.7
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage installation |  |  | E | 2 | Upper | 2050 | 0.7
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2020 | 0.25
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2025 | 0.25
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2030 | 0.25
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2035 | 0.25
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2040 | 0.25
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Est | 2050 | 0.25
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2025 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Lower | 2050 | 0.2
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2025 | 0.3
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Investments, percentage materials |  |  | E | 2 | Upper | 2050 | 0.3
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2020 | 1.5951
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2025 | 1.7494
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2030 | 1.7494
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2035 | 1.7494
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2040 | 1.7494
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Est | 2050 | 1.7494
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Lower | 2025 | 1.3121
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Lower | 2050 | 1.3121
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Upper | 2025 | 2.6241
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Financial data | Variable O&M [€/MWh] | €/MWh |  | M | [1, 4] | Upper | 2050 | 2.6241
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 3504.3785
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 3960.2217
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 3960.2217
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 3960.2217
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 3960.2217
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 3960.2217
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 2706.7547
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 2706.7547
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 5231.3553
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 0-20 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 5231.3553
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 3783.9591
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 4276.1697
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 4276.1697
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 4276.1697
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 4276.1697
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 4276.1697
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 2951.1919
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 2951.1919
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 5592.5358
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 20-50 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 5592.5358
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2020 | 4153.7518
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2025 | 4694.0644
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2030 | 4694.0644
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2035 | 4694.0644
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2040 | 4694.0644
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Est | 2050 | 4694.0644
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2025 | 3295.6762
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Lower | 2050 | 3295.6762
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2025 | 6066.1745
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; service line, 50-100 kW [€/unit] | €/unit |  | [B, E, F, J] | [1, 3] | Upper | 2050 | 6066.1745
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 242.6776
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 274.2447
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 274.2447
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 274.2447
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 274.2447
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 274.2447
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 188.8114
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 188.8114
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 361.0718
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 0-50 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 361.0718
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 561.6715
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 634.7327
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 634.7327
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 634.7327
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 634.7327
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 634.7327
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 501.7082
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 501.7082
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 752.3791
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 1 MW-5 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 752.3791
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 317.9295
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 359.2852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 359.2852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 359.2852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 359.2852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 359.2852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 267.9289
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 267.9289
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 450.6415
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 100-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 450.6415
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 400.1399
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 452.1894
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 452.1894
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 452.1894
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 452.1894
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 452.1894
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 354.3626
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 354.3626
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 543.4908
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 250 kW-1 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 543.4908
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 1012.1237
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 1143.779
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 1143.779
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 1143.779
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 1143.779
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 1143.779
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 916.2945
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 916.2945
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 1355.8852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 5 MW-25 MW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 1355.8852
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2020 | 302.329
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2025 | 341.6554
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2030 | 341.6554
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2035 | 341.6554
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2040 | 341.6554
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Est | 2050 | 341.6554
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2025 | 253.3243
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Lower | 2050 | 253.3243
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2025 | 431.3804
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Investment costs; single line, 50-250 kW [€/m] | €/m |  | [B, E, G] | [1, 3] | Upper | 2050 | 431.3804
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2020 | 92764.2348
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2025 | 105907.0338
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2030 | 105907.0338
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2035 | 105907.0338
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2040 | 105907.0338
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2050 | 105907.0338
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2025 | 59307.9389
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2050 | 59307.9389
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2025 | 127088.4405
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station above 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2050 | 127088.4405
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2020 | 247371.1906
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2025 | 282418.6401
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2030 | 282418.6401
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2035 | 282418.6401
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2040 | 282418.6401
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Est | 2050 | 282418.6401
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2025 | 158154.4384
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Lower | 2050 | 158154.4384
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2025 | 338902.3681
3.4 DH_Distribu New area | Energy Transport District Heating Distribution, New Area | Technology-specific data | Pumping station below 1 MW [€/MW] | €/MW |  | I | 1 | Upper | 2050 | 338902.3681
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2025 | 2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2030 | 2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2035 | 2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2040 | 2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2050 | 2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Lower | 2025 | 1.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Lower | 2050 | 1.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Upper | 2025 | 2.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Upper | 2050 | 2.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.011506
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.011506
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.011506
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.011506
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.011506
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.008
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.008
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.017
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.017
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0092266
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0092266
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0092266
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0092266
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0092266
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.006
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.006
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.014
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.014
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0049895
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0049895
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0049895
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0049895
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0049895
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.003
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.003
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.007
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.007
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0030745
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0030745
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0030745
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0030745
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0030745
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.002
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.002
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.005
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.005
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0024755
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0024755
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0024755
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0024755
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0024755
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.002
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.002
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.004
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.004
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.015092
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.015092
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.015092
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.015092
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.015092
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.011
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.011
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.023
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.023
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2025 | 50
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2030 | 50
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2035 | 50
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2040 | 50
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2050 | 50
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Lower | 2025 | 45
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Lower | 2050 | 45
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Upper | 2025 | 55
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Upper | 2050 | 55
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2025 | 0.85
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2030 | 0.85
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2035 | 0.85
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2040 | 0.85
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2050 | 0.85
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Lower | 2025 | 0.8
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Lower | 2050 | 0.8
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Upper | 2025 | 0.9
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Upper | 2050 | 0.9
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2025 | 0.35
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2030 | 0.35
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2035 | 0.35
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2040 | 0.35
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2050 | 0.35
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Lower | 2025 | 0.3
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Lower | 2050 | 0.3
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Upper | 2025 | 0.4
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Upper | 2050 | 0.4
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2025 | 0.01
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2030 | 0.01
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2035 | 0.01
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2040 | 0.01
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2050 | 0.01
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.03
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.03
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.03
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.03
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.03
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.721
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.721
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.545
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.545
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.14
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.14
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.14
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.14
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.14
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.798
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.798
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.71
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.71
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.41
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.41
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.41
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.41
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.41
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.987
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.987
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 2.115
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 2.115
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 2.13
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 2.13
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 2.13
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 2.13
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 2.13
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 1.491
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 1.491
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 3.195
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 3.195
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 2.65
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 2.65
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 2.65
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 2.65
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 2.65
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 1.855
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 1.855
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 3.975
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 3.975
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 0.92
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 0.92
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 0.92
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 0.92
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 0.92
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.644
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.644
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.38
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.38
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2025 | 0.56
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2030 | 0.56
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2035 | 0.56
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2040 | 0.56
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2050 | 0.56
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Lower | 2025 | 0.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Lower | 2050 | 0.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Upper | 2025 | 0.6
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Upper | 2050 | 0.6
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2025 | 0.44
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2030 | 0.44
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2035 | 0.44
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2040 | 0.44
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2050 | 0.44
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Lower | 2025 | 0.4
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Lower | 2050 | 0.4
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Upper | 2025 | 0.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Upper | 2050 | 0.5
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2025 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2030 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2035 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2040 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2050 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2025 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2030 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2035 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2040 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2050 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Lower | 2025 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Lower | 2050 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Upper | 2025 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Upper | 2050 | 0
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2025 | 1.2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2030 | 1.2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2035 | 1.2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2040 | 1.2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2050 | 1.2
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Lower | 2025 | 0.84
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Lower | 2050 | 0.84
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Upper | 2025 | 2.4
4.1 H2 pipeline transp. 40 barg | Energy Transport, Hydrogen Pipeline 40 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Upper | 2050 | 2.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2025 | 2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2030 | 2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2035 | 2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2040 | 2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2050 | 2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Lower | 2025 | 1.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Lower | 2050 | 1.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Upper | 2025 | 2.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Upper | 2050 | 2.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.023238
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.023238
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.023238
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.023238
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.023238
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.016
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.016
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.035
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.035
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.018652
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.018652
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.018652
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.018652
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.018652
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.013
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.013
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.028
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.028
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.010112
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.010112
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.010112
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.010112
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.010112
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.007
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.007
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.015
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.015
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0062426
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0062426
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0062426
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0062426
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0062426
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.004
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.004
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.009
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.009
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0050302
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0050302
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0050302
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0050302
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0050302
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.004
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.004
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.008
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.008
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.030443
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.030443
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.030443
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.030443
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.030443
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.021
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.021
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.046
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.046
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2025 | 50
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2030 | 50
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2035 | 50
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2040 | 50
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2050 | 50
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Lower | 2025 | 45
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Lower | 2050 | 45
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Upper | 2025 | 55
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Upper | 2050 | 55
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2025 | 0.85
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2030 | 0.85
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2035 | 0.85
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2040 | 0.85
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2050 | 0.85
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Lower | 2025 | 0.8
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Lower | 2050 | 0.8
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Upper | 2025 | 0.9
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Upper | 2050 | 0.9
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2025 | 0.35
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2030 | 0.35
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2035 | 0.35
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2040 | 0.35
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2050 | 0.35
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Lower | 2025 | 0.3
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Lower | 2050 | 0.3
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Upper | 2025 | 0.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Upper | 2050 | 0.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2025 | 0.01
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2030 | 0.01
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2035 | 0.01
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2040 | 0.01
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2050 | 0.01
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.03
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.03
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.03
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.03
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.03
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.721
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.721
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.545
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.545
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.14
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.14
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.14
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.14
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.14
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.798
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.798
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.71
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.71
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.76
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.76
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.76
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.76
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.76
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 1.232
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 1.232
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 2.64
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 2.64
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 2.91
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 2.91
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 2.91
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 2.91
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 2.91
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 2.037
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 2.037
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 4.365
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 4.365
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 3.77
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 3.77
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 3.77
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 3.77
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 3.77
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 2.639
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 2.639
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 5.655
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 5.655
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 0.92
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 0.92
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 0.92
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 0.92
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 0.92
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.644
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.644
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.38
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.38
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2025 | 0.56
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2030 | 0.56
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2035 | 0.56
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2040 | 0.56
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2050 | 0.56
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Lower | 2025 | 0.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Lower | 2050 | 0.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Upper | 2025 | 0.6
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Upper | 2050 | 0.6
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2025 | 0.44
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2030 | 0.44
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2035 | 0.44
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2040 | 0.44
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Est | 2050 | 0.44
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Lower | 2025 | 0.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Lower | 2050 | 0.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Upper | 2025 | 0.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Investments, percentage materials [%] | pct. |  |  | 2 | Upper | 2050 | 0.5
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2025 | 0
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2030 | 0
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2035 | 0
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2040 | 0
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2050 | 0
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2025 | 0.46
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2030 | 0.46
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2035 | 0.46
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2040 | 0.46
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2050 | 0.46
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Lower | 2025 | 0.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Lower | 2050 | 0.4
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Upper | 2025 | 0.51
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Upper | 2050 | 0.51
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2025 | 1.2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2030 | 1.2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2035 | 1.2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2040 | 1.2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2050 | 1.2
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Lower | 2025 | 0.84
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Lower | 2050 | 0.84
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Upper | 2025 | 1.8
4.2 pipeline transp. 90 barg | Energy Transport, Hydrogen Pipeline 90 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Upper | 2050 | 1.8
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2025 | 2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2030 | 2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2035 | 2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2040 | 2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Est | 2050 | 2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Lower | 2025 | 1.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Lower | 2050 | 1.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Upper | 2025 | 2.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Construction time [years] | years |  | E | 2 | Upper | 2050 | 2.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.034265
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.034265
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.034265
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.034265
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.034265
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.024
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.024
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.051
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.051
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.02751
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.02751
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.02751
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.02751
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.02751
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.019
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.019
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.041
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.041
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.014924
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.014924
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.014924
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.014924
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.014924
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.022
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.022
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0092178
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0092178
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0092178
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0092178
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0092178
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.006
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.006
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.014
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.014
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.0074292
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.0074292
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.0074292
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.0074292
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.0074292
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.005
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.005
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.011
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.011
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2025 | 0.044873
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2030 | 0.044873
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2035 | 0.044873
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2040 | 0.044873
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Est | 2050 | 0.044873
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2025 | 0.031
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Lower | 2050 | 0.031
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2025 | 0.067
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | pct.oftransportedenergy/100km |  | A, B | 2 | Upper | 2050 | 0.067
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2025 | 50
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2030 | 50
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2035 | 50
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2040 | 50
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Est | 2050 | 50
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Lower | 2025 | 45
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Lower | 2050 | 45
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Upper | 2025 | 55
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Technical life time [years] | years |  | C | 1 | Upper | 2050 | 55
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2025 | 0.85
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2030 | 0.85
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2035 | 0.85
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2040 | 0.85
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Est | 2050 | 0.85
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Lower | 2025 | 0.8
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Lower | 2050 | 0.8
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Upper | 2025 | 0.9
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Energy/technical data | Typical load profile (-) |  |  | D |  | Upper | 2050 | 0.9
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2025 | 0.35
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2030 | 0.35
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2035 | 0.35
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2040 | 0.35
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Est | 2050 | 0.35
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Lower | 2025 | 0.3
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Lower | 2050 | 0.3
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Upper | 2025 | 0.4
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Additional costs [% of Investment costs] | pct.ofInvestmentcosts |  | G | 2 | Upper | 2050 | 0.4
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2025 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2030 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2035 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2040 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Fixed O&M [% of investment costs] | pct.ofinvestmentcosts |  | H | 2 | Est | 2050 | 0.01
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.08
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.08
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.08
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.08
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.08
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.756
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.756
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.62
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 10 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.62
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 1.23
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 1.23
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 1.23
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 1.23
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 1.23
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.861
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.861
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.845
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 12 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.845
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 2.1
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 2.1
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 2.1
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 2.1
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 2.1
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 1.47
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 1.47
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 3.15
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 20 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 3.15
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 3.68
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 3.68
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 3.68
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 3.68
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 3.68
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 2.576
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 2.576
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 5.52
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 30 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 5.52
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 4.88
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 4.88
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 4.88
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 4.88
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 4.88
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 3.416
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 3.416
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 7.32
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 36 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 7.32
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2025 | 0.92
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2030 | 0.92
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2035 | 0.92
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2040 | 0.92
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Est | 2050 | 0.92
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2025 | 0.644
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Lower | 2050 | 0.644
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2025 | 1.38
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investment costs; single line, 8 inches [MEUR/km] | MEUR/km | 2025 | F | 2 | Upper | 2050 | 1.38
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Est | 2025 | 0.44
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Est | 2030 | 0.44
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Est | 2035 | 0.44
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Est | 2040 | 0.44
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Est | 2050 | 0.44
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Lower | 2025 | 0.4
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Lower | 2050 | 0.4
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Upper | 2025 | 0.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage equipment [%] | pct. |  |  | 2 | Upper | 2050 | 0.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2025 | 0.56
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2030 | 0.56
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2035 | 0.56
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2040 | 0.56
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Est | 2050 | 0.56
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Lower | 2025 | 0.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Lower | 2050 | 0.5
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Upper | 2025 | 0.6
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Investments, percentage installation [%] | pct. |  |  | 2 | Upper | 2050 | 0.6
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2025 | 0
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2030 | 0
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2035 | 0
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2040 | 0
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Financial data | Variable O&M [% of investment costs] | pct.ofinvestmentcosts |  | I | 2 | Est | 2050 | 0
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2025 | 0.769
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2030 | 0.769
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2035 | 0.769
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2040 | 0.769
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Est | 2050 | 0.769
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Lower | 2025 | 0.67
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Lower | 2050 | 0.67
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Upper | 2025 | 0.87
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compression electricity consumption [kWh/kg H2] | kWh/kgH2 |  | K | 2 | Upper | 2050 | 0.87
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2025 | 1.2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2030 | 1.2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2035 | 1.2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2040 | 1.2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Est | 2050 | 1.2
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Lower | 2025 | 0.84
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Lower | 2050 | 0.84
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Upper | 2025 | 1.8
4.3 pipeline transp. 140 barg | Energy Transport, Hydrogen Pipeline 140 barg | Technology-specific data | Compressors stations [MEUR/MWe] | MEUR/MWe | 2025 | J | 2; 3 | Upper | 2050 | 1.8
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | ctrl | 2025 | 1
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | ctrl | 2030 | 1
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | ctrl | 2035 | 1
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | ctrl | 2040 | 1
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | ctrl | 2050 | 1
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | lower | 2025 | 0.5
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | lower | 2050 | 0.5
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | upper | 2025 | 1.5
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Construction time [years] | years |  | C |  | upper | 2050 | 1.5
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | ctrl | 2025 | 13.8
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | ctrl | 2030 | 12.9
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | ctrl | 2035 | 12
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | ctrl | 2040 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | ctrl | 2050 | 7.2
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | lower | 2025 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | lower | 2050 | 5
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | upper | 2025 | 15
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Energy demand truck (MJ/km/t H2) |  |  | A | 1 | upper | 2050 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2025 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2030 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2035 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2040 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | ctrl | 2050 | 10
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | lower | 2025 | 4
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | lower | 2050 | 4
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | upper | 2025 | 12
5.1 H2 road transp. | H₂ road transport by tanker truck | Energy/technical data | Technical life time [years] | years |  | B |  | upper | 2050 | 12
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | ctrl | 2025 | 182.7
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | ctrl | 2030 | 169.2507
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | ctrl | 2035 | 157.9673
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | ctrl | 2040 | 131.6394
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | ctrl | 2050 | 94.7804
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | lower | 2025 | 127.89
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | lower | 2050 | 66.3463
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | upper | 2025 | 274.05
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Transport fixed cost (EUR/t H2) |  |  | D, E, F | 2 | upper | 2050 | 142.1706
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | ctrl | 2025 | 3.11
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | ctrl | 2030 | 2.8885
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | ctrl | 2035 | 2.696
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | ctrl | 2040 | 2.2466
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | ctrl | 2050 | 1.6176
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | lower | 2025 | 2.177
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | lower | 2050 | 1.1323
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | upper | 2025 | 4.665
5.1 H2 road transp. | H₂ road transport by tanker truck | Financial data | Variable cost per km (EUR/t H2/km) |  |  | D, E, F | 2 | upper | 2050 | 2.4264

## Notes
ws | description
1.1 el Main distri50-60kVcabl | 9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.1 el Main distri50-60kVcabl | A. Energy losses are estimated from total energy loss on transmission levels in the voltage range 20kV to 130 kV in Sweden. Transmission lines/cables accounts for approximately 60% of the losses and transformers accounts for approximately 40%.
1.1 el Main distri50-60kVcabl | B. Development of energy loss over time depends on several factors. Today, transmission losses typically range between 1% to 3% in Denmark. The variation in transmission losses depends mainly on the amount of power transfer to neighboring countries. The trend in Denmark is towards increasing tra...
1.1 el Main distri50-60kVcabl | C. Cable life length depends on material characteristics and the thermal loading of the cable. Increasing cable area and thus reducing cable temperature leads to longer life length. Today, up to 40 years are realistic life length of a cable with moderate thermal loading. Technological development...
1.1 el Main distri50-60kVcabl | D. Load profile varies significantly between different stations and cables and a general figure is given. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 6 %, the lower scenario is an increase in peak...
1.1 el Main distri50-60kVcabl | E. Construction time ranges normally from 1 to 2 years. In technically complex projects and for long cable stretches, the construction time increases and could stretch up to 5 years.
1.1 el Main distri50-60kVcabl | F. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2. \nF...
1.1 el Main distri50-60kVcabl | G. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
1.1 el Main distri50-60kVcabl | H. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2.For ...
1.1 el Main distri50-60kVcabl | I. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 60 kV. Cost is calculated as the average cost between dense populated areas and city areas. Adjusting factors for each area are: dense populated: 0,94, and city: 1,06. For power range 100-250 MW the cos...
1.1 el Main distri50-60kVcabl | J. Power levels above 100 MW are normally transported at higher voltage levels. In cases where it is motivated to transport higher power levels at 50/60 kV, this is done in parallele cable budles in the same shaft. The cost of two parallel cables can be calculated as the double cost of one cable ...
1.1 el Main distri50-60kVcabl | K. Reinforcement costs depends on where bottlenecks are situated in the grid. Here the reinforcement cost is given for an upgrade of transformer capacity by 40 MVA. Reinforcement of line/cable capacity is in parity with the investment cost in described in row 18-20 and depends on power level and...
1.1 el Main distri50-60kVcabl | L. Station cost is based on a 40 MW station with 2 x 20 MVA transformers (72/12 kV). Station cost depends on a number of factors, such as power rating, redundancy on transformers etc. Station cost have an almost linear relation to the power rating and following relation holds for the power span...
1.1 el Main distri50-60kVcabl | M. Station cost is based on average cost for capacity banks and inductor with a design voltage of 72 kV. It is assumed that the equipment is installed in a existing station.
1.1 el Main distri50-60kVcabl | O. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
1.1 el Main distri50-60kVcabl | P. The percentage of the investment cost allocated to material cost and installation cost varies depending on area type (rural or city) and power level. An average is given here. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installat...
1.1 el Main distri50-60kVcabl | Q. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost multiplied by the average cost of cables per MW and km given in row 18 to 20. It should be noted that the O&M cost in distribution system mainly is attributed to stations since there is practically no m...
1.1 el Main distri50-60kVcabl | R. Variable O&M cost is in very low for electric transmission systems and considered to be negligible
1.1 el Main distri50-60kVcabl | S. Energy losses and auxiliary electricity consumption can be considered negligible
1.3 el distri suburban | 7. Swedish Energy Markets Inspectorate [http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.3 el distri suburban | A. The line losses were calculated using reference [1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.3 el distri suburban | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.3 el distri suburban | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.3 el distri suburban | D. Calculations for the load profile were based on reference [1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increa...
1.3 el distri suburban | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
1.3 el distri suburban | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
1.3 el distri suburban | G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest powe...
1.3 el distri suburban | H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest po...
1.3 el distri suburban | I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the cur...
1.3 el distri suburban | J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations...
1.3 el distri suburban | K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area [power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In...
1.3 el distri suburban | L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased...
1.3 el distri suburban | M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
1.3 el distri suburban | N. Auxiliary electricity consumption can be considered negligible
1.4 el distri city | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.4 el distri city | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.4 el distri city | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.4 el distri city | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.4 el distri city | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
1.4 el distri city | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
1.4 el distri city | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
1.4 el distri city | G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest powe...
1.4 el distri city | H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest po...
1.4 el distri city | I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the cur...
1.4 el distri city | J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations...
1.4 el distri city | K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In...
1.4 el distri city | L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintenance on cables. The O&M cost is assume to be reduced due to increased ...
1.4 el distri city | M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
1.4 el distri city | N. Auxiliary electricity consumption can be considered negligible
1.5 el distri new area | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.5 el distri new area | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.5 el distri new area | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.5 el distri new area | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.5 el distri new area | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
1.5 el distri new area | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
1.5 el distri new area | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
1.5 el distri new area | G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest powe...
1.5 el distri new area | H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest po...
1.5 el distri new area | I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the cur...
1.5 el distri new area | J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations...
1.5 el distri new area | K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In...
1.5 el distri new area | L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased...
1.5 el distri new area | M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
1.5 el distri new area | N. Auxiliary electricity consumption can be considered negligible
1.6 el trans OH | 3. See [50] in text chapter
1.6 el trans OH | 1. Low and high are minus/plus 30%
1.6 el trans OH | 2. 2025 prices: after adding 20% to price from source
1.6 el trans OH | 3. Prices in 2050 assumed to be as prices before 20% increase in 2025
1.6 el trans OH | 4. Prices assumed to decrease linearly from 2030 to 2050
1.6 el trans OH | 5. Estimates, typical values (AC with compensation)
1.6 el trans OH | 6. Estimates,project specific, depending on e.g., length of line
1.6 el trans OH | 7. Estimates, based on stakeholder information
1.6 el trans OH | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.6 el trans OH | 9. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
1.6 el trans OH | 10. Costs are including compensation (AC)
1.6 el trans OH | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.6 el trans OH | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.6 el trans OH | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.6 el trans OH | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.6 el trans OH | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
1.6 el trans OH | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
1.6 el trans OH | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
1.7 el trans AC&DC cables | 2. See [30], [31], [36], [42] in text chapter
1.7 el trans AC&DC cables | 1. Low and high are minus/plus 30%
1.7 el trans AC&DC cables | 2. 2025 prices: adding 20% to price from source
1.7 el trans AC&DC cables | 3. Prices in 2050 assumed to be as prices before 20% increase in 2025
1.7 el trans AC&DC cables | 4. Prices assumed to decrease linearly from 2030 to 2050
1.7 el trans AC&DC cables | 5. Estimates, typical values.
1.7 el trans AC&DC cables | 6. Estimates, project specific, depending on e.g., length of cable
1.7 el trans AC&DC cables | 7. Estimates, typical values (AC cables with compensation)
1.7 el trans AC&DC cables | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.7 el trans AC&DC cables | 9. 220 kV with capacity of about 500 MW
1.7 el trans AC&DC cables | 10. 525 kV bipole with capacity 1500-2000 MW
1.7 el trans AC&DC cables | 11. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
1.7 el trans AC&DC cables | 12. Costs are including compensation (AC)
1.7 el trans AC&DC cables | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.7 el trans AC&DC cables | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.7 el trans AC&DC cables | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.7 el trans AC&DC cables | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.7 el trans AC&DC cables | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
1.7 el trans AC&DC cables | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
1.7 el trans AC&DC cables | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
1.8 el substations | 2. See [30], [31], [36], [42] in text chapter
1.8 el substations | 1. 2025 prices: adding 20% to "year of source " prices
1.8 el substations | 2. Low and high: minus/plus 30%
1.8 el substations | 3. Prices in 2050 assumed to be as prices before 20% increase in 2025
1.8 el substations | 4. Prices assumed to decrease linearly from 2030 to 2050
1.8 el substations | 5. Estimates, typical values. AC substation includes transformers, switchgear, powerlines, compensation, control equipment etc.
1.8 el substations | 6. Estimates, project specific, depends on size and location of station. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc
1.8 el substations | 7. Estimates, based on stakeholder information
1.8 el substations | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.8 el substations | 9. 220 kV substation, capacity in the range of 500 MW
1.8 el substations | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
1.8 el substations | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.8 el substations | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.8 el substations | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.8 el substations | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.8 el substations | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
1.8 el substations | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
1.8 el substations | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
1.9 el transformers | 2. See [30], [31], [36], [42] in text chapter
1.9 el transformers | 1. 2025 prices: adding 20% to price from source
1.9 el transformers | 2. Low and high: minus/plus 30%
1.9 el transformers | 3. Prices assumed to decrease linearly from 2030 to 2050
1.9 el transformers | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
1.9 el transformers | 5. Estimates, typical values.
1.9 el transformers | 6. Estimates, based on stakeholder information
1.9 el transformers | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.9 el transformers | 6. Estimates, project specific, depending on e.g., length of cable
1.9 el transformers | 7. Estimates, typical values (AC cables with compensation)
1.9 el transformers | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.9 el transformers | 9. 220 kV with capacity of about 500 MW
1.9 el transformers | 10. 525 kV bipole with capacity 1500-2000 MW
1.9 el transformers | 11. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
1.9 el transformers | 12. Costs are including compensation (AC)
1.9 el transformers | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.9 el transformers | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.9 el transformers | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.9 el transformers | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.9 el transformers | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
1.9 el transformers | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
1.9 el transformers | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
1.10 el compensation | 2. See [30], [31], [36], [42] in text chapter
1.10 el compensation | 1. Low and high: minus/plus 30%
1.10 el compensation | 2. 2025 prices: adding 20% to price from source
1.10 el compensation | 3. Prices assumed to decrease linearly from 2030 to 2050
1.10 el compensation | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
1.10 el compensation | 5. Estimates, typical values.
1.10 el compensation | 6. Estimates, load of reactive power
1.10 el compensation | 7. Estimates, (partly) based on stakeholder information
1.10 el compensation | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.10 el compensation | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
1.10 el compensation | 9. 220 kV substation, capacity in the range of 500 MW
1.10 el compensation | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
1.10 el compensation | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.10 el compensation | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
1.10 el compensation | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
1.10 el compensation | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
1.10 el compensation | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
1.10 el compensation | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
1.10 el compensation | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
2.1 gas Main distri line | 2. See [30], [31], [36], [42] in text chapter
2.1 gas Main distri line | 1. 2025 prices: adding 20% to price from source
2.1 gas Main distri line | 2. Low and high: minus/plus 30%
2.1 gas Main distri line | 3. Prices assumed to decrease linearly from 2030 to 2050
2.1 gas Main distri line | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
2.1 gas Main distri line | 5. Estimates, typical values.
2.1 gas Main distri line | 6. Estimates, based on stakeholder information
2.1 gas Main distri line | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.1 gas Main distri line | 6. Estimates, project specific, depending on e.g., length of cable
2.1 gas Main distri line | 7. Estimates, typical values (AC cables with compensation)
2.1 gas Main distri line | 2. HMN Naturgas
2.1 gas Main distri line | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
2.1 gas Main distri line | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
2.1 gas Main distri line | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
2.1 gas Main distri line | D. Includes enginering, tender, and construction.
2.1 gas Main distri line | E. Rates include VVM review, landowner compensation and archaeological screening. Based on 20 km, of which 8 % is based on drilling.
2.1 gas Main distri line | F. Data given is for a 50 MW capacity
2.1 gas Main distri line | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
2.1 gas Main distri line | H. Not possible to give general numbers. Depends on kind of reinforcement. Can be calculated based on the other numbers given.
2.1 gas Main distri line | I. Capacity not relevant-too high
2.1 gas Main distri line | J. Type 1 MR stations supplying the transmission system level 2-not part of the scope
2.1 gas Main distri line | K. Type 1 MR stations supplying the transmission system level 2 .The stated costs are the average cost for a 40/4 bar MR station where reheating after expansion is required and a 19/4 bar MR station where reheating is not necessary. The cost is only modestly size dependent. A 40/4 bar station ca...
2.1 gas Main distri line | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
2.1 gas Main distri line | A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
2.1 gas Main distri line | B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
2.1 gas Main distri line | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
2.1 gas Main distri line | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
2.1 gas Main distri line | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
2.1 gas Main distri line | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
2.2 gas Rural | 2. See [30], [31], [36], [42] in text chapter
2.2 gas Rural | 1. Low and high: minus/plus 30%
2.2 gas Rural | 2. 2025 prices: adding 20% to price from source
2.2 gas Rural | 3. Prices assumed to decrease linearly from 2030 to 2050
2.2 gas Rural | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
2.2 gas Rural | 5. Estimates, typical values.
2.2 gas Rural | 6. Estimates, load of reactive power
2.2 gas Rural | 7. Estimates, (partly) based on stakeholder information
2.2 gas Rural | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.2 gas Rural | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.2 gas Rural | 9. 220 kV substation, capacity in the range of 500 MW
2.2 gas Rural | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
2.2 gas Rural | 2. HMN Naturgas
2.2 gas Rural | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The l...
2.2 gas Rural | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
2.2 gas Rural | C. There is no power consuming parts in the distribution system
2.2 gas Rural | D. Based on given case
2.2 gas Rural | E. Capacity range not relevant for given case
2.2 gas Rural | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
2.2 gas Rural | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
2.2 gas Rural | H. Reinforcement not relevant
2.2 gas Rural | I. No station will be installed for the distribution network
2.2 gas Rural | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
2.2 gas Rural | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
2.2 gas Rural | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
2.2 gas Rural | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
2.3 gas Suburban | 2. See [30], [31], [36], [42] in text chapter
2.3 gas Suburban | 1. 2025 prices: adding 20% to price from source
2.3 gas Suburban | 2. Low and high: minus/plus 30%
2.3 gas Suburban | 3. Prices assumed to decrease linearly from 2030 to 2050
2.3 gas Suburban | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
2.3 gas Suburban | 5. Estimates, typical values.
2.3 gas Suburban | 6. Estimates, based on stakeholder information
2.3 gas Suburban | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.3 gas Suburban | 6. Estimates, project specific, depending on e.g., length of cable
2.3 gas Suburban | 7. Estimates, typical values (AC cables with compensation)
2.3 gas Suburban | 2. HMN Naturgas
2.3 gas Suburban | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
2.3 gas Suburban | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
2.3 gas Suburban | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
2.3 gas Suburban | D. Includes enginering, tender, and construction.
2.3 gas Suburban | 2. HMN Naturgas
2.3 gas Suburban | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. ...
2.3 gas Suburban | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
2.3 gas Suburban | C. There is no power consuming parts in the distribution system
2.3 gas Suburban | D. Based on given case
2.3 gas Suburban | E. Capacity range not relevant for given case
2.3 gas Suburban | F. Stated number is for a Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
2.3 gas Suburban | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
2.3 gas Suburban | H. Reinforcement not relevant
2.3 gas Suburban | I. No station will be installed for the distribution network
2.3 gas Suburban | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
2.3 gas Suburban | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
2.3 gas Suburban | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
2.3 gas Suburban | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
2.4 gas City | 2. See [30], [31], [36], [42] in text chapter
2.4 gas City | 1. Low and high: minus/plus 30%
2.4 gas City | 2. 2025 prices: adding 20% to price from source
2.4 gas City | 3. Prices assumed to decrease linearly from 2030 to 2050
2.4 gas City | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
2.4 gas City | 5. Estimates, typical values.
2.4 gas City | 6. Estimates, load of reactive power
2.4 gas City | 7. Estimates, (partly) based on stakeholder information
2.4 gas City | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.4 gas City | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.4 gas City | 9. 220 kV substation, capacity in the range of 500 MW
2.4 gas City | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
2.4 gas City | 1. HMN Naturgas
2.4 gas City | A. For the defined case "New distribution in existing densely populated areas, city centres etc." it is assessed the natural gas based heating will be designed with one boiler and heat is distributied to the endusers by a locel district heating sytem. This means that the local natural gas system...
2.4 gas City | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
2.4 gas City | C. There is no power consuming parts in the distribution system
2.4 gas City | D. Based on given case
2.4 gas City | E. Stated number is for a service line supplying 1,5 MW.
2.4 gas City | F. Not relavant, see note A
2.4 gas City | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
2.4 gas City | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
2.4 gas City | H. Reinforcement not relevant
2.4 gas City | I. No station will be installed for the distribution network
2.4 gas City | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
2.4 gas City | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
2.4 gas City | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
2.4 gas City | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
2.5 gas New area | 2. See [30], [31], [36], [42] in text chapter
2.5 gas New area | 1. 2025 prices: adding 20% to price from source
2.5 gas New area | 2. Low and high: minus/plus 30%
2.5 gas New area | 3. Prices assumed to decrease linearly from 2030 to 2050
2.5 gas New area | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
2.5 gas New area | 5. Estimates, typical values.
2.5 gas New area | 6. Estimates, based on stakeholder information
2.5 gas New area | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
2.5 gas New area | 6. Estimates, project specific, depending on e.g., length of cable
2.5 gas New area | 7. Estimates, typical values (AC cables with compensation)
2.5 gas New area | 2. HMN Naturgas
2.5 gas New area | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
2.5 gas New area | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
2.5 gas New area | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
2.5 gas New area | D. Includes enginering, tender, and construction.
2.5 gas New area | 2. HMN Naturgas
2.5 gas New area | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
2.5 gas New area | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
2.5 gas New area | C. There are no power consuming parts in the distribution system
2.5 gas New area | D. Based on given case
2.5 gas New area | E. Capacity range not relevant for given case
2.5 gas New area | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
2.5 gas New area | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
2.5 gas New area | H. Reinforcement not relevant
2.5 gas New area | I. No station will be installed for the distribution network
2.5 gas New area | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
2.5 gas New area | D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an incre...
2.5 gas New area | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total ...
2.5 gas New area | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction o...
3.1 DH transmission | 2. See [30], [31], [36], [42] in text chapter
3.1 DH transmission | 1. Low and high: minus/plus 30%
3.1 DH transmission | 2. 2025 prices: adding 20% to price from source
3.1 DH transmission | 3. Prices assumed to decrease linearly from 2030 to 2050
3.1 DH transmission | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
3.1 DH transmission | 5. Estimates, typical values.
3.1 DH transmission | 6. Estimates, load of reactive power
3.1 DH transmission | 7. Estimates, (partly) based on stakeholder information
3.1 DH transmission | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
3.1 DH transmission | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
3.1 DH transmission | 9. 220 kV substation, capacity in the range of 500 MW
3.1 DH transmission | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
3.1 DH transmission | 4. Consolidated with statistics from Danish District Heating Association 2020
3.1 DH transmission | A. The loss is per trench km of transmission pipeline pair.
3.1 DH transmission | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
3.1 DH transmission | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
3.1 DH transmission | D. Two district heating pipes were chosen for each interval (one for the lowest effect level and one for the highest). The average of these two are stated in the table. For cost interpolation: P = a * C^b, where P = cost in €/MW/m, C = capacity in MW, a = 330 and b =-0,571.
3.1 DH transmission | E. Depends on the scale of the transmission grid and supply strategy of reserve capacity. Therefore, it is not possible to generalize these costs.
3.1 DH transmission | F. Soft costs include design, planning, tender, permits, supervision, etc.
3.1 DH transmission | F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
3.1 DH transmission | G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
3.1 DH transmission | H. Reinforcement not relevant
3.1 DH transmission | I. No station will be installed for the distribution network
3.1 DH transmission | C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
3.1 DH transmission | D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an inc...
3.1 DH transmission | E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be transla...
3.1 DH transmission | F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction ...
3.2 DH_Distribu Suburb | 2. See [30], [31], [36], [42] in text chapter
3.2 DH_Distribu Suburb | 1. 2025 prices: adding 20% to price from source
3.2 DH_Distribu Suburb | 2. Low and high: minus/plus 30%
3.2 DH_Distribu Suburb | 3. Prices assumed to decrease linearly from 2030 to 2050
3.2 DH_Distribu Suburb | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
3.2 DH_Distribu Suburb | 5. Estimates, typical values.
3.2 DH_Distribu Suburb | 6. Estimates, based on stakeholder information
3.2 DH_Distribu Suburb | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
3.2 DH_Distribu Suburb | 6. Estimates, project specific, depending on e.g., length of cable
3.2 DH_Distribu Suburb | 7. Estimates, typical values (AC cables with compensation)
3.2 DH_Distribu Suburb | 2. HMN Naturgas
3.2 DH_Distribu Suburb | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
3.2 DH_Distribu Suburb | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
3.2 DH_Distribu Suburb | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
3.2 DH_Distribu Suburb | D. Includes enginering, tender, and construction.
3.2 DH_Distribu Suburb | 2. HMN Naturgas
3.2 DH_Distribu Suburb | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
3.2 DH_Distribu Suburb | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
3.2 DH_Distribu Suburb | 4. Consolidated with statistics from Danish District Heating Association 2020
3.2 DH_Distribu Suburb | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
3.2 DH_Distribu Suburb | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities
3.2 DH_Distribu Suburb | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
3.2 DH_Distribu Suburb | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on an area of scattered single-family houses of 1-2 floors with a heat density of 10 GWh/year/km2.
3.2 DH_Distribu Suburb | E. A paved area is assumed for the distribution network. For service lines 50 % unpaved and 50 % paved area is asumed.
3.2 DH_Distribu Suburb | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
3.2 DH_Distribu Suburb | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
3.2 DH_Distribu Suburb | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
3.2 DH_Distribu Suburb | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
3.2 DH_Distribu Suburb | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
3.2 DH_Distribu Suburb | K. Service lines above 100 kW are not relevant in the specific area type.
3.2 DH_Distribu Suburb | L. Single lines above 25 MW are not relevant in the specific area type.
3.2 DH_Distribu Suburb | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
3.3 DH_Distribu City | 2. See [30], [31], [36], [42] in text chapter
3.3 DH_Distribu City | 1. Low and high: minus/plus 30%
3.3 DH_Distribu City | 2. 2025 prices: adding 20% to price from source
3.3 DH_Distribu City | 3. Prices assumed to decrease linearly from 2030 to 2050
3.3 DH_Distribu City | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
3.3 DH_Distribu City | 5. Estimates, typical values.
3.3 DH_Distribu City | 6. Estimates, load of reactive power
3.3 DH_Distribu City | 7. Estimates, (partly) based on stakeholder information
3.3 DH_Distribu City | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
3.3 DH_Distribu City | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
3.3 DH_Distribu City | 9. 220 kV substation, capacity in the range of 500 MW
3.3 DH_Distribu City | 10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
3.3 DH_Distribu City | 4. Consolidated with statistics from Danish District Heating Association 2020
3.3 DH_Distribu City | A. The loss is per trench km of transmission pipeline pair.
3.3 DH_Distribu City | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
3.3 DH_Distribu City | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
3.3 DH_Distribu City | 4. Consolidated with statistics from Danish District Heating Association 2020
3.3 DH_Distribu City | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
3.3 DH_Distribu City | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
3.3 DH_Distribu City | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
3.3 DH_Distribu City | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
3.3 DH_Distribu City | E. A paved area is assumed for the distribution network as well as for service lines.
3.3 DH_Distribu City | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
3.3 DH_Distribu City | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
3.3 DH_Distribu City | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
3.3 DH_Distribu City | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
3.3 DH_Distribu City | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
3.3 DH_Distribu City | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
3.3 DH_Distribu City | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
3.3 DH_Distribu City | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
3.4 DH_Distribu New area | 2. See [30], [31], [36], [42] in text chapter
3.4 DH_Distribu New area | 1. 2025 prices: adding 20% to price from source
3.4 DH_Distribu New area | 2. Low and high: minus/plus 30%
3.4 DH_Distribu New area | 3. Prices assumed to decrease linearly from 2030 to 2050
3.4 DH_Distribu New area | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
3.4 DH_Distribu New area | 5. Estimates, typical values.
3.4 DH_Distribu New area | 6. Estimates, based on stakeholder information
3.4 DH_Distribu New area | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
3.4 DH_Distribu New area | 6. Estimates, project specific, depending on e.g., length of cable
3.4 DH_Distribu New area | 7. Estimates, typical values (AC cables with compensation)
3.4 DH_Distribu New area | 2. HMN Naturgas
3.4 DH_Distribu New area | A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas n...
3.4 DH_Distribu New area | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
3.4 DH_Distribu New area | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
3.4 DH_Distribu New area | D. Includes enginering, tender, and construction.
3.4 DH_Distribu New area | 2. HMN Naturgas
3.4 DH_Distribu New area | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
3.4 DH_Distribu New area | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
3.4 DH_Distribu New area | 4. Consolidated with statistics from Danish District Heating Association 2020
3.4 DH_Distribu New area | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
3.4 DH_Distribu New area | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
3.4 DH_Distribu New area | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
3.4 DH_Distribu New area | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
3.4 DH_Distribu New area | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
3.4 DH_Distribu New area | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
3.4 DH_Distribu New area | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
3.4 DH_Distribu New area | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
3.4 DH_Distribu New area | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
3.4 DH_Distribu New area | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
3.4 DH_Distribu New area | K. Service lines above 100 kW are not relevant in the specific area type.
3.4 DH_Distribu New area | L. Single lines above 25 MW are not relevant in the specific area type.
3.4 DH_Distribu New area | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
3.4 DH_Distribu New area | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.
4.1 H2 pipeline transp. 40 barg | 2. See [30], [31], [36], [42] in text chapter
4.1 H2 pipeline transp. 40 barg | 1. Low and high: minus/plus 30%
4.1 H2 pipeline transp. 40 barg | 2. 2025 prices: adding 20% to price from source
4.1 H2 pipeline transp. 40 barg | 3. Prices assumed to decrease linearly from 2030 to 2050
4.1 H2 pipeline transp. 40 barg | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
4.1 H2 pipeline transp. 40 barg | 5. Estimates, typical values.
4.1 H2 pipeline transp. 40 barg | 6. Estimates, load of reactive power
4.1 H2 pipeline transp. 40 barg | 7. Estimates, (partly) based on stakeholder information
4.1 H2 pipeline transp. 40 barg | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
4.1 H2 pipeline transp. 40 barg | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
4.1 H2 pipeline transp. 40 barg | 9. 220 kV substation, capacity in the range of 500 MW
4.1 H2 pipeline transp. 40 barg | 3. Bundesnetzargentur - Hydrogen Core Network
4.1 H2 pipeline transp. 40 barg | 4. Consolidated with statistics from Danish District Heating Association 2020
4.1 H2 pipeline transp. 40 barg | A. The loss is per trench km of transmission pipeline pair.
4.1 H2 pipeline transp. 40 barg | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
4.1 H2 pipeline transp. 40 barg | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
4.1 H2 pipeline transp. 40 barg | 4. Consolidated with statistics from Danish District Heating Association 2020
4.1 H2 pipeline transp. 40 barg | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
4.1 H2 pipeline transp. 40 barg | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
4.1 H2 pipeline transp. 40 barg | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
4.1 H2 pipeline transp. 40 barg | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
4.1 H2 pipeline transp. 40 barg | E. A paved area is assumed for the distribution network as well as for service lines.
4.1 H2 pipeline transp. 40 barg | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
4.1 H2 pipeline transp. 40 barg | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
4.1 H2 pipeline transp. 40 barg | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
4.1 H2 pipeline transp. 40 barg | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
4.1 H2 pipeline transp. 40 barg | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
4.1 H2 pipeline transp. 40 barg | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
4.1 H2 pipeline transp. 40 barg | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
4.1 H2 pipeline transp. 40 barg | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
4.2 pipeline transp. 90 barg | 2. See [30], [31], [36], [42] in text chapter
4.2 pipeline transp. 90 barg | 1. 2025 prices: adding 20% to price from source
4.2 pipeline transp. 90 barg | 2. Low and high: minus/plus 30%
4.2 pipeline transp. 90 barg | 3. Prices assumed to decrease linearly from 2030 to 2050
4.2 pipeline transp. 90 barg | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
4.2 pipeline transp. 90 barg | 5. Estimates, typical values.
4.2 pipeline transp. 90 barg | 6. Estimates, based on stakeholder information
4.2 pipeline transp. 90 barg | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
4.2 pipeline transp. 90 barg | 6. Estimates, project specific, depending on e.g., length of cable
4.2 pipeline transp. 90 barg | 7. Estimates, typical values (AC cables with compensation)
4.2 pipeline transp. 90 barg | 2. HMN Naturgas
4.2 pipeline transp. 90 barg | 3. Bundesnetzargentur - Hydrogen Core Network
4.2 pipeline transp. 90 barg | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
4.2 pipeline transp. 90 barg | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
4.2 pipeline transp. 90 barg | D. Includes enginering, tender, and construction.
4.2 pipeline transp. 90 barg | 2. HMN Naturgas
4.2 pipeline transp. 90 barg | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
4.2 pipeline transp. 90 barg | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
4.2 pipeline transp. 90 barg | 4. Consolidated with statistics from Danish District Heating Association 2020
4.2 pipeline transp. 90 barg | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
4.2 pipeline transp. 90 barg | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
4.2 pipeline transp. 90 barg | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
4.2 pipeline transp. 90 barg | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
4.2 pipeline transp. 90 barg | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
4.2 pipeline transp. 90 barg | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
4.2 pipeline transp. 90 barg | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
4.2 pipeline transp. 90 barg | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
4.2 pipeline transp. 90 barg | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
4.2 pipeline transp. 90 barg | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
4.2 pipeline transp. 90 barg | K. Service lines above 100 kW are not relevant in the specific area type.
4.2 pipeline transp. 90 barg | L. Single lines above 25 MW are not relevant in the specific area type.
4.2 pipeline transp. 90 barg | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
4.2 pipeline transp. 90 barg | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.
4.3 pipeline transp. 140 barg | 2. See [30], [31], [36], [42] in text chapter
4.3 pipeline transp. 140 barg | 1. Low and high: minus/plus 30%
4.3 pipeline transp. 140 barg | 2. 2025 prices: adding 20% to price from source
4.3 pipeline transp. 140 barg | 3. Prices assumed to decrease linearly from 2030 to 2050
4.3 pipeline transp. 140 barg | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
4.3 pipeline transp. 140 barg | 5. Estimates, typical values.
4.3 pipeline transp. 140 barg | 6. Estimates, load of reactive power
4.3 pipeline transp. 140 barg | 7. Estimates, (partly) based on stakeholder information
4.3 pipeline transp. 140 barg | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
4.3 pipeline transp. 140 barg | 8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
4.3 pipeline transp. 140 barg | 9. 220 kV substation, capacity in the range of 500 MW
4.3 pipeline transp. 140 barg | 3. Bundesnetzargentur - Hydrogen Core Network
4.3 pipeline transp. 140 barg | 4. Consolidated with statistics from Danish District Heating Association 2020
4.3 pipeline transp. 140 barg | A. The loss is per trench km of transmission pipeline pair.
4.3 pipeline transp. 140 barg | B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
4.3 pipeline transp. 140 barg | C. The cost is per trench meter transmission pipeline pair in unpaved areas.
4.3 pipeline transp. 140 barg | 4. Consolidated with statistics from Danish District Heating Association 2020
4.3 pipeline transp. 140 barg | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
4.3 pipeline transp. 140 barg | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
4.3 pipeline transp. 140 barg | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
4.3 pipeline transp. 140 barg | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
4.3 pipeline transp. 140 barg | E. A paved area is assumed for the distribution network as well as for service lines.
4.3 pipeline transp. 140 barg | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
4.3 pipeline transp. 140 barg | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
4.3 pipeline transp. 140 barg | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
4.3 pipeline transp. 140 barg | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
4.3 pipeline transp. 140 barg | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
4.3 pipeline transp. 140 barg | K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
4.3 pipeline transp. 140 barg | L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
4.3 pipeline transp. 140 barg | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
5.1 H2 road transp. | 2. COWI transport model
5.1 H2 road transp. | A. Values dependent on truck fuel consumption used for propulsion and amount of hydrogen stored per truck. Fuel consumption of 18 MJ/km is based on 50-60 t truck with trailer for road cargo transport baseline global average. Decrease over years ie expected due to an increase in capacity for hydro...
5.1 H2 road transp. | B. Technical lifetime of truck (puller) will depend on the distance driven, 4-10 years. Lifetime trailer 10 years or more.
5.1 H2 road transp. | C. Based on expert judgement.
5.1 H2 road transp. | D. Capital cost of truck and fixed O&M is split into the fixed and variable cost based on relative time spend on loading/unloading and on driving.
5.1 H2 road transp. | E. Main fixed and variable costs assumptions are: CAPEX (Truck + Tanker) is 800.000 EUR, annual fixed OPEX is 5% truck capital cost, truck availability is 8000 hours per year, loading and unloading time is 120 minutes each, driver cost 40 EUR/MWh (24/7 operation), fuel cost for diesel 47 EUR/kJ, ...
5.1 H2 road transp. | F. Parameters that contributes in a decrease of both fixed and variable costs: increased transport capacity per truck, faster loading and unloading time, increased truck availability, decreased in truck CAPEX or any other OPEX. Expected decrease in fixed and variable cost is mostly driven by an e...
5.1 H2 road transp. | 2. See [30], [31], [36], [42] in text chapter
5.1 H2 road transp. | 1. 2025 prices: adding 20% to price from source
5.1 H2 road transp. | 2. Low and high: minus/plus 30%
5.1 H2 road transp. | 3. Prices assumed to decrease linearly from 2030 to 2050
5.1 H2 road transp. | 4. Prices in 2050 assumed to be as prices before 20% increase in 2025
5.1 H2 road transp. | 5. Estimates, typical values.
5.1 H2 road transp. | 6. Estimates, based on stakeholder information
5.1 H2 road transp. | 7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
5.1 H2 road transp. | 6. Estimates, project specific, depending on e.g., length of cable
5.1 H2 road transp. | 7. Estimates, typical values (AC cables with compensation)
5.1 H2 road transp. | 2. HMN Naturgas
5.1 H2 road transp. | 3. Bundesnetzargentur - Hydrogen Core Network
5.1 H2 road transp. | B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
5.1 H2 road transp. | C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
5.1 H2 road transp. | D. Includes enginering, tender, and construction.
5.1 H2 road transp. | 2. HMN Naturgas
5.1 H2 road transp. | A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of...
5.1 H2 road transp. | B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
5.1 H2 road transp. | 4. Consolidated with statistics from Danish District Heating Association 2020
5.1 H2 road transp. | A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
5.1 H2 road transp. | B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
5.1 H2 road transp. | C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
5.1 H2 road transp. | D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
5.1 H2 road transp. | E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
5.1 H2 road transp. | F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
5.1 H2 road transp. | G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
5.1 H2 road transp. | H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
5.1 H2 road transp. | I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
5.1 H2 road transp. | J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
5.1 H2 road transp. | K. Service lines above 100 kW are not relevant in the specific area type.
5.1 H2 road transp. | L. Single lines above 25 MW are not relevant in the specific area type.
5.1 H2 road transp. | M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
5.1 H2 road transp. | For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.

## Ref
ws | description
1.1 el Main distri50-60kVcabl | 1. U.S. Energy Information Administration (http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3)
1.1 el Main distri50-60kVcabl | 2. energinet.dk (http://www.energinet.dk/DA/KLIMA-OG-MILJOE/Energinetdks-miljoepaavirkninger/Miljoepaavirkninger-ved-transport-af-el/Sider/Tab-i-elnettet.aspx)
1.1 el Main distri50-60kVcabl | 3. Svenska Kraftnät, Nätuvecklingsplan 2016 – 2025, Oktober 2015 (http://www.svk.se/siteassets/om-oss/rapporter/natutvecklingsplan-2016-2025.pdf)
1.1 el Main distri50-60kVcabl | 4. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
1.1 el Main distri50-60kVcabl | 5. Svenska Kraftnät, Technology (http://www.svk.se/en/grid-development/the-construction-process/technology/)
1.1 el Main distri50-60kVcabl | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
1.1 el Main distri50-60kVcabl | 7. PEX Guiden, Ericsson
1.1 el Main distri50-60kVcabl | 8. Standard value list for the Swedish Energy Markets Inspectorate (2015 value) (http://ei.se/sv/el/Elnat-och-natprisreglering/forhandsreglering-av-elnatstariffer-ar-2016-2019/dokument-elnatsreglering/normvardeslista-elnat-2016-2019/)
1.1 el Main distri50-60kVcabl | 9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.3 el distri suburban | 1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen [Statistics from Swedish utility companies) from 2014 [http://www.ei.se/sv/Publikationer/Arsrapporter/)
1.3 el distri suburban | 2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, [2001).
1.3 el distri suburban | 3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution [http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
1.3 el distri suburban | 4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
1.3 el distri suburban | 5. Sweco, Project data
1.3 el distri suburban | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
1.3 el distri suburban | 7. Swedish Energy Markets Inspectorate [http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.4 el distri city | 1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
1.4 el distri city | 2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
1.4 el distri city | 3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
1.4 el distri city | 4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
1.4 el distri city | 5. Sweco, Project data
1.4 el distri city | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
1.4 el distri city | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.5 el distri new area | 1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
1.5 el distri new area | 2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
1.5 el distri new area | 3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
1.5 el distri new area | 4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
1.5 el distri new area | 5. Sweco, Project data
1.5 el distri new area | 6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
1.5 el distri new area | 7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
1.6 el trans OH | 1. Netzentwicklungsplan Strom (German TSOs), version 2021
1.6 el trans OH | 2. See [30], [31], [36], [42] in text chapter
1.6 el trans OH | 3. See [50] in text chapter
1.7 el trans AC&DC cables | 1. Netzentwicklungsplan Strom (German TSOs), version 2023
1.7 el trans AC&DC cables | 2. See [30], [31], [36], [42] in text chapter
1.8 el substations | 1. Netzentwicklungsplan Strom (German TSOs), version 2023
1.8 el substations | 2. See [30], [31], [36], [42] in text chapter
1.9 el transformers | 1. Netzentwicklungsplan Strom (German TSOs), version 2021
1.9 el transformers | 2. See [30], [31], [36], [42] in text chapter
1.10 el compensation | 1. Netzentwicklungsplan Strom (German TSOs), version 2021
1.10 el compensation | 2. See [30], [31], [36], [42] in text chapter
2.1 gas Main distri line | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2.1 gas Main distri line | 2. HMN Naturgas
2.2 gas Rural | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2.2 gas Rural | 2. HMN Naturgas
2.3 gas Suburban | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2.3 gas Suburban | 2. HMN Naturgas
2.4 gas City | 1. HMN Naturgas
2.5 gas New area | 1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2.5 gas New area | 2. HMN Naturgas
3.1 DH transmission | 1. Based on Ramboll experience figures
3.1 DH transmission | 2. LOGSTOR A/S
3.1 DH transmission | 3. Consolidated with data from Danish District Heating Association
3.1 DH transmission | 4. Consolidated with statistics from Danish District Heating Association 2020
3.2 DH_Distribu Suburb | 1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
3.2 DH_Distribu Suburb | 2. Ramboll experience and technical data from LOGSTOR A/S
3.2 DH_Distribu Suburb | 3. Consolidated with data from Danish District Heating Association
3.2 DH_Distribu Suburb | 4. Consolidated with statistics from Danish District Heating Association 2020
3.3 DH_Distribu City | 1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
3.3 DH_Distribu City | 2. Ramboll experience and technical data from LOGSTOR A/S
3.3 DH_Distribu City | 3. Consolidated with data from Danish District Heating Association
3.3 DH_Distribu City | 4. Consolidated with statistics from Danish District Heating Association 2020
3.4 DH_Distribu New area | 1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
3.4 DH_Distribu New area | 2. Ramboll experience and technical data from LOGSTOR A/S
3.4 DH_Distribu New area | 3. Consolidated with data from Danish District Heating Association
3.4 DH_Distribu New area | 4. Consolidated with statistics from Danish District Heating Association 2020
4.1 H2 pipeline transp. 40 barg | 1. Energinet assessment for DHB project.
4.1 H2 pipeline transp. 40 barg | 2. COWI experience
4.1 H2 pipeline transp. 40 barg | 3. Bundesnetzargentur - Hydrogen Core Network
4.2 pipeline transp. 90 barg | 1. Energinet assessment for DHB project.
4.2 pipeline transp. 90 barg | 2. COWI experience
4.2 pipeline transp. 90 barg | 3. Bundesnetzargentur - Hydrogen Core Network
4.3 pipeline transp. 140 barg | 1. Energinet assessment for DHB project.
4.3 pipeline transp. 140 barg | 2. COWI experience
4.3 pipeline transp. 140 barg | 3. Bundesnetzargentur - Hydrogen Core Network
5.1 H2 road transp. | 1. Network for Transport Measures (NTM) database, 2025
5.1 H2 road transp. | 2. COWI transport model

## 1.1 el Main distri50-60kVcabl
Technology |  | Energy Transport Electricity Main distribution, electricity cables
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, lines 20-100 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, lines above 100 MW [%] | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.5 | 0.15 | 0.5 | [A, B] | [1, 2, 3, 4]
| Energy losses, stations type 1 [%] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 | [A, B] | [1, 2, 3, 4]
| Energy losses, stations type 2 [%] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [A, B, S]
| Auxiliary electricity consumption [%] of energy transmitted | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [A, B, S] | 4
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 40 | 50 | C | 5
| Typical load profile [-] | 45% | 45% | 45% | 45% | 45% | 45% | 42.3% | 54% | D
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 5 | 1 | 5 | E
Financial data
| Investment costs; single line, 0-50 MW [€/MW/m] | 6.3802 | 6.3802 | 6.3802 | 6.3802 | 6.1061 | 6.7846 | 5.8438 | 7.2145 | [F, G] | [6, 7]
| Investment costs; single line, 50-100 MW [€/MW/m] | 4.1472 | 4.1472 | 4.1472 | 4.1472 | 3.969 | 4.41 | 3.7984 | 4.6894 | [H, G] | [6, 7]
| Investment costs; single line, 100-250 MW [€/MW/m] | 3.2965 | 3.2965 | 3.2965 | 3.2965 | 3.1548 | 3.5054 | 3.0193 | 3.7275 | [I, G] | [6, 7]
| Investment costs; single line, 250-500 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 6
| Investment costs; single line, 500-1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 7
| Investment costs; single line, above 1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J | 8
| Reinforcement costs [€/MW] | 16801.2889 | 16801.2889 | 16801.2889 | 16801.2889 | 17044.1948 | 17866.0323 | 17290.6125 | 18998.2513 | [K, O] | 6
| Investment costs; type 1 station [€/MW] | 80816.3266 | 80816.3266 | 80816.3266 | 80816.3266 | 81984.7345 | 85937.8768 | 83170.0348 | 91383.9937 | [L, O] | 8
| Investment costs; type 2 station [€/MW] | 4759.6563 | 4759.6563 | 4759.6563 | 4759.6563 | 4828.4694 | 5061.2886 | 4898.2773 | 5382.0363 | [M, O]
| Investments, percentage installation | 42% | 42% | 42% | 42% | 37.37% | 42% | 32.96% | 42% | P | 6
| Investments, percentage materials | 58% | 58% | 58% | 58% | 58% | 62.63% | 58% | 67.04% | P | 6
| Fixed O&M [€/MW/km/year] | 24.9898 | 26.2015 | 27.4719 | 28.8039 | 26.0952 | 26.5735 | 25.1642 | 26.5735 | Q | 9
| Variable O&M [€/MWh/km] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | R
Technology-specific data
References:
1. U.S. Energy Information Administration (http://www.eia.gov/tools/faqs/faq.cfm?id=105&t=3)
2. energinet.dk (http://www.energinet.dk/DA/KLIMA-OG-MILJOE/Energinetdks-miljoepaavirkninger/Miljoepaavirkninger-ved-transport-af-el/Sider/Tab-i-elnettet.aspx)
3. Svenska Kraftnät, Nätuvecklingsplan 2016 – 2025, Oktober 2015 (http://www.svk.se/siteassets/om-oss/rapporter/natutvecklingsplan-2016-2025.pdf)
4. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
5. Svenska Kraftnät, Technology (http://www.svk.se/en/grid-development/the-construction-process/technology/)
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. PEX Guiden, Ericsson
8. Standard value list for the Swedish Energy Markets Inspectorate (2015 value) (http://ei.se/sv/el/Elnat-och-natprisreglering/forhandsreglering-av-elnatstariffer-ar-2016-2019/dokument-elnatsreglering/normvardeslista-elnat-2016-2019/)
9. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. Energy losses are estimated from total energy loss on transmission levels in the voltage range 20kV to 130 kV in Sweden. Transmission lines/cables accounts for approximately 60% of the losses and transformers accounts for approximately 40%.
B. Development of energy loss over time depends on several factors. Today, transmission losses typically range between 1% to 3% in Denmark. The variation in transmission losses depends mainly on the amount of power transfer to neighboring countries. The trend in Denmark is towards increasing transfer and thus increasing losses. The uncertainty span for 2020 mainly takes changes in power transfer into account, where the lower bound corresponds to a reduction of power transfer to a 1998 level, and the upper bound corresponds to a continued increase in losses stemming from increased power transfer. Technology development with introduction of e.g. super conducting transformers and super conducting power lines could lead to reduced losses on transmission level. Other factors, such as load control/optimization could also reduce losses in generators due to increased load factor. This technology development is not anticipated to have effect before 2020, but is possible in a second upgrade of electricity system in 2050.
C. Cable life length depends on material characteristics and the thermal loading of the cable. Increasing cable area and thus reducing cable temperature leads to longer life length. Today, up to 40 years are realistic life length of a cable with moderate thermal loading. Technological development on cable materials is anticipated to give an increase in cable life length. This in combination with low thermal loadings could give life length of up to 50 years in the future.
D. Load profile varies significantly between different stations and cables and a general figure is given. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 20%.
E. Construction time ranges normally from 1 to 2 years. In technically complex projects and for long cable stretches, the construction time increases and could stretch up to 5 years.
F. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2. For power range 0-50 MW the costs is calculated as the average cost of two cables types with cross section areas 240 mm2 and 630 mm2,, corresponding to power levels of 20-35 MW and 50-60 MW respectively. The cost per MV decreases with increasing power level. The interval 20-35 MW has a cost of 6,7 €/MW/m and the interval 50-60 MW a cost of 4,2 €/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9. Power level below 20MW is not considered for this voltage level.
G. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
H. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 50 kV. Cost is calculated as the average cost between rural areas, dense populated areas and city areas. Adjusting factors for each area are: rural areas: 0,75, dense populated: 1,04, and city: 1,2.For power range 50-100 MW the costs is calculated as the average cost for three cables with cross section areas 630 mm2, 800mm2 and 1000 mm2, corresponding to power levels of 50-60 MW, 69 MW and 76 MW respectively. The cost per MV decreases with increasing power level. The power interval 50-60 MW has a cost of 4,2 €/MW/m, at power level of 69 MW the cost is 3,6 €/MW/m and at the power level 76 the cost is 3,4 €/MW/m. An increase in operation level to 60 kV will decrease the cost by a factor 0,9.
I. Costs are based on data for cables with design voltage of 72 kV and a operation voltage of 60 kV. Cost is calculated as the average cost between dense populated areas and city areas. Adjusting factors for each area are: dense populated: 0,94, and city: 1,06. For power range 100-250 MW the costs is given for a cable with cross section area of 1200 mm2, corresponding to a power level of 100 MW. Power levels above 100 MW are not considered for this voltage level.
J. Power levels above 100 MW are normally transported at higher voltage levels. In cases where it is motivated to transport higher power levels at 50/60 kV, this is done in parallele cable budles in the same shaft. The cost of two parallel cables can be calculated as the double cost of one cable reduced with 60 800 EUR per kilometer.
K. Reinforcement costs depends on where bottlenecks are situated in the grid. Here the reinforcement cost is given for an upgrade of transformer capacity by 40 MVA. Reinforcement of line/cable capacity is in parity with the investment cost in described in row 18-20 and depends on power level and cable length.
L. Station cost is based on a 40 MW station with 2 x 20 MVA transformers (72/12 kV). Station cost depends on a number of factors, such as power rating, redundancy on transformers etc. Station cost have an almost linear relation to the power rating and following relation holds for the power span 20-126 MW: Station cost (EUR) = 16 000 (€/MW) x Power rating (MW) + 2 350 000 (EUR). Using a single transformer instead of two reduces the cost by a factor 0,86-0,87.
M. Station cost is based on average cost for capacity banks and inductor with a design voltage of 72 kV. It is assumed that the equipment is installed in a existing station.
O. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
P. The percentage of the investment cost allocated to material cost and installation cost varies depending on area type (rural or city) and power level. An average is given here. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
Q. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost multiplied by the average cost of cables per MW and km given in row 18 to 20. It should be noted that the O&M cost in distribution system mainly is attributed to stations since there is practically no maintenaince on cables. The O&M cost is assumed to be reduced over time by an annual factor of 1-1,8% due to increased efficiency. Upper uncertainty bounds for 2020 and 2050 corresponds to no efficiency increase in O&M and lower bounds corresponds to a continuous annual efficiency increase of 1,8%
R. Variable O&M cost is in very low for electric transmission systems and considered to be negligible
S. Energy losses and auxiliary electricity consumption can be considered negligible

## 1.2 el distri Rural
Technology |  | Energy Transport Electricity Distribution, Rural
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 4.5 | 5.25 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D | [1, 5]
| - Residential | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D
| - Commercial | 44% | 44% | 44% | 44% | 44% | 44% | 32.56% | 46.64% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] Rural | 183.9635 | 183.9635 | 183.9635 | 183.9635 | 165.5671 | 183.9635 | 140.0698 | 218.9165 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 557.2073 | 557.2073 | 557.2073 | 557.2073 | 501.4866 | 557.2073 | 451.3379 | 557.2073 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 1501.4823 | 1501.4823 | 1501.4823 | 1501.4823 | 1351.3341 | 1501.4823 | 1216.2006 | 1501.4823 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 1683.319 | 1683.319 | 1683.319 | 1683.319 | 1514.9871 | 1683.319 | 1363.4884 | 1683.319 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 3982.3308 | 3982.3308 | 3982.3308 | 3982.3308 | 3584.0977 | 3982.3308 | 3225.688 | 3982.3308 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 43.5983 | 43.5983 | 43.5983 | 43.5983 | 39.3448 | 43.5983 | 35.4103 | 43.5983 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 93.5768 | 93.5768 | 93.5768 | 93.5768 | 90.3867 | 93.5768 | 81.348 | 93.5768 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 11690.7197 | 12228.7863 | 11176.328 | 12228.7863 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 71777.6585 | 71777.6585 | 71777.6585 | 71777.6585 | 68619.4415 | 71777.6585 | 65600.1861 | 71777.6585 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 62% | 62% | 62% | 62% | 57.35% | 62% | 52.56% | 62% | K | 6
| Investments, percentage materials [cables] | 38% | 38% | 38% | 38% | 38% | 42.65% | 42% | 38% | K | 6
| Investments, percentage installation [stations] | 22% | 22% | 22% | 22% | 18.86% | 22% | 16.61% | 19% | K | 6
| Investments, percentage materials [stations] | 78% | 78% | 78% | 78% | 78% | 81% | 78% | 81% | K | 6
| Fixed O&M [€/MW/year] | 1730.968 | 1706.7345 | 1682.8402 | 1659.2804 | 1699.8106 | 1730.968 | 1639.1681 | 1730.968 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 19%.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacing the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty bounds for 2020 assumes a reduction of 4,4% of the costs due to more efficient installations and a continued reduction by an additional 4,4% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty bounds for 2020 assumes a reduction of 17,6% of the investment costs due to more efficient installations and a continued reduction by an additional 10% for 2050.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeable
N. Auxiliary electricity consumption can be considered negligible

## 1.3 el distri suburban
Technology |  | Energy Transport Electricity Distribution, Suburban
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 3 | 3 | 3 | 3 | 3 | 3 | 2.25 | 3 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D | [1, 5]
| - Residential | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| - Commercial | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] Suburban | 409.3985 | 409.3985 | 409.3985 | 409.3985 | 368.4586 | 409.3985 | 331.6128 | 517.8891 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 1527.0032 | 1527.0032 | 1527.0032 | 1527.0032 | 1374.3029 | 1527.0032 | 1236.8726 | 1527.0032 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 4286.4554 | 4286.4554 | 4286.4554 | 4286.4554 | 3857.8099 | 4286.4554 | 3472.0289 | 4286.4554 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 4511.8904 | 4511.8904 | 4511.8904 | 4511.8904 | 4060.7014 | 4511.8904 | 3654.6313 | 4511.8904 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 9640.5371 | 9640.5371 | 9640.5371 | 9640.5371 | 8676.4834 | 9640.5371 | 7808.835 | 9640.5371 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 79.753 | 79.753 | 79.753 | 79.753 | 69.1192 | 79.753 | 62.2073 | 79.753 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 85.0698 | 85.0698 | 85.0698 | 85.0698 | 74.4361 | 85.0698 | 66.9925 | 85.0698 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 136.1117 | 136.1117 | 136.1117 | 136.1117 | 125.478 | 136.1117 | 112.9302 | 136.1117 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 11690.7197 | 12228.7863 | 11176.328 | 12228.7863 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 40408.1633 | 40408.1633 | 40408.1633 | 40408.1633 | 38630.2041 | 40408.1633 | 36930.4751 | 40408.1633 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 80% | 80% | 80% | 80% | 78% | 80% | 78% | 80% | K | 6
| Investments, percentage materials [cables] | 20% | 20% | 20% | 20% | 22% | 20% | 22% | 20% | K | 6
| Investments, percentage installation [stations] | 14% | 14% | 14% | 14% | 13% | 14% | 13% | 14% | K | 6
| Investments, percentage materials [stations] | 86% | 86% | 86% | 86% | 87% | 86% | 87% | 86% | K | 6
| Fixed O&M [€/MW/year] | 2851.2624 | 2811.3448 | 2771.9859 | 2733.1781 | 2799.9397 | 2851.2624 | 2700.0491 | 2851.2624 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen [Statistics from Swedish utility companies) from 2014 [http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, [2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution [http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate [http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference [1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference [1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor remains the same, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 26%.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval [one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level [a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area [power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level [a decrease by 17,6 %), this will decrease the installation costs.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N. Auxiliary electricity consumption can be considered negligible

## 1.4 el distri city
Technology |  | Energy Transport Electricity Distribution, City
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 1.5 | 2.25 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D | [1, 5]
| - Residential | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D
| - Commercial | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 57.5% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] City | 388.131 | 388.131 | 388.131 | 388.131 | 371.4552 | 412.728 | 334.166 | 531.0492 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 2285.188 | 2285.188 | 2285.188 | 2285.188 | 2187.0059 | 2285.188 | 2093.0422 | 2285.188 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 5974.0279 | 5974.0279 | 5974.0279 | 5974.0279 | 5717.3565 | 5974.0279 | 5471.7128 | 5974.0279 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 6139.9141 | 6139.9141 | 6139.9141 | 6139.9141 | 5876.1154 | 6139.9141 | 5623.6507 | 6139.9141 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 12899.7744 | 12899.7744 | 12899.7744 | 12899.7744 | 12345.5414 | 12899.7744 | 11815.1207 | 12899.7744 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 122.2879 | 122.2879 | 122.2879 | 122.2879 | 106.3373 | 122.2879 | 101.7685 | 122.2879 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 127.6047 | 127.6047 | 127.6047 | 127.6047 | 110.5908 | 127.6047 | 105.8393 | 127.6047 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 179.71 | 179.71 | 179.71 | 179.71 | 163.7594 | 179.71 | 156.7235 | 179.71 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 12431.5923 | 13003.7577 | 12637.7618 | 13003.7577 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 40408.1633 | 40408.1633 | 40408.1633 | 40408.1633 | 41078.3051 | 42968.9384 | 41759.5608 | 45691.9968 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 86% | 86% | 86% | 86% | N/A | N/A | N/A | N/A | K | 6
| Investments, percentage materials [cables] | 14% | 14% | 14% | 14% | N/A | N/A | N/A | N/A | K | 6
| Investments, percentage installation [stations] | 5% | 5% | 5% | 5% | 4% | 5% | 4% | 5% | K | 6
| Investments, percentage materials [stations] | 95% | 95% | 95% | 95% | 96% | 95% | 96% | 95% | K | 6
| Fixed O&M [€/MW/year] | 3240.4576 | 3397.5728 | 3562.3058 | 3735.026 | 3383.7895 | 3445.8142 | 3263.0694 | 3445.8142 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference (1). This gave an average value of 44 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor is increased by 6 %, the lower scenario is an increase in peak load without the use of smart grid leading to a decrease in load factor by 21%.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a constant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decrease the installation costs.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintenance on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N. Auxiliary electricity consumption can be considered negligible

## 1.5 el distri new area
Technology |  | Energy Transport Electricity Distribution, New developed areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 3 | 3 | 3 | 3 | 2.25 | 3 | 2.25 | 3 | A | 1
| Energy losses, stations [%] | 1.125 | 1.125 | 1.125 | 1.125 | 0.75 | 1.5 | 0.75 | 1.5 | B | 2
| Auxiliary electricity consumption [%] of energy delivered | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N | 3
| Technical life time [years] | 40 | 40 | 40 | 40 | 35 | 40 | 35 | 50 | C | [4, 5]
| Typical load profile [-] | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D | [1, 5]
| - Residential | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| - Commercial | 48% | 48% | 48% | 48% | 48% | 48% | 43.2% | 55.2% | D
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 5
Financial data
| Distribution network costs [€/MWh/year] New developed area | 183.9635 | 183.9635 | 183.9635 | 183.9635 | 165.5671 | 183.9635 | 140.0698 | 218.9165 | [E, F] | [1, 6]
| Investment costs; service line, 0-20 kW [€/unit] | 557.2073 | 557.2073 | 557.2073 | 557.2073 | 501.4866 | 557.2073 | 451.3379 | 557.2073 | [G, F] | 6
| Investment costs; service line, 20-50 kW [€/unit] | 1501.4823 | 1501.4823 | 1501.4823 | 1501.4823 | 1351.3341 | 1501.4823 | 1216.2006 | 1501.4823 | [G, F] | 6
| Investment costs; service line, 50-100 kW [€/unit] | 1683.319 | 1683.319 | 1683.319 | 1683.319 | 1514.9871 | 1683.319 | 1363.4884 | 1683.319 | [G, F] | 6
| Investment costs; service line, above 100 kW [€/unit] | 3982.3308 | 3982.3308 | 3982.3308 | 3982.3308 | 3584.0977 | 3982.3308 | 3225.688 | 3982.3308 | [G, F] | 6
| Investment costs; single line, 0-50 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 50-250 kW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Investment costs; single line, 100-250 kW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 250 kW-1 MW [€/m] | 38.2814 | 38.2814 | 38.2814 | 38.2814 | 34.0279 | 38.2814 | 30.6251 | 38.2814 | [H, F] | 6
| Investment costs; single line, 1 MW-5 MW [€/m] | 43.5983 | 43.5983 | 43.5983 | 43.5983 | 39.3448 | 43.5983 | 35.4103 | 43.5983 | [H, F] | 6
| Investment costs; single line, 5 MW-25 MW [€/m] | 93.5768 | 93.5768 | 93.5768 | 93.5768 | 90.3867 | 93.5768 | 81.348 | 93.5768 | [H, F] | 6
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [H, F]
| Reinforcement costs [€/MW] (Station) | 12228.7863 | 12228.7863 | 12228.7863 | 12228.7863 | 11690.7197 | 12228.7863 | 11176.328 | 12228.7863 | [I, F, J] | 6
| Investment costs; type 1 station [€/MW] | 40408.1633 | 40408.1633 | 40408.1633 | 40408.1633 | 38630.2041 | 40408.1633 | 36930.4751 | 40408.1633 | J | 6
| Investment costs; type 2 station [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0
| Investments, percentage installation [cables] | 80% | 80% | 80% | 80% | 78% | 80% | 78% | 80% | K | 6
| Investments, percentage materials [cables] | 20% | 20% | 20% | 20% | 22% | 20% | 22% | 20% | K | 6
| Investments, percentage installation [stations] | 14% | 14% | 14% | 14% | 13% | 14% | 13% | 14% | K | 6
| Investments, percentage materials [stations] | 86% | 86% | 86% | 86% | 87% | 86% | 87% | 86% | K | 6
| Fixed O&M [€/MW/year] | 1444.3554 | 1424.1344 | 1404.1965 | 1384.5378 | 1418.357 | 1444.3554 | 1367.7557 | 1444.3554 | L | 7
| Variable O&M [€/MWh] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M
Technology-specific data
References:
1. Särskilda rapporten-teknisk data from Energimarknadsinspektionen (Statistics from Swedish utility companies) from 2014 (http://www.ei.se/sv/Publikationer/Arsrapporter/)
2. The Scope for Energy Saving in the EU through the Use of Energy-Efficient Electricity Distribution Transformers. H. De Keukeabaer, D. Chapman, S. Fassbinder, M. McDermott, (2001).
3. International Electrotechnical Comission, Efficient Electrical Energy Transmission and Distribution (http://www.iec.ch/about/brochures/pdf/technology/transmission.pdf)
4. Energimarknadsinspektionens föreskrifter om intäktsramar för elnätsföretag. http://ei.se/Documents/Publikationer/rapporter_och_pm/Rapporter%202015/Ei_R2015_01.pdf
5. Sweco, Project data
6. EBR cost database, developed by Swedish bransch organisation Svensk Energi.
7. Swedish Energy Markets Inspectorate (http://ei.se/sv/el/Elnat-och-natprisreglering/de-olika-delarna-i-intaktsramen/)
Notes:
A. The line losses were calculated using reference (1) and the formula Total energy exported to customer / Total energy fed into the system. Lines in rural areas have a higher loss than lines in more populated areas.
B. Losses in a transformer tends to decrease with increasing transformer capacity. The losses also depends on the transformer load. When the transformer load decreases under 20 % there is a large increase in the losses. In general the losses are about 1-2 %
C. According to the network price regulation from Energimarknadsinspektionen, the technical life time for stations and cables are 40 years. In practice, cable technical life can be shorter, depending on the thermal loading of the cable.
D. Calculations for the load profile were based on reference (1). This gave an average value of 48 % for all areas. The load profile is not expected to change to 2020. For 2050 the upper scenario is a smart grid scenario, in which the load factor increases by 10 %, the lower scenario is an increase in peak load of 15 % without the use of smart grid leading to a corresponding decrease in load factor.
E. The distributions network costs are based on the average station cost and cable cost per customer divided by the average yearly energy transported to a customer. Assumptions on the average cable length per customer and the average number of stations per customer could be translated to a total distribution network cost per customer using the EBR cost database. Cost per MWh are affected both by changes in actual costs and changes in load factors. In 2020 load factors are assumed to be constant. Lower bounds assumes a reduction of 10% of the costs due to more efficient installations, no cost increased is assumed. For 2050 the lower bounds corresponds to a smart grid scenario with power factor increased by 15% in combination with a continued 10% cost decrease due to increased efficiency. The upper bound corresponds to a scenario where peak loads are increased by 15%, leading to reduced power factors and increased cost per MWh.
F. Price projections are based on an extrapolation of price development over the years 2000-2014 corrected for inflation. Over the six last years the prices have stabilized on a costant level and it is assumed that prices will remain stable. Lower uncertainty bounds for 2020 assumes a reduction of 10% of the costs due to more efficient installations and a continued reduction by an additional 10% for 2050. No increases in costs are anticipated and upper bounds are set to today's level for both 2020 and 2050.
G. Costs for service lines are based on cables with a design voltage of 0,4 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. The service line length was bases on the guidelines: 0-20 kW-20 m, 20-100 kW-50 m, Above 100 kW -100 m.
H. Costs for the single lines are based on cables with a design voltage of 12 kV. For each power level the corresponding current was calculated using a power factor of 0,90. The current corresponds to different cable areas and costs. Two cables were chosen for each interval (one for the lowest power level and one for the highest level in the interval). The average of these two costs were used in the table. Power levels below 250 kW and above 25 MW are not relevant for the specific voltage level. Above 6 MW more than one cable is needed. The cost of the material increases linear with the number of cables. The installation cost does not increase linear. An average cost based on the installation cost for one cable was used as a cost for more than one cable.
I. Reinforcement costs depends on whether it is the cables or stations that needs reinforcements. Reinforcement cost of cables is in parity with the investment cost for new single lines and depends on power level and cable length. Reinforcement of stations might be possible by replacering the current transformer with a new transformer with a higher power level. The cost for a new transformer, assuming the current station can still be used, is on average 11500 €/MW for a 800 kVA or 1250 kVA transformer.
J. The cost in €/MW of a 10/0.4 kV station depends on the desired power level of the station. A station with a low power level is more expensive per MW than a station with a high power level. In rural areas a lower power level is usually required. This results in a higher cost per MW for stations in rural areas. These assumptions were made: Rural areas: 1x315 kVA station. Suburban areas: 1x800 kVA station. City: 2x1250 kVA station. Costs for other requirements such as embedded/integrated stations are not included. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %). Upper level is if costs stay on today’s level. For 2050 better efficiency is expected which is estimated to decrease the cost by an additional 10 %.
K. The percentage of the investment cost allocated to material cost and installation cost varies widely depending on cable area (power level). When the number och cables in each shaft increases the percentage of the material cost also increases. The average for one cable was used in the table. In more densely populated areas the installation costs increases due to expensive shafts. Lower uncertainty is if Danish salaries decrease to the Swedish level (a decrease by 17,6 %), this will decreace the installation costs.
L. The fixed O&M cost are calculated as a standard annual cost of 0,51% of the investment cost. It should be noted that the O&M cost in distribution system is mainly attributed to stations since there is practically no maintanaince on cables. The O&M cost is assume to be reduced due to increased efficiency by an annual factor of 1-1,8%. Lower uncertainty bounds for 2020 and 2050 corresponds to a continuous annual efficiency increase of 1,8% and upper bounds corresponds to no efficiency increase in O&M.
M. Variable O&M cost is in very low for electric transmission systems and considered to be negligeble
N. Auxiliary electricity consumption can be considered negligible

## 1.6 el trans OH
Technology |  | Overhead lines AC, Overhead lines DC
year |  |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, OH lines AC [%/100 km] at rated power |  | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | 5 | 3
| Energy losses, OH lines DC [%/100 km] at rated power |  | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 | 5 | 3
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 4 | 2 | 4 | 6
Financial data
| Investment, OH lines AC [kEUR/km/MW], 4000 MW capacity |  | 0.75 | 0.75 | 0.72 | 0.68 | 0.65 | 0.62 | 0.58 | 0.98 | 0.48 | 0.8 | 1,2,3,4,9,10 | 1
| Investment, OH lines DC [kEUR/km/MW], 4000 MW capacity |  | 0.6 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.46 | 0.78 | 0.38 | 0.65 | 1,2,3,4,9 | 1
| Investments, percentage installation |  | 45% | 45% | 45% | 45% | 45% | 45% | 40% | 50% | 40% | 50% | 7
| Investments, percentage materials |  | 55% | 55% | 55% | 55% | 55% | 55% | 50% | 60% | 50% | 60% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
2. See [30], [31], [36], [42] in text chapter
3. See [50] in text chapter
Notes:
1. Low and high are minus/plus 30%
2. 2025 prices: after adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. Estimates, typical values (AC with compensation)
6. Estimates,project specific, depending on e.g., length of line
7. Estimates, based on stakeholder information
8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
9. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
10. Costs are including compensation (AC)

## 1.7 el trans AC&DC cables
Technology |  | Cables AC and DC, Onshore and Offshore
year |  |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, cables AC [%/100 km] at rated power |  | 5 | 5 | 5 | 5 | 5 | 5 | 2.5 | 7 | 2.5 | 7 | 7
| Energy losses, cables DC [%/100 km] at rated power |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 4 | 2 | 4 | 6
Financial data
| AC onshore cables [kEUR/km/MW], 500 MW capacity |  | 4.51 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 3.47 | 5.86 | 2.88 | 4.88 | 1,2,3,4,9,11,12 | 1
| AC offshore cables [kEUR/km/MW], 500 MW capacity |  | 4.51 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 3.47 | 5.86 | 2.88 | 4.88 | 1,2,3,4,9,11,12 | 1
| DC onshore cables [kEUR/km/MW], 1500-2000 MW capacity |  | 4.07 | 4.07 | 3.91 | 3.74 | 3.57 | 3.4 | 3.13 | 5.29 | 2.62 | 4.42 | 1,2,3,4,10,11 | 1
| DC offshore cables [kEUR/km/MW], 1500-2000 MW capacity |  | 3.22 | 3.22 | 3.09 | 2.95 | 2.82 | 2.68 | 2.48 | 4.19 | 2.06 | 3.48 | 1,2,3,4,10,11 | 1
| Investments, percentage installation |  | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 55% | 45% | 55% | 7
| Investments, percentage materials |  | 50% | 50% | 50% | 50% | 50% | 50% | 45% | 55% | 45% | 55% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2023
2. See [30], [31], [36], [42] in text chapter
Notes:
1. Low and high are minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. Estimates, typical values.
6. Estimates, project specific, depending on e.g., length of cable
7. Estimates, typical values (AC cables with compensation)
8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
9. 220 kV with capacity of about 500 MW
10. 525 kV bipole with capacity 1500-2000 MW
11. Nominal capacities. In practice lower values are achieved due to network limitations, losses etc.
12. Costs are including compensation (AC)

## 1.8 el substations
Technology |  | Substations AC and DC, Onshore and Offshore
year |  |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, substation [%] |  | 2 | 2 | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | 5
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 | 6
Financial data
| AC onshore substation [MEUR/MW], 500 MW capacity |  | 0.25 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.19 | 0.33 | 0.16 | 0.27 | 1,2,3,4,5,9 | 1
| AC offshore substation, incl. platform [MEUR/MW], 500 MW capacity |  | 0.6 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.46 | 0.78 | 0.38 | 0.65 | 1,2,3,4,5,9 | 1
| DC onshore substation [MEUR/MW], 1500-2000 MW capacity |  | 0.32 | 0.32 | 0.3 | 0.29 | 0.28 | 0.27 | 0.25 | 0.42 | 0.21 | 0.35 | 1,2,3,4,6,10 | 1
| DC offshore substation, incl. platform [MEUR/MW], 1500-2000 MW capacity |  | 0.75 | 0.75 | 0.72 | 0.69 | 0.66 | 0.63 | 0.58 | 0.98 | 0.48 | 0.82 | 1,2,3,4,6,10 | 1
| Investments, percentage installation |  | 45% | 45% | 45% | 45% | 45% | 45% | 40% | 50% | 40% | 50% | 7
| Investments, percentage materials |  | 55% | 55% | 55% | 55% | 55% | 55% | 50% | 60% | 50% | 60% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2023
2. See [30], [31], [36], [42] in text chapter
Notes:
1. 2025 prices: adding 20% to "year of source " prices
2. Low and high: minus/plus 30%
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. Estimates, typical values. AC substation includes transformers, switchgear, powerlines, compensation, control equipment etc.
6. Estimates, project specific, depends on size and location of station. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc
7. Estimates, based on stakeholder information
8. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here
9. 220 kV substation, capacity in the range of 500 MW
10. 525 kV HVDC substation, capacity in the range of 1500-2000 MW

## 1.9 el transformers
Technology |  | Transformers
year |  |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy losses, Transformer [%] |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 5
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 5
| Construction time [years] |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | 5
Financial data
| 380/110 kV, 300 MVA [kEUR/MVA] |  | 20.8 | 20.8 | 19.9 | 19.1 | 18.2 | 17.3 | 16 | 27 | 13.31 | 22.49 | 1,2,3,4 | 1
| 380/220 kV, 600 MVA [kEUR/MVA] |  | 16 | 16 | 15.3 | 14.7 | 14 | 13.3 | 12.3 | 20.8 | 10.23 | 17.29 | 1,2,3,4 | 1
| 220/110 kV, 200 MVA [kEUR/MVA] |  | 20.9 | 20.9 | 20 | 19.2 | 18.3 | 17.4 | 16.1 | 27.2 | 13.38 | 22.62 | 1,2,3,4 | 1
| Investments, percentage installation |  | 20% | 20% | 20% | 20% | 20% | 20% | 15% | 25% | 15% | 25% | 6
| Investments, percentage materials |  | 80% | 80% | 80% | 80% | 80% | 80% | 75% | 85% | 75% | 85% | 6
| Additional costs | -: 7
| Fixed O&M [& of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
2. See [30], [31], [36], [42] in text chapter
Notes:
1. 2025 prices: adding 20% to price from source
2. Low and high: minus/plus 30%
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025
5. Estimates, typical values.
6. Estimates, based on stakeholder information
7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here

## 1.10 el compensation
Technology |  | Compensation
year |  |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Technical life time [years] |  | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | 5
| Typical load profile (-) |  | 50% | 50% | 50% | 50% | 50% | 50% | 40% | 60% | 40% | 60% | 6
| Construction time [years] |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | 5
Financial data
| Capacitor bank [kEUR/MVAr] |  | 24 | 24 | 23 | 22 | 21 | 20 | 18 | 31 | 15 | 26 | 1,2,3,4 | 1
| SVC [kEUR/MVAr] |  | 60 | 60 | 58 | 55 | 53 | 50 | 46 | 78 | 38 | 65 | 1,2,3,4 | 1
| Reactor [kEUR/MVAr] |  | 25 | 25 | 24 | 23 | 22 | 21 | 19 | 33 | 16 | 27 | 1,2,3,4 | 1
| STATCOM [kEUR/MVAr] |  | 155 | 155 | 148 | 142 | 135 | 129 | 119 | 202 | 99 | 168 | 1,2,3,4 | 1
| Investments, percentage installation |  | 20% | 20% | 20% | 20% | 20% | 20% | 15% | 25% | 15% | 25% | 7
| Investments, percentage materials |  | 80% | 80% | 80% | 80% | 80% | 80% | 75% | 85% | 75% | 85% | 7
| Additional costs | -: 8
| Fixed O&M [% of capex per year] |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 2
Variable O&M [EUR/MWh/km]
Technology-specific data
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
2. See [30], [31], [36], [42] in text chapter
Notes:
1. Low and high: minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025
5. Estimates, typical values.
6. Estimates, load of reactive power
7. Estimates, (partly) based on stakeholder information
7. Additional costs:permits, rights, compensation for landowners, planning, project management may add up to 50% to investment (based on stakeholder information), but is not included here

## Input 1.6 - OH-lines
Go to Index | Go to relevant chapter
OH lines | [5 empty] | 2020 price level |  | Size of data sample | Reference | Comment
|  |  | Original price from source | Original, from source: Low | Original from, source: High | Pice from source | 2025
ACER, pwc, UIC, 2023 | Overhead line (MEUR/km)- AC | 110-150 kV 2 circuits | 0.32499 | 0.22437 | 0.39298 | 0.29053 |  | 3 | 1 | 1.2
|  | 220 kV 1 circuit | 0.41189 | 0.3033 | 0.54291 | 0.36822 |  | 7 | 1 | 1.2
|  | 220 kV 2 circuits | 0.5305 | 0.44169 | 0.67314 | 0.47425 |  | 21 | 1 | 1.2
|  | 330 kV 2 circuits | 0.5736 | 0.52186 | 0.5727 | 0.51278 |  | 5 | 1 | 1.2
|  | 380-400 kV 1 circuit | 0.46529 | 0.29774 | 0.60581 | 0.41595 |  | 18 | 1 | 1.2
|  | 400 kV 2 circuits | 1.261 | 0.5332 | 1.6349 | 1.1273 |  | 45 | 1 | 1.2
Overhead line (kEUR/km/MW)- AC
1100 | MW | 110-150 kV 2 circuits | 0.29545 | 0.20397 | 0.35725 | 0.26412 |  | 3 | 1 | 1.2
1100 | MW | 220 kV 1 circuit | 0.37444 | 0.27573 | 0.49355 | 0.33474 |  | 7 | 1 | 1.2
2200 | MW | 220 kV 2 circuits | 0.24114 | 0.20077 | 0.30597 | 0.21557 |  | 21 | 1 | 1.2
3300 | MW | 330 kV 2 circuits | 0.17382 | 0.15814 | 0.17355 | 0.15539 |  | 5 | 1 | 1.2
2000 | MW | 380-400 kV 1 circuit | 0.23264 | 0.14887 | 0.3029 | 0.20798 |  | 18 | 1 | 1.2
4000 | MW | 400 kV 2 circuits | 0.31524 | 0.1333 | 0.40872 | 0.28182 |  | 45 | 1 | 1.2
Netz, 2021 | Overhead line (MEUR/km)- AC | 380 kV, 2 circuits-AC | 2.5 |  |  | 2.4881 |  |  | 3 | 2
| 4000 MW OH line AC (kEUR/km/MW) | 381 kV, 2 circuits-AC | 0.625 |  |  | 0.62201 | 0.74642 |  | 3 | 2
Netz, 2021 | Overhead line (MEUR/km) DC | 2 circuits; 2 GW per circuit | 2 |  |  | 1.9904 |  |  | 3 | 2
| 4000 MW (kEUR/km/MW) DC | 2 circuits | 0.5 |  |  | 0.49761 | 0.59713 |  | 3 | 2
Balmorel model, 2022 | Overhead line - DC-kEUR/km/MW |  | 0.76 |  |  | 0.73786 |  |  | 2 | 3
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023
2. Balmorel Model assumptions
3. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment | 1. Low and high prices correspond to the 25 and 75 pencentiles of the data sample
2. 2025 prices are calculated by adding 20% to price from source
3. Balmorel 2022 data have already been lifted
OH lines, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
OH lines AC | kEUR/km/MW (4000 MW capacity) | 0.75 | 0.58 | 0.98 | 0.75 | 0.72 | 0.68 | 0.65 | 0.62 | 0.48 | 0.8 | 1 | 1,2,3,4
OH lines DC | kEUR/km/MW (4000 MW capacity) | 0.6 | 0.46 | 0.78 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.38 | 0.65 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment
1. Low and high are minus/plus 30%
2. 2025 prices: after adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050

## Input 1.7 - Cables
Go to Index | Go to relevant chapter
Cables
[7 empty] | 2020 price level |  | Size of data sample | Reference | Comment
|  |  |  | Original price from source | Original from source, low | Original from source , high | Price from source | 2025
ACER, pwc, UIC, 2023 | AC, Onshore underground cable | 110 - 150 kV 1 circuit | mEUR/km | 0.83066 | 0.43 | 0.64 | 0.74259 |  | 14 | 1 | 1
|  | 110 - 150 kV 2 circuits | mEUR/km | 2.2321 | 0.85 | 3.06 | 1.9954 |  | 4 | 1 | 1
|  | 220 - 225 kV 1 circuit | mEUR/km | 1.7784 | 1.23 | 2.11 | 1.5898 |  | 16 | 1 | 1
|  | 220 - 225 kV 2 circuits | mEUR/km | 4.4015 | 4.23 | 4.56 | 3.9349 |  | 4 | 1 | 1
|  | 300 - 500 kV 1 circuit | mEUR/km | 1.309 | 1.05 | 1.39 | 1.1702 |  | 4 | 1 | 1
280 | MW | 110 - 150 kV 1 circuit | kEUR/km/MW | 2.9666 | 1.5357 | 2.2857 | 2.6521 |  | 14 | 1 | 1
560 | MW | 110 - 150 kV 2 circuits | kEUR/km/MW | 3.9858 | 1.5179 | 5.4643 | 3.5632 |  | 4 | 1 | 1
560 | MW | 220 - 225 kV 1 circuit | kEUR/km/MW | 3.1756 | 2.1964 | 3.7679 | 2.8389 |  | 16 | 1 | 1
1120 | MW | 220 - 225 kV 2 circuits | kEUR/km/MW | 3.9299 | 3.7768 | 4.0714 | 3.5133 |  | 4 | 1 | 1
1000 | MW | 300 - 500 kV 1 circuit | kEUR/km/MW | 1.309 | 1.05 | 1.39 | 1.1702 |  | 4 | 1 | 1
Netz, 2023 prices | AC, 220 kV cable system, onshore |  | mEUR/km | 2.1 | [5 empty] | 5
| AC, 220 kV cable system, onshore | 500 MW | kEUR/km/MW | 4.2 |  |  | 3.7547 | 4.5056 |  | 5 | 2.3
AC Offshore cable
NETZ, 2021 prices | AC cable system 220 kV (offshore) Baltic Sea |  | mEUR/km | 2.9 |  |  | 2.8861 |  |  | 2
NETZ, 2023 prices | AC cable system 220 kV (offshore) Baltic Sea |  | mEUR/km | 2.1 |  |  | 1.8773 |  |  | 5
NETZ, 2023 prices | AC cable system 220 kV (offshore) Baltic Sea | 500 MW | kEUR/km/MW | 4.2 |  |  | 3.7547 | 4.5056 |  | 5 | 2.3
NETZ, 2021 prices | AC cable system 155 kV (offshore) Nord Sea |  | mEUR/km | 1.5 |  |  | 1.4928 |  |  | 2
ACER, pwc, UIC, 2023 | AC Offshore cable (132-380 kV) |  | mEUR/km | 2.0065 |  |  | 1.7938 |  | 9 | 1
Balmorel, 2022 prices | AC Offshore cable |  | kEUR/km/MW | 1.96 |  |  | 1.9023 |  |  | 3
NETZ, 2021 prices | DC onshore cable, 525 kV Nord Sea |  | mEUR/km | 6.5 |  |  | 6.4689 |  |  | 2
NETZ, 2023 prices | DC onshore cable, 525 kV Nord Sea and Baltic Sea |  | mEUR/km | 7.6 |  |  | 6.7942 |  |  | 5
NETZ, 2023 prices | DC cable system 525 kV (onshore) (bipole) | 2000 MW | kEUR/km/MW) | 3.8 |  |  | 3.4 | 4.07 |  | 5 | 2.4
Balmorel, 2022 prices | DC onshore cables |  | kEUR/(km*MW) | 1.7386 |  |  | 1.6875 |  |  | 3
ACER 2023 prices | DC offshore cable (300-500 kV) |  | mEUR/km | 1.1084 |  |  | 0.99092 |  | 6 | 1
| Offshore transmission cable, 150-320 kV (AC?, DC?- unclear) |  | mEUR/km | 3.2893 |  |  | 2.9406 |  | 7 | 1
NETZ 2021 prices | DC offshore cable system, 525 kV Nord Sea |  | mEUR/km | 4 |  |  | 3.9809 |  |  | 2
NETZ 2023 prices | DC offshore cable system, 525 kV Nord Sea and Baltic Sea |  | mEUR/km | 6 |  |  | 5.3638 |  |  | 5
NETZ 2023 prices | DC offshore cable system, 525 kV (bipole) | 2000 MW | kEUR/km/MW | 3 |  |  | 2.68 | 3.22 |  | 5 | 2.4
NETZ 2021 prices | DC offshore cable system, 525 kV Nord Sea and Baltic Sea |  | mEUR/km | 2 |  |  | 1.9904 |  |  | 2
2024 ENTSO-E planning prices | DC offshore cables |  | kEUR/(km*MW) | 1.618 |  |  | 1.4038 |  |  | 4
Tyndp 2022-project promoters (2022 prices) | DC offshore cables |  | kEUR/(km*MW) | 1.7 |  |  | 1.65 |  |  | 6
DNV2021 prices | DC offshore cables
| 0,5 GW 525 kV Cable |  | mEUR/km | 1.64 |  |  | 1.6322 |  |  | 7
| 1 GW 525 kV Cable |  | mEUR/km | 1.89 |  |  | 1.881 |  |  | 7
| 1,5 GW 525 kV Cable |  | mEUR/km | 2.14 |  |  | 2.1298 |  |  | 7
| 2 GW 525 kV cable |  | mEUR/km | 2.47 |  |  | 2.4582 |  |  | 7
DNV2021 prices | DC offshore cables
| 0,5 GW 525 kV Cable |  | kEUR/km/MW | 3.28 |  |  | 3.28 |  |  | 7
| 1 GW 525 kV Cable |  | kEUR/km/MW | 1.89 |  |  | 1.89 |  |  | 7
| 1,5 GW 525 kV Cable |  | kEUR/km/MW | 1.4267 |  |  | 1.4267 |  |  | 7
| 2 GW 525 kV cable |  | kEUR/km/MW | 1.235 |  |  | 1.235 |  |  | 7
Balmorel 2022 prices | DC offshore cables |  | kEUR/(km*MW) | 2.1272 |  |  | 2.0646 |  |  | 3
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023, https://www.acer.europa.eu/sites/default/files/documents/Publications/UIC_report_2023.pdf
2. Netzentwicklungsplan Strom (German TSOs), version 2021
3. Balmorel model data
4. ENTSO-E planning prices for TYNDP 2024
5. Netzentwicklungsplan Strom (German TSOs), version 2023
6. TYNDP 2022 project sheets (from project promoters)
7. Screening of possible hub concepts to integrate offshore wind capacity in the North Sea, DNV for DEA, 2021
Comments | 1. Low and High values are 25 and 75 percentiles of the sample
2. Shown 2025 prices estimated by adding 20 % to price from source
3. 220 kV with capacity of about 500 MW
4. 525 kV bipole with capacity 1500-2000 MW
Cables, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
AC onshore cables | kEUR/km/MW (500 MW capacity) | 4.51 | 3.47 | 5.86 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 2.88 | 4.88 | 1 | 1,2,3,4
AC offshore cables | kEUR/km/MW (500 MW capacity) | 4.51 | 3.47 | 5.86 | 4.51 | 4.32 | 4.13 | 3.94 | 3.75 | 2.88 | 4.88 | 1 | 1,2,3,4
DC onshore cables | kEUR/km/MW (1500-2000 MW capacity) | 4.07 | 3.13 | 5.29 | 4.07 | 3.91 | 3.74 | 3.57 | 3.4 | 2.62 | 4.42 | 1 | 1,2,3,4
DC offshore cables | kEUR/km/MW (1500-2000 MW capacity) | 3.22 | 2.48 | 4.19 | 3.22 | 3.09 | 2.95 | 2.82 | 2.68 | 2.06 | 3.48 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2023
Comment
1. Low and high are minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050

## Input 1.8 - Substations
Go to Index | Go to relevant chapter
Substations | [6 empty] | 2020 price level
|  |  |  | Original price from source | Original, low | Original, high | Price from source | 2025 | Size of data sample | Reference | Comment
ACER, 2023 prices | Onshore AC substation | 0-5 bays, all | mEUR/asset | 5.307 | 2.2 | 6.7 | 4.7443 |  | 77 | 1 | 1
|  | New/AIS/maximum 5 bays |  | 11.7127 | 3.59 | 16.91 | 10.4708 |  | 24 | 1
|  | New/GIS/maximum 5 bays |  | 13.619 | 5.4 | 15.99 | 12.175 |  | 8 | 1
|  | Refurbishment or Upgrade/AIS/maximum 5 bays |  | 3.4011 | 2.12 | 4.3 | 3.0405 |  | 28 | 1
|  | Refurbishment or Upgrade/GIS/maximum 5 bays |  | 4.4476 | 1 | 6.4 | 3.976 |  | 13 | 1
|  | 6-9 bays, all |  | 12.586 | 7.88 | 16.41 | 11.2516 |  | 62 | 1
|  | New/AIS/from 6 to 9 bays |  | 12.1413 | 8.18 | 16.68 | 10.854 |  | 24 | 1
|  | New/GIS/from 6 to 9 bays |  | 9.8208 | 7.82 | 11.53 | 8.7795 |  | 20 | 1
|  | Refurbishment or Upgrade/AIS/from 6 to 9 bays |  | 15.3779 | 6.81 | 23.44 | 13.7474 |  | 14 | 1
|  | 10-60 bays, all |  | 29.845 | 19.26 | 40.33 | 26.6807 |  | 23 | 1
|  | 10-60 bays , New |  | 43.572 | 22.72 | 58.86 | 38.9523 |  | 13 | 1
|  | 10-60 bays Refurbishment/upgrade |  | 29.8453 | 20.88 | 41.92 | 26.681 |  | 10 | 1
ACER, 2023 prices | Onshore AC substation | All | kEUR/kV | 31.248 | 16.683 | 43.45 | 27.9349 |  | 118 | 1 | 3
|  | AIS New |  | 31.72 | 18.52 | 43.62 | 28.3569 |  | 48 | 1 | 4
|  | AIS updated/Refurbished |  | 27.566 | 12.33 | 45.26 | 24.6433 |  | 33 | 1
|  | GIS New |  | 35.105 | 27.68 | 42.31 | 31.383 |  | 26 | 1 | 5
ACER, 2023 prices | Onshore AC substation | All | kEUR/MVA | 68.823 | 37.58 | 93.13 | 61.526 |  | 44 | 1 | 2
|  | AIS New |  | 65.884 | 43.41 | 81.89 | 58.8986 |  | 19 | 1
|  | AIS updated/Refurbished |  | 50.028 | 23.46 | 70.73 | 44.7238 |  | 16 | 1
|  | GIS New |  | 123.678 | 93.48 | 133.74 | 110.565 |  | 8 | 1
ACER, 2023 prices | Onshore AC substation | 220-275 kV | mEUR/bay | 1.206 | 0.84 | 1.52 | 1.0781 |  | 48 | 1
|  | 300-330 kV |  | 1.21 | 1.05 | 1.37 | 1.0817 |  | 4 | 1
|  | 380-400 kV |  | 3.382 | 1.15 | 5.24 | 3.0234 |  | 56 | 1
Netz, 2023 | AC onshore substation, 220 kV |  | mEUR/MW | 0.24 |  |  | 0.21455 | 0.25 |  | 4 | 7.8
ACER, 2023 prices | AC Offshore substation |  | mEUR/asset | 133.0696 | 104.73 | 154.83 | 118.9608 |  | 6 | 1
Netz, 2023 | AC offshore substation, 220 kV (with platform) |  | mEUR/MW | 0.56 |  |  | 0.50063 | 0.6 |  | 4 | 7.8
NETZ, 2021 prices | AC (Offshore +Onshore station)/2 | Baltic Sea | mEUR/MW | 0.35 |  |  | 0.34833 |  |  | 2 | 6
NETZ, 2023 prices | AC (Offshore +Onshore station)/2 | 220 kV, AC, Baltic SEA | mEUR/MW | 0.4 |  |  | 0.35759 |  |  | 4 | 6
NETZ, 2021 prices | DC (offshore +onshore station)/2, 320 kV (with AC/DC converter ) | North Sea | mEUR/MW | 0.5 |  |  | 0.49761 |  |  | 2 | 6 | -
NETZ, 2021 prices | DC (onshore +offshore station)/2, 525 kV (with AC/DC converter) | North Sea | mEUR/MW | 0.38 |  |  | 0.37818 |  |  | 2 | 6
NETZ, 2023 prices | DC onshore 525 kV station with converter (AC/DC) | North Sea and Baltic Sea | mEUR/MW | 0.3 |  |  | 0.26819 | 0.32 |  | 4 | 7.9
NETZ, 2023 prices | DC offshore station 525 kV with converter (AC/DC), incl. platform | North Sea and Baltic Sea | mEUR/MW | 0.7 |  |  | 0.62578 | 0.75 |  | 4 | 7.9
ENTSO-E-planning prices 2024 | Onshore DC station with converter (AC/DC) |  | mEUR/MW | 0.25 |  |  | 0.22 |  |  | 5
Tyndp 2022-project promoters | Onshore DC station with converter (AC/DC) |  | mEUR/MW | 0.15 |  |  | 0.14 |  |  | 6
DNV 2021 prices | Onshore DC station with converter (AC/DC) | 1 GW, 525 kV | mEUR/MW | 0.18 |  |  | 0.18 |  |  | 7
Balmorel 2022 prices | One DC/AC substation |  | mEUR/MW | 0.23547 |  |  | 0.22855 |  |  | 3
| Offshore platform AC (no substation) |  | mEUR/MW | 0.1523 |  |  | 0.14782 |  |  | 3
| Offshore platform DC (no substation) |  | mEUR/MW | 0.46813 |  |  | 0.45437 |  |  | 3
Comments
1. Substation bay: A set of equipment which connects a circuit into a substation.
2. MVA: Mega Volt Ampere measures the size of transformers/substations
3. kV is busbar rating
4. AIS: Air insulated substation (typical open air station).
5.GIS: In a gas insulated substation (GIS) the major conducting structures are contained within a sealed environment with a dielectric gas (SF6)
6.Half of one offshore + one onshore station
7. Prices for 2025 by adding 20% to price from source
8. 220 kV substation, capacity in the range of 500 MW
9. 525 kV HVDC substation, capacity in the range of 1500-2000 MW
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023, https://www.acer.europa.eu/sites/default/files/documents/Publications/UIC_report_2023.pdf
2. Netzentwicklungsplan Strom (German TSOs), version 2021
3. Balmorel model data
4. Netzentwicklungsplan Strom (German TSOs), version 2023
5. ENTSO-E planning prices for TYNDP 2024
6. TYNDP 2022 project sheets (from project promoters)
7. Screening of possible hub concepts to integrate offshore wind capacity in the North Sea, DNV for DEA, 2021
Substations, 2020 price level
|  | Price from source | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
AC onshore substation | MEUR/MW (500 MW capacity) | 0.21 | 0.25 | 0.19 | 0.33 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.16 | 0.27 | 1 | 1,2,3,4,5
AC offshore substation, incl. platform | MEUR/MW (500 MW capacity) | 0.5 | 0.6 | 0.46 | 0.78 | 0.6 | 0.58 | 0.55 | 0.53 | 0.5 | 0.38 | 0.65 | 1 | 1,2,3,4,5
DC onshore substation with converter (AC/DC) | MEUR/MW (1500-2000 MW capacity) | 0.27 | 0.32 | 0.25 | 0.42 | 0.32 | 0.3 | 0.29 | 0.28 | 0.27 | 0.21 | 0.35 | 1 | 1,2,3,4,6
DC offshore substation with converter (AC/DC), incl. platform | MEUR/MW (1500-2000 MW capacity) | 0.63 | 0.75 | 0.58 | 0.98 | 0.75 | 0.72 | 0.69 | 0.66 | 0.63 | 0.48 | 0.82 | 1 | 1,2,3,4,6
References
1. Netzentwicklungsplan Strom (German TSOs), version 2023
Comment
1. 2025 prices: adding 20% to "year of source " prices
2. Low and high: minus/plus 30%
3. Prices in 2050 assumed to be as prices before 20% increase in 2025
4. Prices assumed to decrease linearly from 2030 to 2050
5. AC substation includes transformers, switchgear, powerlines, compensation, control equipment etc.
| 6. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc | DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters , lightning towers, ancillary plant etc

## Input 1.9 - Transformers
Go to Index | Go to relevant chapter
Transformers | [5 empty] | 2020 price level
|  |  | Original price from source | Original low | Original high | Price from source | 2025 | Size of data sample | Reference | Comment
ACER, 2023 prices | 150/60 kV | mEUR/asset | 1.2123 | 1.1 | 1.27 | 1.0837 |  | 3 | 1 | 1
| 220/66 kV | mEUR/asset | 1.5361 | 1.34 | 1.72 | 1.3732 |  | 12 | 1 | 1
| 400/110 kV | mEUR/asset | 4.36 | 3.63 | 4.73 | 3.8977 |  | 15 | 1 | 1
| 400/220 kV | mEUR/asset | 4.6312 | 2.94 | 6.18 | 4.1402 |  | 7 | 1 | 1
| 150/60 kV | kEUR/MVA | 63.8 | 51.26 | 88.79 | 57.0356 |  | 3 | 1 | 1
| 220/66 kV | kEUR/MVA | 97.7 | 82.66 | 108.7 | 87.3413 |  | 12 | 1 | 1
| 400/110 kV | kEUR/MVA | 76.8 | 57.39 | 92.83 | 68.6573 |  | 15 | 1 | 1
| 400/220 kV | kEUR/MVA | 28.2 | 22.75 | 34.46 | 25.2101 |  | 7 | 1 | 1
DNV, 2021 prices | 210/30 kV, 700 MVA | mEUR/asset | 7.5 |  |  | 7.4642 |  |  | 2
| 210/30 kV, 500 MVA | mEUR/asset | 5.1 |  |  | 5.0756 |  |  | 2
| 210/30 kV, 700 MVA | kEUR/MVA | 10.7143 |  |  | 10.6631 |  |  | 2
| 210/30 kV, 500 MVA | kEUR/MVA | 10.2 |  |  | 10.1513 |  |  | 2
NETZ, 2021 prices
| 380/110 kV, 300 MVA | kEUR/MVA | 17.3333 |  |  | 17.2505 | 20.8 |  | 3 | 2
| 380/220 kV, 600 MVA | kEUR/MVA | 13.3333 |  |  | 13.2696 | 16 |  | 3 | 2
| 220/110 kV, 200 MVA | kEUR/MVA | 17.5 |  |  | 17.4164 | 20.9 |  | 3 | 2
Comments
1. Low and high are the 25 and 75 percentiles of the sample
2. 2025 prices obtained by adding 20% to price from source
References
1. Unit Investment Cost Indicators - Project Support to ACER. Final report, pwc, Sept. 2023
2. Screening of possible hub concepts to integrate offshore wind capacity in the North Sea, DNV for DEA, 2021
3. Netzentwicklungsplan Strom (German TSOs), version 2021
Transformers, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
380/110 kV, 300 MVA | kEUR/MVA | 20.8 | 16 | 27 | 20.8 | 19.9 | 19.1 | 18.2 | 17.3 | 13.31 | 22.49 | 1 | 1,2,3,4
380/220 kV, 600 MVA | kEUR/MVA | 16 | 12.3 | 20.8 | 16 | 15.3 | 14.7 | 14 | 13.3 | 10.23 | 17.29 | 1 | 1,2,3,4
220/110 kV, 200 MVA | kEUR/MVA | 20.9 | 16.1 | 27.2 | 20.9 | 20 | 19.2 | 18.3 | 17.4 | 13.38 | 22.62 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment
1. 2025 prices: adding 20% to price from source
2. Low and high: minus/plus 30%
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025

## Input 1.10 - Compensation
Go to Index | Go to relevant chapter
Compensation | Year of source: 2022 prices (price level 2020)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV | Reference | Comment
| Reactor (kEUR/MVAr) | 13.4929 | 13.4929 | 13.4929 | 13.4929 | 13.4929 | 13.4929 | 20.7682 | 29.9985 | 1 | 1,2,3
| Capacitor bank (kEUR/MVAr) | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 9.9401 | 1 | 1,2,3
| SVC, Static VAr compensator (kEUR/MVAr) | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 95.5984 | 1 | 1,2,3
| STATCOM (kEUR/MVAr) | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 189.2216 | 1 | 1,2,3
Comments
1. MVAr: MVA reactive power
2. Unit costs include all material, shipping, foundation, and installation costs, taxes (not specified) and contingency
3. Original prices in 2022 US$: exchange rate in 2022 is 0,951 EUR/$;
References
1. Transmission Cost Estimation Guide For MTEP22, April 2022 (DRAFT)
Compensation | 2025 prices (price level 2020)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV | Reference | Comment
| Reactor (kEUR/MVAr) | 16.1915 | 16.1915 | 16.1915 | 16.1915 | 16.1915 | 16.1915 | 24.9219 | 35.9983 | 1 | 1,2,3,4
| Capacitor bank (kEUR/MVAr) | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 11.9282 | 1 | 1,2,3,4
| SVC, Static VAr compensator (kEUR/MVAr) | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 114.7181 | 1 | 1,2,3,4
| STATCOM (kEUR/MVAr) | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 227.0659 | 1 | 1,2,3,4
References
1. Transmission Cost Estimation Guide For MTEP22, April 2022 (DRAFT)
Comments
1. MVAr: MVA reactive power
2. Unit costs include all material, shipping, foundation, and installation costs, taxes (not specified) and contingency
3. Original prices in 2022 US$: exchange rate in 2022 is 0,951 EUR/$;
4. Prices in 2025: addition of 20% to price from source
Compensation
Price level 2020
|  |  | Unit | Price, original from source | Price from source | 2025 | Reference | Comment
Netz,2021 | 380 kV, 100 MVAr | Capacitor bank | kEUR/MVAr | 20 | 19.9045 | 24 | 1 | 1
Netz,2021 | 380 kV, SVC | SVC | kEUR/MVAr | 50 | 49.7611 | 60 | 1 | 1
Netz,2021 | 380 kV, 100 MVAr | Reactor | kEUR/MVAr | 21 | 20.8997 | 25 | 1 | 1
Netz,2021 | 380 kV | STATCOM | kEUR/MVAr | 130 | 129.379 | 155 | 1 | 1
References:
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment:
1. 2025 prices by adding 20% to price from source
Compensation, 2020 price level
|  | 2025 | 2025 low | 2025 high | 2030 | 2035 | 2040 | 2045 | 2050 | 2050 low | 2050 high | Reference | Comment
Capacitor bank | kEUR/MVAr | 24 | 18 | 31 | 24 | 23 | 22 | 21 | 20 | 15 | 26 | 1 | 1,2,3,4
SVC | kEUR/MVAr | 60 | 46 | 78 | 60 | 58 | 55 | 53 | 50 | 38 | 65 | 1 | 1,2,3,4
Reactor | kEUR/MVAr | 25 | 19 | 33 | 25 | 24 | 23 | 22 | 21 | 16 | 27 | 1 | 1,2,3,4
STATCOM | kEUR/MVAr | 155 | 119 | 202 | 155 | 148 | 142 | 135 | 129 | 99 | 168 | 1 | 1,2,3,4
References
1. Netzentwicklungsplan Strom (German TSOs), version 2021
Comment
1. Low and high: minus/plus 30%
2. 2025 prices: adding 20% to price from source
3. Prices assumed to decrease linearly from 2030 to 2050
4. Prices in 2050 assumed to be as prices before 20% increase in 2025

## 2.1 gas Main distri line
Technology |  | Energy Transport, Natural Gas Main distribution line
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A | 1
| Energy losses, lines 20-100 MW [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A
| Energy losses, lines above 100 MW [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 0.15 | 0.01 | 0.15 | A
Energy losses, stations type 1 [%] | bar: Est to -
| Energy losses, stations type 2 [%] | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.12 | 0 | 0.12 | C | 2
| Auxiliary electricity consumption [%] of energy transmitted | 0.005 | 0.005 | 0.005 | 0.005 | 0.00425 | 0.00575 | 0.00425 | 0.00575 |  | 2
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
| Typical load profile [-] | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.4 | 0.05 | 0.4 |  | 2
| Construction time [years] | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.7 | 1.5 | D | 2
Financial data
| Investment costs; single line, 0-50 MW [€/MW/m] | 11.4844 | 11.4844 | 11.4844 | 11.4844 | 9.1875 | 13.7813 | 9.1875 | 13.7813 | [E, F] | 2
| Investment costs; single line, 50-100 MW [€/MW/m] | 4.4662 | 4.4662 | 4.4662 | 4.4662 | 3.5729 | 5.3594 | 3.5729 | 5.3594 | [E, G] | 2
| Investment costs; single line, 100-250 MW [€/MW/m] | 2.382 | 2.382 | 2.382 | 2.382 | 1.9056 | 2.8583 | 1.9056 | 2.8583 | [E, G] | 2
| Investment costs; single line, 250-500 MW [€/MW/m] | 1.2441 | 1.2441 | 1.2441 | 1.2441 | 0.99532 | 1.493 | 0.99532 | 1.493 | [E, G] | 2
| Investment costs; single line, 500-1000 MW [€/MW/m] | 0.72309 | 0.72309 | 0.72309 | 0.72309 | 0.57847 | 0.86771 | 0.57847 | 0.86771 | [E, G] | 1
Investment costs; single line, above 1000 MW [€/MW/m] | bar: Est to -
Reinforcement costs [€/MW] | bar: Est to -
| Investment costs; type 1 station [€/MW] | - | - | - | - | - | - | - | - | [B, J]
| Investment costs; type 2 station [€/MW] | 28711.0634 | 28711.0634 | 28711.0634 | 28711.0634 | 7443.609 | 47851.7723 | - | - | [C, K] | 2
| Investments, percentage installation | 75% | 75% | 75% | 75% | 65% | 85% | 65% | 85% | 0 | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 15% | 35% | 15% | 35% | 0 | 2
| Fixed O&M [€/MW/km/year] | 0.12865 | 0.12865 | 0.12865 | 0.12865 | 0.10292 | 0.15438 | 0.10292 | 0.15438 | 0 | 2
| Variable O&M [€/MWh/km] | 1.1968e-05 | 1.1968e-05 | 1.1968e-05 | 1.1968e-05 | 9.5743e-06 | 1.4361e-05 | 9.5743e-06 | 1.4361e-05 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. There are no general data available for the Danish gas system. The stated losses are based on a European survey that includes all parts in level 2 of the transmission, including stations. It is assumed that the losses (given as kg/km) are the same for transmission level 1 and 2. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. Type 1 MR stations supplying the transmission system level 2-not part of the scope
C. Type 2 MR stations supplying the 4 bar distribution system. The stated number represents the gas consumption for preheating before expansion from 40 to 4 bar. Expansion from 19 or 16 bar to 4 bar doesn't require preheating. Losses are included in the number stated for lines, see note A.
D. Includes enginering, tender, and construction.
E. Rates include VVM review, landowner compensation and archaeological screening. Based on 20 km, of which 8 % is based on drilling.
F. Data given is for a 50 MW capacity
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H. Not possible to give general numbers. Depends on kind of reinforcement. Can be calculated based on the other numbers given.
I. Capacity not relevant-too high
J. Type 1 MR stations supplying the transmission system level 2-not part of the scope
K. Type 1 MR stations supplying the transmission system level 2 .The stated costs are the average cost for a 40/4 bar MR station where reheating after expansion is required and a 19/4 bar MR station where reheating is not necessary. The cost is only modestly size dependent. A 40/4 bar station capacity of 10.000 m3/h is 20 % higher than a similar station with a capacity of 5.000 m3/h.

## 2.2 gas Rural
Technology |  | Energy Transport Natural Gas Distribution, New distribution in existing rual areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
Energy losses, stations [%] | bar: Est to -
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
Typical load profile [-] | bar: -
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | Est: N/A; Est: N/A; Est: N/A; Est: N/A; -: D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs [€/MWh/year], Rural | 148.8722 | 148.8722 | 148.8722 | 148.8722 | 138.2385 | 159.5059 | 138.2385 | 159.5059 | 0 | 2
| Investment costs; service line, 0-20 kW [€/unit] | 1701.3963 | 1701.3963 | 1701.3963 | 1701.3963 | 1488.7218 | 1914.0709 | 1488.7218 | 1914.0709 | 0 | 2
Investment costs; service line, 20-50 kW [€/unit] | bar: Est to -
Investment costs; service line, 50-100 kW [€/unit] | bar: Est to -
Investment costs; service line, above 100 kW [€/unit] | bar: Est to -
| Investment costs; single line, 0-50 kW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 50-250 kW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 100-250 kW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 250 kW-1 MW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | F
| Investment costs; single line, 1 MW-5 MW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | G
| Investment costs; single line, 5 MW-25 MW [€/m] | 72.6638 | 72.6638 | 72.6638 | 72.6638 | 65.3974 | 79.9302 | 65.3974 | 79.9302 | G
| Investment costs; single line, 25 MW-100 MW [€/m] | - | - | - | - | - | - | - | - | 0
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 2
| Fixed O&M [€/MW/year] | 797.5295 | 797.5295 | 797.5295 | 797.5295 | 638.0236 | 957.0354 | 638.0236 | 957.0354 | 0 | 2
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There is no power consuming parts in the distribution system
D. Based on given case
E. Capacity range not relevant for given case
F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two is stated in the table.
H. Reinforcement not relevant
I. No station will be installed for the distribution network

## 2.3 gas Suburban
Technology |  | Energy Transport, Natural Gas Distribution, New distribution in existing suburban areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
Energy losses, stations [%] | bar: Est to -
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
Typical load profile [-] | bar: Est to Upper
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | Est: N/A; Est: N/A; Est: N/A; Est: N/A; -: D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs [€/MWh/year] Suburban | 159.5059 | 159.5059 | 159.5059 | 159.5059 | 148.8722 | 180.7734 | 148.8722 | 180.7734 | 0 | 2
| Investment costs; service line, 0-20 kW [€/unit] | 1701.3963 | 1701.3963 | 1701.3963 | 1701.3963 | 1488.7218 | 1914.0709 | 1488.7218 | 1914.0709 | 0 | 2
Investment costs; service line, 20-50 kW [€/unit] | bar: Est to -
Investment costs; service line, 50-100 kW [€/unit] | bar: Est to -
Investment costs; service line, above 100 kW [€/unit] | bar: Est to -
| Investment costs; single line, 0-50 kW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 50-250 kW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 100-250 kW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 250 kW-1 MW [€/m] | 56.7132 | 56.7132 | 56.7132 | 56.7132 | 51.0419 | 62.3845 | 51.0419 | 62.3845 | F
| Investment costs; single line, 1 MW-5 MW [€/m] | 63.8024 | 63.8024 | 63.8024 | 63.8024 | 57.4221 | 70.1826 | 57.4221 | 70.1826 | G
| Investment costs; single line, 5 MW-25 MW [€/m] | 92.159 | 92.159 | 92.159 | 92.159 | 82.9431 | 101.3749 | 82.9431 | 101.3749 | G
| Investment costs; single line, 25 MW-100 MW [€/m] | - | - | - | - | - | - | - | - | 0
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 2
| Fixed O&M [€/MW/year] | 329.6455 | 329.6455 | 329.6455 | 329.6455 | 265.8432 | 393.4479 | 265.8432 | 393.4479 | 0 | 2
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. There are no general data available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected that the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There is no power consuming parts in the distribution system
D. Based on given case
E. Capacity range not relevant for given case
F. Stated number is for a Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H. Reinforcement not relevant
I. No station will be installed for the distribution network

## 2.4 gas City
Technology |  | Energy Transport Natural Gas Distribution, New distribution in existing city areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | - | - | - | - | - | - | - | - | A | 1
| Energy losses, stations [%] | - | - | - | - | - | - | - | - | B | 1
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C | 1
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 1
Typical load profile [-] | bar: -
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 1
Financial data
| Distribution network costs [€/MWh/year] City | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 0 | 1
| Investment costs; service line, 0-20 kW [€/unit] | - | - | - | - | - | - | - | - | 0
| Investment costs; service line, 20-50 kW [€/unit] | - | - | - | - | - | - | - | - | 0
| Investment costs; service line, 50-100 kW [€/unit] | - | - | - | - | - | - | - | - | 0
| Investment costs; service line, above 100 kW [€/unit] | 15950.5908 | 15950.5908 | 15950.5908 | 15950.5908 | 12760.4726 | 19140.7089 | 12760.4726 | 19140.7089 | E | 1
| Investment costs; single line, 0-50 kW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 50-250 kW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 100-250 kW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 250 kW-1 MW [€/m] | 68.0559 | 68.0559 | 68.0559 | 68.0559 | 61.2503 | 74.8614 | 61.2503 | 74.8614 | 0 | 1
| Investment costs; single line, 1 MW-5 MW [€/m] | 76.5628 | 76.5628 | 76.5628 | 76.5628 | 68.9066 | 84.2191 | 68.9066 | 84.2191 | 0 | 1
| Investment costs; single line, 5 MW-25 MW [€/m] | 110.5908 | 110.5908 | 110.5908 | 110.5908 | 99.5317 | 121.6498 | 99.5317 | 121.6498 | 0 | 1
Investment costs; single line, 25 MW-100 MW [€/m] | bar: Est to -
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 1
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 1
| Fixed O&M [€/MW/year] | 21.2675 | 21.2675 | 21.2675 | 21.2675 | 17.014 | 25.5209 | 17.014 | 25.5209 | 0 | 1
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Technology-specific data
References:
1. HMN Naturgas
Notes:
A. For the defined case "New distribution in existing densely populated areas, city centres etc." it is assessed the natural gas based heating will be designed with one boiler and heat is distributied to the endusers by a locel district heating sytem. This means that the local natural gas system will only consist of a A service line with a capacity of 1.5 MW supplying a boiler aswell a meter and a pressure regulator. Therefore losses are neglegted
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There is no power consuming parts in the distribution system
D. Based on given case
E. Stated number is for a service line supplying 1,5 MW.
F. Not relavant, see note A

## 2.5 gas New area
Technology |  | Energy Transport Natural Gas Distribution, New developed residential areas
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines [%] | 0.26307 | 0.26307 | 0.26307 | 0.26307 | 0.05 | 0.3 | 0.05 | 0.3 | A | 1
Energy losses, stations [%] | bar: Est to -
| Auxiliary electricity consumption [%] of energy delivered | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 80 | 50 | 80 |  | 2
Typical load profile [-] | bar: Est to Upper
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25 | D
| - Commercial | Est: N/A; Est: N/A; Est: N/A; Est: N/A; -: D
| Construction time [years] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 |  | 2
Financial data
| Distribution network costs [€/MWh/year] City | 287.1106 | 287.1106 | 287.1106 | 287.1106 | 255.2095 | 319.0118 | 255.2095 | 319.0118 | 0 | 2
| Investment costs; service line, 0-20 kW [€/unit] | 1701.3963 | 1701.3963 | 1701.3963 | 1701.3963 | 1488.7218 | 1914.0709 | 1488.7218 | 1914.0709 | 0 | 2
Investment costs; service line, 20-50 kW [€/unit] | bar: Est to -
Investment costs; service line, 50-100 kW [€/unit] | bar: Est to -
Investment costs; service line, above 100 kW [€/unit] | bar: Est to -
| Investment costs; single line, 0-50 kW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 50-250 kW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 100-250 kW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 250 kW-1 MW [€/m] | 49.6241 | 49.6241 | 49.6241 | 49.6241 | 44.6617 | 54.5865 | 44.6617 | 54.5865 | F
| Investment costs; single line, 1 MW-5 MW [€/m] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 47.8518 | 58.4855 | 47.8518 | 58.4855 | G
| Investment costs; single line, 5 MW-25 MW [€/m] | 67.3469 | 67.3469 | 67.3469 | 67.3469 | 60.6122 | 74.0816 | 60.6122 | 74.0816 | G
| Investment costs; single line, 25 MW-100 MW [€/m] | - | - | - | - | - | - | - | - | 0
Reinforcement costs [€/MW] | bar: Est to -
Type 1 station [€/MW] | bar: Est to -
Type 2 station [€/MW] | bar: Est to -
| Investments, percentage installation | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90% | 0 | 2
| Investments, percentage materials | 20% | 20% | 20% | 20% | 10% | 30% | 10% | 30% | 0 | 2
| Fixed O&M [€/MW/year] | 978.3029 | 978.3029 | 978.3029 | 978.3029 | 786.8958 | 1169.71 | 786.8958 | 1169.71 | 0 | 2
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
Technology-specific data
References:
1. Survey methane emissions for gas transmission and distribution in Europe Marcogaz WG-ME-14-26 29/02/2016
2. HMN Naturgas
Notes:
A. No general data are available for the Danish gas system. The stated losses are based on a European survey. European gas networks are generally older than the Danish system. Therefore, it is expected the losses from the Danish system are significantly lower than stated in the table. The lack of data explains the high uncertainty stated.
B. As mentioned in the qualitative description, new gas systems will be constructed without stations in the distribution network
C. There are no power consuming parts in the distribution system
D. Based on given case
E. Capacity range not relevant for given case
F. Stated number is for Ø40 pipes-the smallest pipe applied. It is only marginally cheaper to apply smaller pipes.
G. Two pipes were chosen for each interval (one for the lowest power level and one for the highest). The average of these two are stated in the table.
H. Reinforcement not relevant
I. No station will be installed for the distribution network

## 3.1 DH transmission
Technology |  | Energy Transport District Heating Transmission
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, lines 1-20 MW [% per km] | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 1.5 | 0.8 | 1.2 | A | [1, 2]
| Energy losses, lines 20-100 MW [% per km] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.375 | 0.2 | 0.3 | A | [1, 2]
| Energy losses, lines above 100 MW [% per km] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.15 | 0.08 | 0.12 | A | [1, 2]
| Energy losses, Heat exchanger stations [%] | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 1.5 | 0.8 | 1.2 |  | 1
| Energy losses, Pumping stations [%] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G | 1
| Auxiliary electricity consumption [%] energy transmitted | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 4]
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | B | [1, 2]
| Typical load profile [-] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.6 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 1
Financial data
| Investment costs; single line, 0-50 MW [€/MW/m] | 55.9207 | 63.1948 | 63.1948 | 63.1948 | 63.1948 | 63.1948 | 50.7489 | 75.0024 | 50.7489 | 75.0024 | [C, D] | [1, 3]
| Investment costs; single line, 50-100 MW [€/MW/m] | 27.9431 | 31.5779 | 31.5779 | 31.5779 | 31.5779 | 31.5779 | 25.4138 | 37.4085 | 25.4138 | 37.4085 | [C, D] | [1, 3]
| Investment costs; single line, 100-250 MW [€/MW/m] | 17.477 | 19.7504 | 19.7504 | 19.7504 | 19.7504 | 19.7504 | 15.8655 | 23.4058 | 15.8655 | 23.4058 | [C, D] | [1, 3]
| Investment costs; single line, 250-500 MW [€/MW/m] | 10.5204 | 11.8888 | 11.8888 | 11.8888 | 11.8888 | 11.8888 | 9.5484 | 14.0843 | 9.5484 | 14.0843 | [C, D] | [1, 3]
| Investment costs; single line, 500-1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Investment costs; single line, above 1000 MW [€/MW/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Fixed O&M [€/MW/km/year] | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 200 | 50 | 200
| Variable O&M [€/MWh/km] | 0.10634 | 0.11663 | 0.11663 | 0.11663 | 0.11663 | 0.11663 | 0.038487 | 1.7494 | 0.038487 | 1.7494 |  | [1, 4]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | C | 2
| Investments, percentage materials | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% |  | 2
| Investment, percentage soft cost | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | F | 2
Technology-specific data
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | E
| Investment costs; Heat exchanger station [€/MW] | 122287.8884 | 140161.8193 | 140161.8193 | 140161.8193 | 140161.8193 | 140161.8193 | 77089.0006 | 168194.1831 | 77089.0006 | 168194.1831 |  | 1
| Investment costs; Pump station [€/MW] | 111654.0923 | 127473.1986 | 127473.1986 | 127473.1986 | 127473.1986 | 127473.1986 | 70110.2592 | 152967.8384 | 70110.2592 | 152967.8384 |  | 1
References:
1. Based on Ramboll experience figures
2. LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. The loss is per trench km of transmission pipeline pair.
B. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
C. The cost is per trench meter transmission pipeline pair in unpaved areas.
D. Two district heating pipes were chosen for each interval (one for the lowest effect level and one for the highest). The average of these two are stated in the table. For cost interpolation: P = a * C^b, where P = cost in €/MW/m, C = capacity in MW, a = 330 and b =-0,571.
E. Depends on the scale of the transmission grid and supply strategy of reserve capacity. Therefore, it is not possible to generalize these costs.
F. Soft costs include design, planning, tender, permits, supervision, etc.

## 3.2 DH_Distribu Suburb
Technology |  | Energy Transport District Heating Distribution, Suburban
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, network [%] | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 10 | 16 | 9 | 14 | [A, B] | 2
| Auxiliary electricity consumption [%] of energy delivered | 2 | 2 | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 4
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | C | 2
Typical load factor [-]
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.18 | 0.22 | 0.18 | 0.22
| - Commercial | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3
Financial data
| Investments cost, distribution network [M€/km2] | 6.4626 | 7.3032 | 7.3032 | 7.3032 | 7.3032 | 7.3032 | 5.4797 | 9.0684 | 5.4797 | 9.0684 | [D, E] | [1, 3]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | E | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 25% | 25% | 20% | 30% | 20% | 30% | E | 2
| Investment, percentage soft costs percentage | 15% | 15% | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | H | 2
| Fixed O&M [€/MW/year] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 750 | 2000 | 750 | 2000 | M | 1
| Variable O&M [€/MWh] | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 1.508 | 3.0161 | 1.508 | 3.0161 | M | [1, 4]
Technology-specific data
| Investment costs; service line, 0-20 kW [€/unit] | 4164.6016 | 4706.3255 | 4706.3255 | 4706.3255 | 4706.3255 | 4706.3255 | 3242.5827 | 6192.4458 | 3242.5827 | 6192.4458 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 20-50 kW [€/unit] | 4518.7972 | 5106.5942 | 5106.5942 | 5106.5942 | 5106.5942 | 5106.5942 | 3547.7252 | 6678.7487 | 3547.7252 | 6678.7487 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 50-100 kW [€/unit] | 4987.2013 | 5635.9275 | 5635.9275 | 5635.9275 | 5635.9275 | 5635.9275 | 3953.0763 | 7309.6865 | 3953.0763 | 7309.6865 | [B, E, F, J] | [1, 3]
| Investment costs; service line, above 100 kW [€/unit] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | K
| Investment costs; single line, 0-50 kW [€/m] | 308.4523 | 348.5752 | 348.5752 | 348.5752 | 348.5752 | 348.5752 | 241.1895 | 455.9609 | 241.1895 | 455.9609 | [B, E, G] | [1, 3]
| Investment costs; single line, 50-250 kW [€/m] | 389.9116 | 440.6306 | 440.6306 | 440.6306 | 440.6306 | 440.6306 | 327.206 | 554.0552 | 327.206 | 554.0552 | [B, E, G] | [1, 3]
| Investment costs; single line, 100-250 kW [€/m] | 406.5826 | 459.4701 | 459.4701 | 459.4701 | 459.4701 | 459.4701 | 342.0119 | 576.9283 | 342.0119 | 576.9283 | [B, E, G] | [1, 3]
| Investment costs; single line, 250 kW-1 MW [€/m] | 515.5657 | 582.6296 | 582.6296 | 582.6296 | 582.6296 | 582.6296 | 456.5441 | 700.0145 | 456.5441 | 700.0145 | [B, E, G] | [1, 3]
| Investment costs; single line, 1 MW-5 MW [€/m] | 724.6157 | 818.8724 | 818.8724 | 818.8724 | 818.8724 | 818.8724 | 646.1684 | 971.0722 | 646.1684 | 971.0722 | [B, E, G] | [1, 3]
| Investment costs; single line, 5 MW-25 MW [€/m] | 1308.5602 | 1478.7753 | 1478.7753 | 1478.7753 | 1478.7753 | 1478.7753 | 1184.4561 | 1752.5903 | 1184.4561 | 1752.5903 | [B, E, G] | [1, 3]
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Pumping station above 1 MW [€/MW] | 98736.0339 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 61998.7032 | 135269.898 | 61998.7032 | 135269.898 | I | 1
| Pumping station below 1 MW [€/MW] | 255209.4707 | 291367.4445 | 263879.9497 | 263879.9497 | 263879.9497 | 263879.9497 | 160252.0945 | 349640.9333 | 160252.0945 | 349640.9333 | I | 1
References:
1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
2. Ramboll experience and technical data from LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities
C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on an area of scattered single-family houses of 1-2 floors with a heat density of 10 GWh/year/km2.
E. A paved area is assumed for the distribution network. For service lines 50 % unpaved and 50 % paved area is asumed.
F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
K. Service lines above 100 kW are not relevant in the specific area type.
L. Single lines above 25 MW are not relevant in the specific area type.
M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.

## 3.3 DH_Distribu City
Technology |  | Energy Transport District Heating Distribution, City
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, network [%] | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 9 | 4 | 8 | [A, B] | 2
| Auxiliary electricity consumption [%] of energy delivered | 2 | 2 | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 4
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | C | 2
Typical load factor [-]
| - Residential | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.18 | 0.25 | 0.18 | 0.25
| - Commercial | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.15 | 0.25 | 0.15 | 0.25
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3
Financial data
| Investments cost, distribution network [M€/km2] | 5.968 | 6.7443 | 6.7443 | 6.7443 | 6.7443 | 6.7443 | 5.0474 | 8.3655 | 5.0474 | 8.3655 | [D, E] | [1, 3]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | E | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 25% | 25% | 20% | 30% | 20% | 30% | E | 2
| Investment, percentage soft costs | 15% | 15% | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | H | 2
| Fixed O&M [€/MW/year] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 750 | 2000 | 750 | 2000 | M | 1
| Variable O&M [€/MWh] | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 2.0107 | 1.508 | 3.0161 | 1.508 | 3.0161 | M | [1, 4]
Technology-specific data
| Investment costs; service line, 0-20 kW [€/unit] | 4961.2182 | 5606.5644 | 5606.5644 | 5606.5644 | 5606.5644 | 5606.5644 | 3804.7675 | 7431.9167 | 3804.7675 | 7431.9167 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 20-50 kW [€/unit] | 5333.929 | 6027.7568 | 6027.7568 | 6027.7568 | 6027.7568 | 6027.7568 | 4135.3976 | 7883.1671 | 4135.3976 | 7883.1671 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 50-100 kW [€/unit] | 5826.9859 | 6584.9497 | 6584.9497 | 6584.9497 | 6584.9497 | 6584.9497 | 4627.3368 | 8482.0584 | 4627.3368 | 8482.0584 | [B, E, F, J] | [1, 3]
| Investment costs; service line, above 100 kW [€/unit] | 7159.8328 | 8091.1709 | 8091.1709 | 8091.1709 | 8091.1709 | 8091.1709 | 6264.0232 | 9918.3185 | 6264.0232 | 9918.3185 | [B, E, F, J, K] | [1, 3]
| Investment costs; single line, 0-50 kW [€/m] | 338.688 | 382.7439 | 382.7439 | 382.7439 | 382.7439 | 382.7439 | 262.3075 | 506.8973 | 262.3075 | 506.8973 | [B, E, G] | [1, 3]
| Investment costs; single line, 50-100 kW [€/m] | 380.2063 | 429.6629 | 429.6629 | 429.6629 | 429.6629 | 429.6629 | 303.189 | 559.8538 | 303.189 | 559.8538 | [B, E, G] | [1, 3]
| Investment costs; single line, 100-250 kW [€/m] | 441.2294 | 498.6238 | 498.6238 | 498.6238 | 498.6238 | 498.6238 | 372.4651 | 624.7824 | 372.4651 | 624.7824 | [B, E, G] | [1, 3]
| Investment costs; single line, 250 kW-1 MW [€/m] | 551.4741 | 623.2089 | 623.2089 | 623.2089 | 623.2089 | 623.2089 | 488.4229 | 749.2944 | 488.4229 | 749.2944 | [B, E, G] | [1, 3]
| Investment costs; single line, 1 MW-5 MW [€/m] | 773.1749 | 873.7481 | 873.7481 | 873.7481 | 873.7481 | 873.7481 | 691.7201 | 1035.2719 | 691.7201 | 1035.2719 | [B, E, G] | [1, 3]
| Investment costs; single line, 5 MW-25 MW [€/m] | 1390.4364 | 1571.3019 | 1571.3019 | 1571.3019 | 1571.3019 | 1571.3019 | 1258.996 | 1863.1035 | 1258.996 | 1863.1035 | [B, E, G] | [1, 3]
| Investment costs; single line, 25 MW-100 MW [€/m] | 2532.9797 | 2862.4651 | 2862.4651 | 2862.4651 | 2862.4651 | 2862.4651 | 2305.633 | 3393.1957 | 2305.633 | 3393.1957 | [B, E, G, L] | [1, 3]
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Pumping station above 1 MW [€/MW] | 98736.0339 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 112724.915 | 61998.7032 | 135269.898 | 61998.7032 | 143842.3191 | I | 1
| Pumping station below 1 MW [€/MW] | 255209.4707 | 291367.4445 | 291367.4445 | 291367.4445 | 291367.4445 | 291367.4445 | 160252.0945 | 349640.9333 | 160252.0945 | 349640.9333 | I | 1
References:
1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
2. Ramboll experience and technical data from LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on mixed densely packed buildings in 2-3 storeys and with a heat density of 15 GWh/year/km2.
E. A paved area is assumed for the distribution network as well as for service lines.
F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 33%
K. The value stated is for a DN50 twin pipe. This pipe size is able to deliver up to around 250 kW. If a higher capacity is needed the price will increase.
L. The value stated is for a DN400 pipe pair. This pipe size is able to deliver up to around 45 MW. If a higher capacity is needed the price will increase.
M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.

## 3.4 DH_Distribu New area
Technology |  | Energy Transport District Heating Distribution, New Area
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy losses, network [%] | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 24 | 10 | 20 | [A, B] | 2
| Auxiliary electricity consumption [%] of energy delivered | 2 | 2 | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 |  | 4
| Technical life time [years] | 45 | 45 | 45 | 45 | 45 | 45 | 30 | 60 | 30 | 60 | C | 2
Typical load factor [-]
| - Residential | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.1 | 0.2 | 0.1 | 0.2
| - Commercial | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.1 | 0.2 | 0.1 | 0.2
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2
Financial data
| Investments cost, distribution network [M€/km2] | 4.7197 | 5.3336 | 5.3336 | 5.3336 | 5.3336 | 5.3336 | 3.9965 | 6.6191 | 3.9965 | 6.6191 | [D, E] | [1, 3]
| Investments, percentage installation | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70% | E | 2
| Investments, percentage materials | 25% | 25% | 25% | 25% | 25% | 25% | 20% | 30% | 20% | 30% | E | 2
| Investment, percentage soft costs | 15% | 15% | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% | H | 2
| Fixed O&M [€/MW/year] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 750 | 2000 | 750 | 2000 | M | 1
| Variable O&M [€/MWh] | 1.5951 | 1.7494 | 1.7494 | 1.7494 | 1.7494 | 1.7494 | 1.3121 | 2.6241 | 1.3121 | 2.6241 | M | [1, 4]
Technology-specific data
| Investment costs; service line, 0-20 kW [€/unit] | 3504.3785 | 3960.2217 | 3960.2217 | 3960.2217 | 3960.2217 | 3960.2217 | 2706.7547 | 5231.3553 | 2706.7547 | 5231.3553 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 20-50 kW [€/unit] | 3783.9591 | 4276.1697 | 4276.1697 | 4276.1697 | 4276.1697 | 4276.1697 | 2951.1919 | 5592.5358 | 2951.1919 | 5592.5358 | [B, E, F, J] | [1, 3]
| Investment costs; service line, 50-100 kW [€/unit] | 4153.7518 | 4694.0644 | 4694.0644 | 4694.0644 | 4694.0644 | 4694.0644 | 3295.6762 | 6066.1745 | 3295.6762 | 6066.1745 | [B, E, F, J] | [1, 3]
| Investment costs; service line, above 100 kW [€/unit] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | K
| Investment costs; single line, 0-50 kW [€/m] | 242.6776 | 274.2447 | 274.2447 | 274.2447 | 274.2447 | 274.2447 | 188.8114 | 361.0718 | 188.8114 | 361.0718 | [B, E, G] | [1, 3]
| Investment costs; single line, 50-250 kW [€/m] | 302.329 | 341.6554 | 341.6554 | 341.6554 | 341.6554 | 341.6554 | 253.3243 | 431.3804 | 253.3243 | 431.3804 | [B, E, G] | [1, 3]
| Investment costs; single line, 100-250 kW [€/m] | 317.9295 | 359.2852 | 359.2852 | 359.2852 | 359.2852 | 359.2852 | 267.9289 | 450.6415 | 267.9289 | 450.6415 | [B, E, G] | [1, 3]
| Investment costs; single line, 250 kW-1 MW [€/m] | 400.1399 | 452.1894 | 452.1894 | 452.1894 | 452.1894 | 452.1894 | 354.3626 | 543.4908 | 354.3626 | 543.4908 | [B, E, G] | [1, 3]
| Investment costs; single line, 1 MW-5 MW [€/m] | 561.6715 | 634.7327 | 634.7327 | 634.7327 | 634.7327 | 634.7327 | 501.7082 | 752.3791 | 501.7082 | 752.3791 | [B, E, G] | [1, 3]
| Investment costs; single line, 5 MW-25 MW [€/m] | 1012.1237 | 1143.779 | 1143.779 | 1143.779 | 1143.779 | 1143.779 | 916.2945 | 1355.8852 | 916.2945 | 1355.8852 | [B, E, G] | [1, 3]
| Investment costs; single line, 25 MW-100 MW [€/m] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Reinforcement costs [€/MW] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Pumping station above 1 MW [€/MW] | 92764.2348 | 105907.0338 | 105907.0338 | 105907.0338 | 105907.0338 | 105907.0338 | 59307.9389 | 127088.4405 | 59307.9389 | 127088.4405 | I | 1
| Pumping station below 1 MW [€/MW] | 247371.1906 | 282418.6401 | 282418.6401 | 282418.6401 | 282418.6401 | 282418.6401 | 158154.4384 | 338902.3681 | 158154.4384 | 338902.3681 | I | 1
References:
1. Based on Ramboll experience figures. Costs have been deflated by a factor of 0.870 to 2020-EURO from project data in 2024.
2. Ramboll experience and technical data from LOGSTOR A/S
3. Consolidated with data from Danish District Heating Association
4. Consolidated with statistics from Danish District Heating Association 2020
Notes:
A. For entire distribution network inclusive pump stations and service lines. For pump stations the heat loss is negligible.
B. Twin pipes assumed up to 5 MW and pipe pairs for larger pipe capacities.
C. The technical life time of a district heating pipe is minimum 30 years. However the life time can be substantially longer depending on operation conditions e.g. temperaturevariation, soil conditions etc.
D. The distribution network costs are inclusive pumping stations but exclusive service pipelines and based on close cluster housing in 1-2 floors in shared green areas and with a heat density of 6.5 GWh/year/km2.
E. An unpaved area is assumed for the distribution network as well as for service lines. Coordination with the establishment of other infrastructure (electricity, water, sewerage) may entail construction cost benefits.
F. Cost of service lines are based on an average service line lenght of 15 meters. Two service lines were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table.
G. Two district heating pipes were chosen for each interval (one for the lowest capacity level and one for the highest). The average of these two are stated in the table. The cost is per trench meter.
H. Soft costs include costs for design, planning, tender, permits, supervision, etc. after the final investment decision.
I. Investment costs per MW for pumping stations below 1 MW are very different from costs for stations above 1 MW.
J It is assumed that the service line is constructed at the same time as the street line. For a subsequent customer connection (saddle connection), the investment costs for service lines are increased by 50%
K. Service lines above 100 kW are not relevant in the specific area type.
L. Single lines above 25 MW are not relevant in the specific area type.
M. The amount of thermal energy in MWh can be calculated from the heat density mentioned in note D. The effect in MW equals: amount of energy [MWh]/(8760⋅load factor). For a district heating system, the load factor is around 0.34.
For the entire table: With low-temperature district heating (LTDH), the stated heat loss of the district heating network is reduced by 20-25% and the district heating network investment is reduced by up to 5%.

## 4.1 H2 pipeline transp. 40 barg
Technology |  | Energy Transport, Hydrogen Pipeline 40 barg
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy to compensate pressure drop, 8 inches line, 200 MW [% of transported energy per 100km] | 1.509% | 1.509% | 1.509% | 1.509% | 1.509% | 1.1% | 2.3% | 1.1% | 2.3% | A, B | 2
| Energy to compensate pressure drop, 10 inches line, 400 MW [% of transported energy per 100km] | 1.151% | 1.151% | 1.151% | 1.151% | 1.151% | 0.8% | 1.7% | 0.8% | 1.7% | A, B | 2
| Energy to compensate pressure drop, 12 inches line, 600 MW [% of transported energy per 100km] | 0.9227% | 0.9227% | 0.9227% | 0.9227% | 0.9227% | 0.6% | 1.4% | 0.6% | 1.4% | A, B | 2
| Energy to compensate pressure drop, 20 inches line, 1600 MW [% of transported energy per 100km] | 0.499% | 0.499% | 0.499% | 0.499% | 0.499% | 0.3% | 0.7% | 0.3% | 0.7% | A, B | 2
| Energy to compensate pressure drop, 30 inches line, 3500 MW [% of transported energy per 100km] | 0.3075% | 0.3075% | 0.3075% | 0.3075% | 0.3075% | 0.2% | 0.5% | 0.2% | 0.5% | A, B | 2
| Energy to compensate pressure drop, 36 inches line, 5000 MW [% of transported energy per 100km] | 0.2475% | 0.2475% | 0.2475% | 0.2475% | 0.2475% | 0.2% | 0.4% | 0.2% | 0.4% | A, B | 2
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | C | 1
| Typical load profile (-) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.9 | 0.8 | 0.9 | D
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | E | 2
Financial data
| Investment costs; single line, 8 inches [MEUR/km] | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.644 | 1.38 | 0.644 | 1.38 | F | 2
| Investment costs; single line, 10 inches [MEUR/km] | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 0.721 | 1.545 | 0.721 | 1.545 | F | 2
| Investment costs; single line, 12 inches [MEUR/km] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 0.798 | 1.71 | 0.798 | 1.71 | F | 2
| Investment costs; single line, 20 inches [MEUR/km] | 1.41 | 1.41 | 1.41 | 1.41 | 1.41 | 0.987 | 2.115 | 0.987 | 2.115 | F | 2
| Investment costs; single line, 30 inches [MEUR/km] | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 1.491 | 3.195 | 1.491 | 3.195 | F | 2
| Investment costs; single line, 36 inches [MEUR/km] | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 1.855 | 3.975 | 1.855 | 3.975 | F | 2
| Investments, percentage installation [%] | 56% | 56% | 56% | 56% | 56% | 50% | 60% | 50% | 60% |  | 2
| Investments, percentage materials [%] | 44% | 44% | 44% | 44% | 44% | 40% | 50% | 40% | 50% |  | 2
| Additional costs [% of Investment costs] | 35% | 35% | 35% | 35% | 35% | 30% | 40% | 30% | 40% | G | 2
| Fixed O&M [% of investment costs] | 1% | 1% | 1% | 1% | 1% |  |  |  |  | H | 2
| Variable O&M [% of investment costs] | 0% | 0% | 0% | 0% | 0% |  |  |  |  | I | 2
Technology-specific data
| Compressors stations [MEUR/MWe] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.84 | 2.4 | 0.84 | 2.4 | J | 2; 3
| Compression electricity consumption [kWh/kg H2] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K | 2
References:
1. Energinet assessment for DHB project.
2. COWI experience
3. Bundesnetzargentur - Hydrogen Core Network
Notes:
A. | H2 is assumed to already be at required inlet pressure, thus no compressor is accounted for at inlet, but only ones needed over the 100 km line to compensate pressure drops. Energy needed to compensate pressure drop for several pipeline diameters for the reported operating pressure level of 140 barg. It is the estimated energy consumption in % respect to the transported energy. No energy losses are expected when transmitting H2. Booster compressors needed over 100 km distance for given capacity (full utilization), pipeline dimension and assumed minimum pressure level (2/3 P_inlet) : 8 inches - 3 comp. ; 10 inches - 2 comp. ; 12 inches - 2 comp. ; 20 inches - 1 comp.; 30 inches - 0 comp. ; 36 inches - 0 comp.
B. | Capacity for each pipeline size at this inlet pressure level P_inlet (40 barg), assuming full pipeline utilization, 20 m/s velocity and minimum pressure level of 25 barg are: 8 inches - 200 MW; 10 inches - 400 MW; 12 inches - 600 MW; 20 inches - 1600 MW; 30 inches - 3500 MW; 36 inches - 5000 MW.
C. | 50 years lifetime for new-built pipelines. 30 years lifetime are considered for the repurposed sections. Newbuilt stations and compressors have a lifetime of 20 year and up to 50 years under good maintenance.
D. | Typical load from natural gas pipeline, as the current load factor for new hydrogen pipelines is not well known at this stage.
E. | Construction time depens on pipeline size and length. Reported value is an average between short distance distribution and long distance transmission projects.
F. | PLR and LV stations are included in the pipeline investment cost (MEUR/km) and account for approximately 20% of the cost. As reported in qualitative description, these are estimated assuming a 100 km pipeline, with PLR stations installed at both the inlet and outlet, and LV stations positioned every 20 km, including at both ends of the pipeline. Uncertainty range is estimated based on Class 5 estimates (lower range -30%, upper range +50%).
G. | Additional costs are not related to pipeline and station construction (equipment and installation costs), and need to be added on top of these to capture the full project costs. Additional costs account for construction management and owner´s costs.
H. | Fixed O&M is estimated as fixed yearly cost of investment costs.
I. | Operation costs do not include energy losses. There might be costs for auxilliary electricity consumption of compressors, which can be added in a project specific case (see consumptino under technical data)
J. | Compressors, or boosters, can be included if relevant to the scope, e.g. compression after electrolysis at inlet to pipeline or inlets/outlets between pipelines. There might be efficiency gains in the future based on technological development, which is not documentet enough to include in the catalogue.
K. | Basis assumption is that hydrogen is delivered at the required pressure. In case compression is part of scope, the amount of power needed for compression depends on inlet and outlet pressure required, in this case to compress from 40 to 40 barg from hydrogen producers/branch pipeline to transmission. Higher pressure levels require more energy and thus higher compressor capacity installed.

## 4.2 pipeline transp. 90 barg
Technology |  | Energy Transport, Hydrogen Pipeline 90 barg
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy to compensate pressure drop, 8 inches line, 500 MW [% of transported energy per 100km] | 3.044% | 3.044% | 3.044% | 3.044% | 3.044% | 2.1% | 4.6% | 2.1% | 4.6% | A, B | 2
| Energy to compensate pressure drop, 10 inches line, 800 MW [% of transported energy per 100km] | 2.324% | 2.324% | 2.324% | 2.324% | 2.324% | 1.6% | 3.5% | 1.6% | 3.5% | A, B | 2
| Energy to compensate pressure drop, 12 inches line, 1200 MW [% of transported energy per 100km] | 1.865% | 1.865% | 1.865% | 1.865% | 1.865% | 1.3% | 2.8% | 1.3% | 2.8% | A, B | 2
| Energy to compensate pressure drop, 20 inches line, 3300 MW [% of transported energy per 100km] | 1.011% | 1.011% | 1.011% | 1.011% | 1.011% | 0.7% | 1.5% | 0.7% | 1.5% | A, B | 2
| Energy to compensate pressure drop, 30 inches line, 7500 MW [% of transported energy per 100km] | 0.6243% | 0.6243% | 0.6243% | 0.6243% | 0.6243% | 0.4% | 0.9% | 0.4% | 0.9% | A, B | 2
| Energy to compensate pressure drop, 36 inches line, 10800 MW [% of transported energy per 100km] | 0.503% | 0.503% | 0.503% | 0.503% | 0.503% | 0.4% | 0.8% | 0.4% | 0.8% | A, B | 2
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | C | 1
| Typical load profile (-) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.9 | 0.8 | 0.9 | D
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | E | 2
Financial data
| Investment costs; single line, 8 inches [MEUR/km] | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.644 | 1.38 | 0.644 | 1.38 | F | 2
| Investment costs; single line, 10 inches [MEUR/km] | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 0.721 | 1.545 | 0.721 | 1.545 | F | 2
| Investment costs; single line, 12 inches [MEUR/km] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 0.798 | 1.71 | 0.798 | 1.71 | F | 2
| Investment costs; single line, 20 inches [MEUR/km] | 1.76 | 1.76 | 1.76 | 1.76 | 1.76 | 1.232 | 2.64 | 1.232 | 2.64 | F | 2
| Investment costs; single line, 30 inches [MEUR/km] | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.037 | 4.365 | 2.037 | 4.365 | F | 2
| Investment costs; single line, 36 inches [MEUR/km] | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 2.639 | 5.655 | 2.639 | 5.655 | F | 2
| Investments, percentage installation [%] | 56% | 56% | 56% | 56% | 56% | 50% | 60% | 50% | 60% |  | 2
| Investments, percentage materials [%] | 44% | 44% | 44% | 44% | 44% | 40% | 50% | 40% | 50% |  | 2
| Additional costs [% of Investment costs] | 35% | 35% | 35% | 35% | 35% | 30% | 40% | 30% | 40% | G | 2
| Fixed O&M [% of investment costs] | 1% | 1% | 1% | 1% | 1% |  |  |  |  | H | 2
| Variable O&M [% of investment costs] | 0% | 0% | 0% | 0% | 0% |  |  |  |  | I | 2
Technology-specific data
| Compressors stations [MEUR/MWe] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.84 | 1.8 | 0.84 | 1.8 | J | 2; 3
| Compression electricity consumption [kWh/kg H2] | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.4 | 0.51 | 0.4 | 0.51 | K | 2
References:
1. Energinet assessment for DHB project.
2. COWI experience
3. Bundesnetzargentur - Hydrogen Core Network
Notes:
A. | H2 is assumed to already be at required inlet pressure, thus no compressor is accounted for at inlet, but only ones needed over the 100 km line to compensate pressure drops. Energy needed to compensate pressure drop for several pipeline diameters for the reported operating pressure level of 90 barg. It is the estimated energy consumption in % respect to the transported energy. No energy losses are expected when transmitting H2. Booster compressors needed over 100 km distance for given capacity (full utilization), pipeline dimension and assumed minimum pressure level (2/3 P_inlet) : 8 inches - 3 comp. ; 10 inches - 3 comp. ; 12 inches - 2 comp. ; 20 inches - 1 comp.; 30 inches - 0 comp. ; 36 inches - 0 comp.
B. | Capacity for each pipeline size at this inlet pressure level P_inlet (90 barg), assuming full pipeline utilization, 20 m/s velocity and minimum pressure level of 2/3 P_inlet are: 8 inches - 500 MW; 10 inches - 800 MW; 12 inches - 1200 MW; 20 inches - 3300 MW; 30 inches - 7500 MW; 36 inches - 10800 MW.
C. | 50 years lifetime for new-built pipelines. 30 years lifetime are considered for the repurposed sections. Newbuilt stations and compressors have a lifetime of 20 year and up to 50 years under good maintenance.
D. | Typical load from natural gas pipeline, as the current load factor for new hydrogen pipelines is not well known at this stage.
E. | Construction time depens on pipeline size and length. Reported value is an average between short distance distribution and long distance transmission projects.
F. | PLR and LV stations are included in the pipeline investment cost (MEUR/km) and account for approximately 20% of the cost. As reported in qualitative description, these are estimated assuming a 100 km pipeline, with PLR stations installed at both the inlet and outlet, and LV stations positioned every 20 km, including at both ends of the pipeline. Uncertainty range is estimated based on Class 5 estimates (lower range -30%, upper range +50%).
G. | Additional costs are not related to pipeline and station construction (equipment and installation costs), and need to be added on top of these to capture the full project costs. Additional costs account for construction management and owner´s costs.
H. | Fixed O&M is estimated as fixed yearly cost of investment costs.
I. | Operation costs do not include energy losses. There might be costs for auxilliary electricity consumption of compressors, which can be added in a project specific case (see consumptino under technical data)
J. | Compressors, or boosters, can be included if relevant to the scope, e.g. compression after electrolysis at inlet to pipeline or inlets/outlets between pipelines. There might be efficiency gains in the future based on technological development, which is not documentet enough to include in the catalogue.
K. | Basis assumption is that hydrogen is delivered at the required pressure. In case compression is part of scope, the amount of power needed for compression depends on inlet and outlet pressure required, in this case to compress from 40 to 90 barg from hydrogen producers/branch pipeline to transmission. Higher pressure levels require more energy and thus higher compressor capacity installed.

## 4.3 pipeline transp. 140 barg
Technology |  | Energy Transport, Hydrogen Pipeline 140 barg
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | Est | Est | Est | Est | Est | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Energy to compensate pressure drop, 8 inches line, 800 MW [% of transported energy per 100km] | 4.487% | 4.487% | 4.487% | 4.487% | 4.487% | 3.1% | 6.7% | 3.1% | 6.7% | A, B | 2
| Energy to compensate pressure drop, 10 inches line, 1200 MW [% of transported energy per 100km] | 3.426% | 3.426% | 3.426% | 3.426% | 3.426% | 2.4% | 5.1% | 2.4% | 5.1% | A, B | 2
| Energy to compensate pressure drop, 12 inches line, 1800 MW [% of transported energy per 100km] | 2.751% | 2.751% | 2.751% | 2.751% | 2.751% | 1.9% | 4.1% | 1.9% | 4.1% | A, B | 2
| Energy to compensate pressure drop, 20 inches line, 5000 MW [% of transported energy per 100km] | 1.492% | 1.492% | 1.492% | 1.492% | 1.492% | 1% | 2.2% | 1% | 2.2% | A, B | 2
| Energy to compensate pressure drop, 30 inches line, 11100 MW [% of transported energy per 100km] | 0.9218% | 0.9218% | 0.9218% | 0.9218% | 0.9218% | 0.6% | 1.4% | 0.6% | 1.4% | A, B | 2
| Energy to compensate pressure drop, 36 inches line, 16000 MW [% of transported energy per 100km] | 0.7429% | 0.7429% | 0.7429% | 0.7429% | 0.7429% | 0.5% | 1.1% | 0.5% | 1.1% | A, B | 2
| Technical life time [years] | 50 | 50 | 50 | 50 | 50 | 45 | 55 | 45 | 55 | C | 1
| Typical load profile (-) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.9 | 0.8 | 0.9 | D
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | E | 2
Financial data
| Investment costs; single line, 8 inches [MEUR/km] | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.644 | 1.38 | 0.644 | 1.38 | F | 2
| Investment costs; single line, 10 inches [MEUR/km] | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 0.756 | 1.62 | 0.756 | 1.62 | F | 2
| Investment costs; single line, 12 inches [MEUR/km] | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 0.861 | 1.845 | 0.861 | 1.845 | F | 2
| Investment costs; single line, 20 inches [MEUR/km] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.47 | 3.15 | 1.47 | 3.15 | F | 2
| Investment costs; single line, 30 inches [MEUR/km] | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 2.576 | 5.52 | 2.576 | 5.52 | F | 2
| Investment costs; single line, 36 inches [MEUR/km] | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 3.416 | 7.32 | 3.416 | 7.32 | F | 2
| Investments, percentage installation [%] | 56% | 56% | 56% | 56% | 56% | 50% | 60% | 50% | 60% |  | 2
| Investments, percentage equipment [%] | 44% | 44% | 44% | 44% | 44% | 40% | 50% | 40% | 50% |  | 2
| Additional costs [% of Investment costs] | 35% | 35% | 35% | 35% | 35% | 30% | 40% | 30% | 40% | G | 2
| Fixed O&M [% of investment costs] | 1% | 1% | 1% | 1% | 1% |  |  |  |  | H | 2
| Variable O&M [% of investment costs] | 0% | 0% | 0% | 0% | 0% |  |  |  |  | I | 2
Technology-specific data
| Compressors stations [MEUR/MWe] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.84 | 1.8 | 0.84 | 1.8 | J | 2; 3
| Compression electricity consumption [kWh/kg H2] | 0.769 | 0.769 | 0.769 | 0.769 | 0.769 | 0.67 | 0.87 | 0.67 | 0.87 | K | 2
References:
1. Energinet assessment for DHB project.
2. COWI experience
3. Bundesnetzargentur - Hydrogen Core Network
Notes:
A. | H2 is assumed to already be at required inlet pressure, thus no compressor is accounted for at inlet, but only ones needed over the 100 km line to compensate pressure drops. Energy needed to compensate pressure drop for several pipeline diameters for the reported operating pressure level of 140 barg. It is the estimated energy consumption in % respect to the transported energy. No energy losses are expected when transmitting H2. Booster compressors needed over 100 km distance for given capacity (full utilization), pipeline dimension and assumed minimum pressure level (2/3 P_inlet) : 8 inches - 3 comp. ; 10 inches - 2 comp. ; 12 inches - 2 comp. ; 20 inches - 1 comp.; 30 inches - 0 comp. ; 36 inches - 0 comp.
B. | Capacity for each pipeline size at this inlet pressure level P_inlet (140 barg), assuming full pipeline utilization, 20 m/s velocity and minimum pressure level of 2/3 P_inlet are: 8 inches - 800 MW; 10 inches - 1200 MW; 12 inches - 1800 MW; 20 inches - 5000 MW; 30 inches - 11100 MW; 36 inches - 16000 MW.
C. | 50 years lifetime for new-built pipelines. 30 years lifetime are considered for the repurposed sections. Newbuilt stations and compressors have a lifetime of 20 year and up to 50 years under good maintenance.
D. | Typical load from natural gas pipeline, as the current load factor for new hydrogen pipelines is not well known at this stage.
E. | Construction time depens on pipeline size and length. Reported value is an average between short distance distribution and long distance transmission projects.
F. | PLR and LV stations are included in the pipeline investment cost (MEUR/km) and account for approximately 20% of the cost. As reported in qualitative description, these are estimated assuming a 100 km pipeline, with PLR stations installed at both the inlet and outlet, and LV stations positioned every 20 km, including at both ends of the pipeline. Uncertainty range is estimated based on Class 5 estimates (lower range -30%, upper range +50%).
G. | Additional costs are not related to pipeline and station construction (equipment and installation costs), and need to be added on top of these to capture the full project costs. Additional costs account for construction management and owner´s costs.
H. | Fixed O&M is estimated as fixed yearly cost of investment costs.
I. | Operation costs do not include energy losses. There might be costs for auxilliary electricity consumption of compressors, which can be added in a project specific case (see consumptino under technical data)
J. | Compressors, or boosters, can be included if relevant to the scope, e.g. compression after electrolysis at inlet to pipeline or inlets/outlets between pipelines. There might be efficiency gains in the future based on technological development, which is not documentet enough to include in the catalogue.
K. | Basis assumption is that hydrogen is delivered at the required pressure. In case compression is part of scope, the amount of power needed for compression depends on inlet and outlet pressure required, in this case to compress from 40 to 140 barg from hydrogen producers/branch pipeline to transmission. Higher pressure levels require more energy and thus higher compressor capacity installed.

## 5.1 H2 road transp.
Technology |  | H₂ road transport by tanker truck
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Energy demand truck (MJ/km/t H2) | 13.8 | 12.9 | 12 | 10 | 7.2 | 10 | 15 | 5 | 10 | A | 1
| Technical life time [years] | 10 | 10 | 10 | 10 | 10 | 4 | 12 | 4 | 12 | B
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | C
Financial data
| Transport fixed cost (EUR/t H2) | 182.7 | 169.2507 | 157.9673 | 131.6394 | 94.7804 | 127.89 | 274.05 | 66.3463 | 142.1706 | D, E, F | 2
| Variable cost per km (EUR/t H2/km) | 3.11 | 2.8885 | 2.696 | 2.2466 | 1.6176 | 2.177 | 4.665 | 1.1323 | 2.4264 | D, E, F | 2
Technology-specific data
References:
1. Network for Transport Measures (NTM) database, 2025
2. COWI transport model
Notes:
A. Values dependent on truck fuel consumption used for propulsion and amount of hydrogen stored per truck. Fuel consumption of 18 MJ/km is based on 50-60 t truck with trailer for road cargo transport baseline global average. Decrease over years ie expected due to an increase in capacity for hydrogen stored per truck. Basline capacity for 2025 is 1.3 ton H2 per truck.
B. Technical lifetime of truck (puller) will depend on the distance driven, 4-10 years. Lifetime trailer 10 years or more.
C. Based on expert judgement.
D. Capital cost of truck and fixed O&M is split into the fixed and variable cost based on relative time spend on loading/unloading and on driving.
E. Main fixed and variable costs assumptions are: CAPEX (Truck + Tanker) is 800.000 EUR, annual fixed OPEX is 5% truck capital cost, truck availability is 8000 hours per year, loading and unloading time is 120 minutes each, driver cost 40 EUR/MWh (24/7 operation), fuel cost for diesel 47 EUR/kJ, truck fuel consumption 18 MJ/km, truck average speed 50 km/h. In the future other engines types and fuels, such as electric trucks, can be come relevant, which can change CAPEX and OPEX.
F. Parameters that contributes in a decrease of both fixed and variable costs: increased transport capacity per truck, faster loading and unloading time, increased truck availability, decreased in truck CAPEX or any other OPEX. Expected decrease in fixed and variable cost is mostly driven by an expected increase in transport hydrogen capacity per truck. Capacity used across years: 1.3 ton H2 (2025), 1.4 ton H2 (2020), 1.5 ton H2 (2035), 1.8 ton H2 (2040), 2.5 ton H2 (2050).